## N-0 Volt Mag
PJM N-0 Voltage Magnitude Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026-W1-N1-WVM1 | 212041 | EHAZ TP2 | 69 | 229 | 0.92116 | 0.92116 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM2 | 211962 | WHHA 1 | 69 | 229 | 0.90173 | 0.90173 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM3 | 211961 | WHHA TP2 | 69 | 229 | 0.90957 | 0.90957 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM4 | 211960 | WHHA 2 | 69 | 229 | 0.90173 | 0.90173 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM5 | 211946 | FLND DC | 69 | 229 | 0.90447 | 0.90447 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM6 | 211945 | WEAT TP2 | 69 | 229 | 0.91407 | 0.91407 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM7 | 211944 | WEAT | 69 | 229 | 0.91245 | 0.91245 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM8 | 211533 | FLND | 69 | 229 | 0.90337 | 0.90337 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM9 | 211532 | FLND TP2 | 69 | 229 | 0.90448 | 0.90448 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM10 | 210918 | WHHA DC | 69 | 229 | 0.90173 | 0.90173 | 0.923 | Single | BASE CASE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## N-1 Thermal
PJM N-1 Thermal Result (Winter 2031 Case) | [16 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026-W1-N1-WT1 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138/138 | 205/205 | 345 | 102.8696 | 104.55 | Tower | 'AEP_P7-1_#17439___SRT-A' | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026-W1-N1-WT2 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138/138 | 205/205 | 345 | 98.6377 | 100.3 | Tower | 'AEP_P7-1_#17440___SRT-A' | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A

## N-1 Volt Mag
Will be addressed through the interregional process
PJM N-1 Voltage Magnitude Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026-W1-N1-WVM1 | 211962 | WHHA 1 | 69 | 229 | 0.88792 | 0.90173 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM2 | 211962 | WHHA 1 | 69 | 229 | 0.88777 | 0.90173 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM3 | 211962 | WHHA 1 | 69 | 229 | 0.88686 | 0.90173 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM4 | 211960 | WHHA 2 | 69 | 229 | 0.88792 | 0.90173 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM5 | 211960 | WHHA 2 | 69 | 229 | 0.88777 | 0.90173 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM6 | 211960 | WHHA 2 | 69 | 229 | 0.88686 | 0.90173 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM7 | 211946 | FLND DC | 69 | 229 | 0.89075 | 0.90447 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM8 | 211946 | FLND DC | 69 | 229 | 0.8906 | 0.90447 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM9 | 211946 | FLND DC | 69 | 229 | 0.88969 | 0.90447 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM10 | 211533 | FLND | 69 | 229 | 0.88962 | 0.90337 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM11 | 211533 | FLND | 69 | 229 | 0.88947 | 0.90337 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM12 | 211533 | FLND | 69 | 229 | 0.88856 | 0.90337 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM13 | 211532 | FLND TP2 | 69 | 229 | 0.89075 | 0.90448 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM14 | 211532 | FLND TP2 | 69 | 229 | 0.8906 | 0.90448 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM15 | 211532 | FLND TP2 | 69 | 229 | 0.88969 | 0.90448 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM16 | 210918 | WHHA DC | 69 | 229 | 0.88792 | 0.90173 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM17 | 210918 | WHHA DC | 69 | 229 | 0.88777 | 0.90173 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N1-WVM18 | 210918 | WHHA DC | 69 | 229 | 0.88686 | 0.90173 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment

## N-1 Load Drop
PJM N-1 Load Drop Result (Winter 2031 Case)
FG # Status | FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational Only | N/A | DVP_P7-1: LN 2165-2170_SRT-A | Tower | 345 | 0.0 | 345.0 | 345 | No | To be addressed through supplemental process.