## Thermal
PJM N-1-1 Thermal Result (Winter 2031 Case) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026-W1-N11-WT1 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 133.85 | 131.02 | No | Substation Equipment Exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-WT2 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 133.85 | 130.96 | No | Substation Equipment Exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-WT3 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069A_SRT-A | 131.61 | 128.64 | No | Substation Equipment Exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-WT4 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23069A_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 131.61 | 128.34 | No | Substation Equipment Exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-WT5 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 118.21 | 114.34 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT6 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#8668_659_SRT-A | 118.21 | 113.81 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT7 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#8668_659_SRT-A | 115.37 | 111.71 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT8 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 115.37 | 111.5 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT9 | 243579 | 05STROUD | 243835 | 05STRDREQ2 | 1 | 138/1.0 | 205 | 105 | 118 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 110.8 | 110.8 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 93 | 107 | N/A | N/A | 105 | 118 | N/A | N/A | 96 | 110 | N/A | N/A
Active | 2026-W1-N11-WT10 | 243579 | 05STROUD | 243835 | 05STRDREQ2 | 1 | 138/1.0 | 205 | 105 | 118 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 110.8 | 110.8 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 93 | 107 | N/A | N/A | 105 | 118 | N/A | N/A | 96 | 110 | N/A | N/A
Active | 2026-W1-N11-WT11 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#5858_13837_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 109.67 | 109.06 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT12 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#18473_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 107.41 | 106.81 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT13 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5858_13837_SRT-A | 109.67 | 106.29 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT14 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 110.09 | 106.21 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT15 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 107.14 | 106.12 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT16 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#8668_659_SRT-A | 110.09 | 105.67 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT17 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | DAY_P1_MILLCREEK_MEADOW_138KV_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 107.09 | 105.61 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT18 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#17431_SRT-A | AEP_P1-2_#6227_574_SRT-A | 105.26 | 105.14 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026-W1-N11-WT19 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#6227_574_SRT-A | AEP_P1-2_#17431_SRT-A | 105.26 | 104.66 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026-W1-N11-WT20 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#727_573_SRT-A | 104.2 | 104.28 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026-W1-N11-WT21 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#5784_654_SRT-A | Base Case | 108.06 | 104.26 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT22 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | ATSI_P1-2_OES-138-035B_SRT-A | 107.14 | 104.13 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT23 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#18473_SRT-A | 107.41 | 104.05 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT24 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#727_573_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 104.2 | 104.02 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026-W1-N11-WT25 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#5858_13837_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 104.51 | 103.9 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT26 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | DAY_P1_DARBY_MEADOW_138KV_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 104.37 | 103.83 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT27 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#8668_659_SRT-A | 107.23 | 103.55 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT28 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 107.23 | 103.35 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT29 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | DAY_P1_MILLCREEK_MEADOW_138KV_SRT-A | 107.09 | 103.35 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT30 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | Base Case | 103.63 | 102.51 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT31 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | Base Case | 106.02 | 102.14 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT32 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5858_13837_SRT-A | 104.51 | 101.86 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT33 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#18473_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 102.25 | 101.65 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT34 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | DAY_P1_DARBY_MEADOW_138KV_SRT-A | 104.37 | 101.65 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT35 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5784_654_SRT-A | 102.18 | 101.3 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT36 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 102.01 | 101 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026-W1-N11-WT37 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#17432_SRT-A | AEP_P1-2_#6227_574_SRT-A | 100.97 | 100.84 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026-W1-N11-WT38 | 238964 | 02MLCRK+ | 291044 | 09MEADOW | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 104.72 | 100.83 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT39 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#18125_SRT-A | Base Case | 101.47 | 100.64 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT40 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | DAY_P1_MILLCREEK_MEADOW_138KV_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 102.1 | 100.62 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT41 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 281 | 281 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#18125_SRT-A | 100.82 | 100.58 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026-W1-N11-WT42 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | Base Case | 102.81 | 100.51 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT43 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | Base Case | 102.81 | 100.51 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT44 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | 101.04 | 100.38 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026-W1-N11-WT45 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#6227_574_SRT-A | AEP_P1-2_#17432_SRT-A | 100.97 | 100.36 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026-W1-N11-WT46 | 238964 | 02MLCRK+ | 291044 | 09MEADOW | 1 | 138 | 202 | 180 | 228 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#8668_659_SRT-A | 104.72 | 100.28 | No | Substation Equipment Exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217

## Volt Mag
PJM N-1-1 Voltage Magnitude Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026-W1-N11-WVM1 | 235212 | 01LOYALH1 | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-138-052_SRT-A | AP_P1-3_WP-138-023_SRT-A | 0.97994 | 0.89926 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM2 | 235212 | 01LOYALH1 | 138 | 201 | 0.92 | 1.05 | AP_P1-3_WP-138-023_SRT-A | AP_P1-2_WP-138-052_SRT-A | 0.96937 | 0.89926 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM3 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5915_4306_SRT-A | AEP_P1-2_#16351_SRT-A | 0.98142 | 0.88003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM4 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5915_4306_SRT-A | AEP_P1-2_#16351_SRT-A | 0.98141 | 0.88003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM5 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.9749 | 0.81528 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM6 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.9749 | 0.81528 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM7 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 0.96688 | 0.81529 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM8 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 0.96689 | 0.81529 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM9 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#16352_SRT-A | 0.96688 | 0.86542 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM10 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#16352_SRT-A | 0.96689 | 0.86542 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM11 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5915_4306_SRT-A | 0.96688 | 0.88003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM12 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5915_4306_SRT-A | 0.96689 | 0.88003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM13 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16352_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97918 | 0.86541 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM14 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16352_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97917 | 0.86542 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM15 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99894 | 0.90412 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM16 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.005 | 0.90939 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM17 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0104 | 0.91207 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM18 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.9282 | 0.90376 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM19 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.9282 | 0.90431 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM20 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93369 | 0.90903 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM21 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93369 | 0.90959 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM22 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.937 | 0.91171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM23 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.937 | 0.91228 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM24 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.94153 | 0.91986 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM25 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99905 | 0.90466 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM26 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0052 | 0.90994 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM27 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0105 | 0.91262 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM28 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.89795 | 0.88912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM29 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.89795 | 0.88912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM30 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.89795 | 0.88912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM31 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.89795 | 0.89043 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM32 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.89795 | 0.89043 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM33 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.89795 | 0.89043 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM34 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.89795 | 0.89045 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM35 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.89795 | 0.89045 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM36 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.89795 | 0.89045 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM37 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.89795 | 0.89051 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM38 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.89795 | 0.89051 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM39 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.89795 | 0.89051 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM40 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.89795 | 0.89052 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM41 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.89795 | 0.89052 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM42 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.89795 | 0.89052 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM43 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.89961 | 0.89081 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM44 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.90072 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM45 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.90073 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM46 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.89961 | 0.89212 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM47 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.89961 | 0.89214 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM48 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.89961 | 0.8922 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM49 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.89961 | 0.89221 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM50 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.89968 | 0.89099 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM51 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.89968 | 0.89099 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM52 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.89968 | 0.891 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM53 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P12_000189_SRT-A | 0.89968 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM54 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P12_000189_SRT-A | 0.89968 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM55 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P12_000189_SRT-A | 0.89968 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM56 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P11_000840_SRT-A | 0.89968 | 0.8914 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM57 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P11_000840_SRT-A | 0.89968 | 0.8914 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM58 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P11_000840_SRT-A | 0.89968 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM59 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001449_SRT-A | 0.89968 | 0.89147 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM60 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001449_SRT-A | 0.89968 | 0.89147 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM61 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001449_SRT-A | 0.89968 | 0.89147 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM62 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001448_SRT-A | 0.89968 | 0.89148 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM63 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001448_SRT-A | 0.89968 | 0.89148 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM64 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001448_SRT-A | 0.89968 | 0.89148 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM65 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89968 | 0.89155 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM66 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89968 | 0.89155 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM67 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89968 | 0.89155 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM68 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.90133 | 0.89268 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM69 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89381 | 0.88912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM70 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89381 | 0.88912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM71 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89381 | 0.88912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM72 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89381 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM73 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89381 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM74 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89381 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM75 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89381 | 0.88948 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM76 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89381 | 0.88948 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM77 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89381 | 0.88948 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM78 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89381 | 0.88999 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM79 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89381 | 0.88999 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM80 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89381 | 0.88999 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM81 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89381 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM82 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89381 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM83 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89381 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM84 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89548 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM85 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89548 | 0.89092 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM86 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89548 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM87 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89381 | 0.89128 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM88 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89381 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM89 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89381 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM90 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_100842_SRT-A | 0.89381 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM91 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_100842_SRT-A | 0.89381 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM92 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_100842_SRT-A | 0.89381 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM93 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081_SRT-A | 0.89381 | 0.89142 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM94 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081_SRT-A | 0.89381 | 0.89142 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM95 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081_SRT-A | 0.89381 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM96 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_103307_SRT-A | 0.89381 | 0.89159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM97 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_103307_SRT-A | 0.89381 | 0.89159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM98 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_103307_SRT-A | 0.89381 | 0.89159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM99 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446A_SRT-A | 0.89381 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM100 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446A_SRT-A | 0.89381 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM101 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446A_SRT-A | 0.89381 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM102 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89548 | 0.89168 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM103 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89548 | 0.89184 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM104 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.8966 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM105 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89661 | 0.89195 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM106 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.8966 | 0.89205 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM107 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89661 | 0.89205 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM108 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.8966 | 0.8923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM109 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89661 | 0.8923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM110 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.8966 | 0.8928 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM111 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89661 | 0.89281 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM112 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_000793_SRT-A | 0.89548 | 0.8929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM113 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89548 | 0.89294 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM114 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001447_SRT-A | 0.89548 | 0.89296 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM115 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446_SRT-A | 0.89548 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM116 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.8966 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM117 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89661 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM118 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89548 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM119 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P12_000189_SRT-A | 0.90064 | 0.89168 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM120 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P12_000189_SRT-A | 0.90064 | 0.89168 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM121 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P12_000189_SRT-A | 0.90064 | 0.89168 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM122 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P11_000840_SRT-A | 0.90064 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM123 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P11_000840_SRT-A | 0.90064 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM124 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P11_000840_SRT-A | 0.90064 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM125 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001449_SRT-A | 0.90064 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM126 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001449_SRT-A | 0.90064 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM127 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001449_SRT-A | 0.90064 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM128 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001448_SRT-A | 0.90064 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM129 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001448_SRT-A | 0.90064 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM130 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001448_SRT-A | 0.90064 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM131 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90064 | 0.89179 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM132 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90064 | 0.89179 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM133 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90064 | 0.89179 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM134 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.89993 | 0.89106 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM135 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.89993 | 0.89106 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM136 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.89993 | 0.89106 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM137 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.89107 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM138 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.89107 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM139 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.89107 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM140 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.89993 | 0.89113 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM141 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.89993 | 0.89113 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM142 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.89993 | 0.89113 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM143 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.89993 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM144 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.89993 | 0.89116 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM145 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.89993 | 0.89116 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM146 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89993 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM147 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89993 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM148 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89993 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM149 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.90158 | 0.89275 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM150 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.90158 | 0.89276 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM151 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.90158 | 0.89282 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM152 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.90158 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM153 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90158 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM154 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89383 | 0.89001 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM155 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89383 | 0.89001 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM156 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89383 | 0.89001 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM157 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89383 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM158 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89383 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM159 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89383 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM160 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89383 | 0.89042 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM161 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89383 | 0.89042 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM162 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89383 | 0.89042 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM163 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89383 | 0.89046 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM164 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89383 | 0.89046 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM165 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89383 | 0.89046 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM166 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89383 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM167 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89383 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM168 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89383 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM169 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89383 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM170 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89383 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM171 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89383 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM172 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89383 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM173 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89383 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM174 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89383 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM175 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_100842_SRT-A | 0.89383 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM176 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_100842_SRT-A | 0.89383 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM177 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_100842_SRT-A | 0.89383 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM178 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_103307_SRT-A | 0.89383 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM179 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_103307_SRT-A | 0.89383 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM180 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_103307_SRT-A | 0.89383 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM181 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446A_SRT-A | 0.89383 | 0.89168 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM182 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446A_SRT-A | 0.89383 | 0.89168 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM183 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446A_SRT-A | 0.89383 | 0.89168 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM184 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89551 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM185 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89551 | 0.89191 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM186 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89551 | 0.89211 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM187 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89551 | 0.89215 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM188 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89662 | 0.89283 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM189 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89663 | 0.89283 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM190 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89551 | 0.89292 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM191 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89551 | 0.89296 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM192 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001447_SRT-A | 0.89551 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM193 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89551 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM194 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89551 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM195 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89821 | 0.88799 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM196 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89821 | 0.88799 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM197 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89821 | 0.88799 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM198 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89986 | 0.88969 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM199 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.90098 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM200 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.90098 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM201 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_48_P13_001557_SRT-A | 0.89821 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM202 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_48_P13_001557_SRT-A | 0.89821 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM203 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_48_P13_001557_SRT-A | 0.89821 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM204 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89779 | 0.88895 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM205 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89779 | 0.88895 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM206 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89779 | 0.88895 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM207 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89779 | 0.89002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM208 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89779 | 0.89003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM209 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89779 | 0.89003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM210 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89779 | 0.89005 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM211 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89779 | 0.89005 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM212 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89779 | 0.89005 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM213 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89779 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM214 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89779 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM215 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89779 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM216 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89779 | 0.89012 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM217 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89779 | 0.89012 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM218 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89779 | 0.89012 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM219 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89779 | 0.89018 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM220 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89779 | 0.89018 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM221 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89779 | 0.89018 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM222 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89944 | 0.89065 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM223 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89944 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM224 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89944 | 0.89174 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM225 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.90056 | 0.89177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM226 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.90056 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM227 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89944 | 0.8918 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM228 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89944 | 0.89181 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM229 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89944 | 0.89187 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM230 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.90056 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM231 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.90056 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM232 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.90056 | 0.89286 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM233 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.90056 | 0.89287 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM234 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.90056 | 0.89292 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM235 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.90056 | 0.89292 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM236 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.90056 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM237 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.90056 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM238 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90056 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM239 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90056 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM240 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.89999 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM241 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.89999 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM242 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.89999 | 0.89116 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM243 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.89999 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM244 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.89999 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM245 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.89999 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM246 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.89999 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM247 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.89999 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM248 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.89999 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM249 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.89999 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM250 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.89999 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM251 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.89999 | 0.89123 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM252 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89999 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM253 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89999 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM254 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89999 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM255 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.90164 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM256 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.90164 | 0.89289 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM257 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.90164 | 0.89291 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM258 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.90164 | 0.89291 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM259 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.89997 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM260 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.89997 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM261 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.89997 | 0.89116 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM262 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.89997 | 0.8912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM263 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.89997 | 0.8912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM264 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.89997 | 0.8912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM265 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.89997 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM266 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.89997 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM267 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.89997 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM268 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.89997 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM269 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.89997 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM270 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.89997 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM271 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89997 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM272 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89997 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM273 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89997 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM274 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.90162 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM275 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.90162 | 0.89289 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM276 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.90162 | 0.89291 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM277 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.90162 | 0.89291 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM278 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.8939 | 0.89008 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM279 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.8939 | 0.89008 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM280 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.8939 | 0.89008 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM281 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.8939 | 0.89026 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM282 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.8939 | 0.89026 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM283 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.8939 | 0.89026 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM284 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.8939 | 0.89028 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM285 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.8939 | 0.89028 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM286 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.8939 | 0.89028 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM287 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.8939 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM288 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.8939 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM289 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.8939 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM290 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.8939 | 0.89053 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM291 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.8939 | 0.89053 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM292 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.8939 | 0.89053 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM293 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.8939 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM294 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.8939 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM295 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.8939 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM296 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446_SRT-A | 0.8939 | 0.89139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM297 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446_SRT-A | 0.8939 | 0.89139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM298 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446_SRT-A | 0.8939 | 0.89139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM299 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_100842_SRT-A | 0.8939 | 0.89146 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM300 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_100842_SRT-A | 0.8939 | 0.89146 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM301 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_100842_SRT-A | 0.8939 | 0.89146 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM302 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_103307_SRT-A | 0.8939 | 0.89167 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM303 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_103307_SRT-A | 0.8939 | 0.89167 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM304 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_103307_SRT-A | 0.8939 | 0.89167 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM305 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446A_SRT-A | 0.8939 | 0.89176 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM306 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446A_SRT-A | 0.8939 | 0.89176 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM307 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446A_SRT-A | 0.8939 | 0.89176 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM308 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89557 | 0.89177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM309 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.89557 | 0.89195 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM310 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.89557 | 0.89197 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM311 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.89557 | 0.89218 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM312 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.89557 | 0.89222 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM313 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_000793_SRT-A | 0.89557 | 0.89282 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM314 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89669 | 0.89289 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM315 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.8967 | 0.8929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM316 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_001447_SRT-A | 0.89557 | 0.89292 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM317 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_001446_SRT-A | 0.89557 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM318 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89389 | 0.89007 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM319 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89389 | 0.89007 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM320 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89389 | 0.89007 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM321 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89389 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM322 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89389 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM323 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89389 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM324 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89389 | 0.89027 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM325 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89389 | 0.89027 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM326 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89389 | 0.89027 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM327 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89389 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM328 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89389 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM329 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89389 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM330 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89389 | 0.89053 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM331 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89389 | 0.89053 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM332 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89389 | 0.89053 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM333 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89389 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM334 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89389 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM335 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89389 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM336 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_100842_SRT-A | 0.89389 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM337 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_100842_SRT-A | 0.89389 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM338 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_100842_SRT-A | 0.89389 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM339 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446_SRT-A | 0.89389 | 0.89139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM340 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446_SRT-A | 0.89389 | 0.89139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM341 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446_SRT-A | 0.89389 | 0.89139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM342 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_103307_SRT-A | 0.89389 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM343 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_103307_SRT-A | 0.89389 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM344 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_103307_SRT-A | 0.89389 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM345 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446A_SRT-A | 0.89389 | 0.89175 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM346 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446A_SRT-A | 0.89389 | 0.89175 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM347 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446A_SRT-A | 0.89389 | 0.89175 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM348 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89556 | 0.89176 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM349 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89556 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM350 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89556 | 0.89196 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM351 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89556 | 0.89217 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM352 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89556 | 0.89221 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM353 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_000793_SRT-A | 0.89556 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM354 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89668 | 0.89288 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM355 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89669 | 0.89289 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM356 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_001446_SRT-A | 0.89556 | 0.89292 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM357 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_001447_SRT-A | 0.89556 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM358 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89695 | 0.89017 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM359 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89695 | 0.89017 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM360 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89695 | 0.89017 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM361 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89695 | 0.89019 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM362 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89695 | 0.89019 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM363 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89695 | 0.89019 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM364 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89695 | 0.8903 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM365 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89695 | 0.8903 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM366 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89695 | 0.8903 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM367 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89695 | 0.89031 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM368 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89695 | 0.89031 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM369 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89695 | 0.89031 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM370 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89695 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM371 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89695 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM372 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89695 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM373 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100411_SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM374 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100411_SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM375 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100411_SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM376 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_000870_SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM377 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM378 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_000870_SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM379 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM380 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_000870_SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM381 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89695 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM382 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89861 | 0.89186 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM383 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89861 | 0.89188 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM384 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89861 | 0.89199 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM385 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89861 | 0.892 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM386 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P13_100388_SRT-A | 0.89695 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM387 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P13_100388_SRT-A | 0.89695 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM388 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P13_100388_SRT-A | 0.89695 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM389 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89861 | 0.8929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM390 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89973 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM391 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89973 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM392 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.89977 | 0.88836 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM393 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.89977 | 0.88837 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM394 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.89977 | 0.88837 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM395 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.90142 | 0.89006 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM396 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.90253 | 0.89119 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM397 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.90253 | 0.89119 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM398 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.89962 | 0.88846 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM399 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.89962 | 0.88846 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM400 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.89963 | 0.88846 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM401 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.90128 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM402 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.90238 | 0.89128 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM403 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.90239 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM404 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_48_P13_001557_SRT-A | 0.89962 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM405 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_48_P13_001557_SRT-A | 0.89962 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM406 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_48_P13_001557_SRT-A | 0.89963 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM407 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89822 | 0.88929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM408 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89822 | 0.88929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM409 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89823 | 0.88929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM410 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89822 | 0.89081 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM411 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89822 | 0.89081 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM412 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89823 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM413 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89988 | 0.89099 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM414 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.90099 | 0.89211 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM415 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.90099 | 0.89212 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM416 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89988 | 0.8925 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM417 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.89799 | 0.88765 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM418 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.89799 | 0.88765 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM419 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.898 | 0.88765 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM420 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.89799 | 0.88927 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM421 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.89799 | 0.88927 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM422 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.898 | 0.88927 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM423 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.89965 | 0.88935 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM424 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.90076 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM425 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.90077 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM426 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.89965 | 0.89096 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM427 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.89799 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM428 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.89799 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM429 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.898 | 0.89121 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM430 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.90076 | 0.89209 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM431 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.90077 | 0.89209 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM432 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.89965 | 0.89289 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM433 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.89871 | 0.88785 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM434 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.89871 | 0.88785 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM435 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.89871 | 0.88785 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM436 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.89871 | 0.88952 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM437 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.89871 | 0.88952 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM438 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.89871 | 0.88952 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM439 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.90037 | 0.88955 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM440 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.90148 | 0.89068 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM441 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.90148 | 0.89068 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM442 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.90037 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM443 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P13_001557_SRT-A | 0.89871 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM444 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P13_001557_SRT-A | 0.89871 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM445 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P13_001557_SRT-A | 0.89871 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM446 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.90148 | 0.89234 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM447 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.90148 | 0.89235 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM448 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P12_000189_SRT-A | 0.9009 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM449 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P12_000189_SRT-A | 0.9009 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM450 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P12_000189_SRT-A | 0.9009 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM451 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P11_000840_SRT-A | 0.9009 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM452 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P11_000840_SRT-A | 0.9009 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM453 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P11_000840_SRT-A | 0.9009 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM454 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001449_SRT-A | 0.9009 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM455 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001448_SRT-A | 0.9009 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM456 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001449_SRT-A | 0.9009 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM457 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001448_SRT-A | 0.9009 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM458 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001449_SRT-A | 0.9009 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM459 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001448_SRT-A | 0.9009 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM460 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9009 | 0.8915 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM461 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9009 | 0.89151 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM462 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9009 | 0.89151 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM463 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P12_000189_SRT-A | 0.90092 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM464 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P12_000189_SRT-A | 0.90092 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM465 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P12_000189_SRT-A | 0.90092 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM466 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001449_SRT-A | 0.90092 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM467 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001449_SRT-A | 0.90092 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM468 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P11_000840_SRT-A | 0.90092 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM469 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001449_SRT-A | 0.90092 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM470 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P11_000840_SRT-A | 0.90092 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM471 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P11_000840_SRT-A | 0.90092 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM472 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001448_SRT-A | 0.90092 | 0.89149 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM473 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001448_SRT-A | 0.90092 | 0.89149 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM474 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001448_SRT-A | 0.90092 | 0.8915 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM475 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90092 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM476 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90092 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM477 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90092 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM478 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100410_SRT-A | 0.89398 | 0.88935 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM479 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100411_SRT-A | 0.89398 | 0.88955 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM480 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P11_000870_SRT-A | 0.89398 | 0.88969 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM481 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89398 | 0.88969 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM482 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_103484_SRT-A | 0.89398 | 0.88977 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM483 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P13_100388_SRT-A | 0.89398 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM484 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100410_SRT-A | 0.8951 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM485 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100410_SRT-A | 0.8951 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM486 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P14_001171_SRT-A | 0.89398 | 0.89065 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM487 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100411_SRT-A | 0.8951 | 0.89068 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM488 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100411_SRT-A | 0.8951 | 0.89068 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM489 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_000002_SRT-A | 0.89398 | 0.89081 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM490 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P11_000870_SRT-A | 0.8951 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM491 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.8951 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM492 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P11_000870_SRT-A | 0.8951 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM493 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.8951 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM494 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_103484_SRT-A | 0.8951 | 0.8909 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM495 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_103484_SRT-A | 0.8951 | 0.8909 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM496 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100404_SRT-A | 0.89398 | 0.89099 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM497 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P12_103307_SRT-A | 0.89398 | 0.89109 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM498 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P13_100388_SRT-A | 0.8951 | 0.89128 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM499 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P13_100388_SRT-A | 0.8951 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM500 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P14_001171_SRT-A | 0.8951 | 0.89177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM501 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P14_001171_SRT-A | 0.8951 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM502 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_000002_SRT-A | 0.8951 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM503 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_000002_SRT-A | 0.8951 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM504 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100404_SRT-A | 0.8951 | 0.89211 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM505 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100404_SRT-A | 0.8951 | 0.89212 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM506 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P12_103307_SRT-A | 0.8951 | 0.89221 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM507 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P12_103307_SRT-A | 0.8951 | 0.89222 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM508 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | Base Case | 0.8923 | - | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM509 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | Base Case | 0.8923 | - | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM510 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | Base Case | 0.8923 | - | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM511 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89831 | 0.88939 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM512 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89831 | 0.88939 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM513 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89831 | 0.88939 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM514 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89997 | 0.89108 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM515 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P12_000189_SRT-A | 0.89831 | 0.89162 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM516 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P12_000189_SRT-A | 0.89831 | 0.89162 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM517 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P12_000189_SRT-A | 0.89831 | 0.89162 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM518 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P11_000840_SRT-A | 0.89831 | 0.89164 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM519 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P11_000840_SRT-A | 0.89831 | 0.89164 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM520 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P11_000840_SRT-A | 0.89831 | 0.89164 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM521 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89831 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM522 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89831 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM523 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89831 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM524 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001449_SRT-A | 0.89831 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM525 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001449_SRT-A | 0.89831 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM526 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001449_SRT-A | 0.89831 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM527 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001448_SRT-A | 0.89831 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM528 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001448_SRT-A | 0.89831 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM529 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001448_SRT-A | 0.89831 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM530 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.90108 | 0.89221 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM531 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.90108 | 0.89221 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM532 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89692 | 0.88807 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM533 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89692 | 0.88807 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM534 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89692 | 0.88807 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM535 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89692 | 0.88909 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM536 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89692 | 0.88909 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM537 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89692 | 0.88909 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM538 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89858 | 0.88977 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM539 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89858 | 0.89078 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM540 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89969 | 0.8909 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM541 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.8997 | 0.8909 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM542 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89969 | 0.89191 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM543 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.8997 | 0.89191 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM544 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.006 | 0.92735 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM545 | 314613 | 3TRWBRDG | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0057 | 0.92776 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM546 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 168_SRT-A | 1.0079 | 0.91942 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM547 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 167_SRT-A | 1.0079 | 0.91946 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM548 | 314614 | 3TRWBRDG2 | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 168_SRT-A | 1.0082 | 0.92277 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM549 | 314614 | 3TRWBRDG2 | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 167_SRT-A | 1.0082 | 0.92281 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM550 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0079 | 0.92705 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM551 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 1.0079 | 0.92705 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM552 | 314613 | 3TRWBRDG | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0107 | 0.92745 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM553 | 314613 | 3TRWBRDG | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 1.0107 | 0.92745 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM554 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99794 | 0.90937 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM555 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0052 | 0.91588 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM556 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0117 | 0.91993 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM557 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.9 | 0.89125 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM558 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.9 | 0.89125 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM559 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.9 | 0.89125 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM560 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.9 | 0.89127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM561 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.9 | 0.89127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM562 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.9 | 0.89127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM563 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001449_SRT-A | 0.9 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM564 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001449_SRT-A | 0.9 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM565 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001449_SRT-A | 0.9 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM566 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001448_SRT-A | 0.9 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM567 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001448_SRT-A | 0.9 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM568 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001448_SRT-A | 0.9 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM569 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM570 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM571 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM572 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.90165 | 0.89294 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM573 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.90165 | 0.89296 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM574 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.89409 | 0.89027 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM575 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.89409 | 0.89027 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM576 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.8941 | 0.89027 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM577 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446_SRT-A | 0.89409 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM578 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446_SRT-A | 0.89409 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM579 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446_SRT-A | 0.8941 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM580 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_100842_SRT-A | 0.89409 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM581 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_100842_SRT-A | 0.89409 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM582 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_100842_SRT-A | 0.8941 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM583 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_000793_SRT-A | 0.89409 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM584 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_000793_SRT-A | 0.89409 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM585 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_000793_SRT-A | 0.8941 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM586 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89409 | 0.89175 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM587 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89409 | 0.89175 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM588 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.8941 | 0.89175 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM589 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001447_SRT-A | 0.89409 | 0.89177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM590 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001447_SRT-A | 0.89409 | 0.89177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM591 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001447_SRT-A | 0.8941 | 0.89177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM592 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001446_SRT-A | 0.89409 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM593 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001446_SRT-A | 0.89409 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM594 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001446_SRT-A | 0.8941 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM595 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_103307_SRT-A | 0.89409 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM596 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_103307_SRT-A | 0.89409 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM597 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_103307_SRT-A | 0.8941 | 0.89178 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM598 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.89577 | 0.89196 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM599 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446A_SRT-A | 0.89409 | 0.89199 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM600 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446A_SRT-A | 0.89409 | 0.89199 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM601 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446A_SRT-A | 0.8941 | 0.89199 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM602 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89821 | 0.88799 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM603 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89821 | 0.88799 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM604 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89821 | 0.88799 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM605 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89986 | 0.88969 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM606 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.90098 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM607 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.90098 | 0.89082 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM608 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_48_P13_001557_SRT-A | 0.89821 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM609 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_48_P13_001557_SRT-A | 0.89821 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM610 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_48_P13_001557_SRT-A | 0.89821 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM611 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.89983 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM612 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.89983 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM613 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.89983 | 0.89012 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM614 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.89983 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM615 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.89983 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM616 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.89983 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM617 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.89983 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM618 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.89983 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM619 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.89983 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM620 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.89983 | 0.89101 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM621 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.89983 | 0.89101 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM622 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.89983 | 0.89101 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM623 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.90148 | 0.8918 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM624 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.90148 | 0.8919 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM625 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.90148 | 0.89191 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM626 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.90148 | 0.8927 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM627 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.90259 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM628 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.90259 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM629 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.89845 | 0.89047 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM630 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.89845 | 0.89047 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM631 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.89845 | 0.89047 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM632 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.89845 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM633 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.89845 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM634 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.89845 | 0.89049 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM635 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.89845 | 0.89055 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM636 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.89845 | 0.89055 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM637 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.89845 | 0.89055 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM638 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.89845 | 0.89056 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM639 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.89845 | 0.89056 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM640 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.89845 | 0.89056 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM641 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.90011 | 0.89216 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM642 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.90011 | 0.89218 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM643 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.90011 | 0.89223 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM644 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.90011 | 0.89224 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM645 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.006 | 0.92735 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVM646 | 314613 | 3TRWBRDG | 115 | 345 | 0.93 | 1.05 | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0057 | 0.92776 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM646 | 314677 | 6BUCKING | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0009 | 0.87097 | Yes
Active | 2026W1-N11-WVM647 | 316322 | AB2-045 | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0009 | 0.87097 | Yes
Active | 2026W1-N11-WVM648 | 971844 | AH1-439_POI | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0006 | 0.87106 | Yes
Active | 2026W1-N11-WVM649 | 82745 | AH1-439_MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0006 | 0.87106 | Yes
Active | 2026W1-N11-WVM650 | 314692 | 6FARMVIL | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.9994 | 0.87144 | Yes
Active | 2026W1-N11-WVM651 | 972002 | AH1-546_POI | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.87152 | Yes
Active | 2026W1-N11-WVM652 | 82920 | AH1-546_MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.87154 | Yes
Active | 2026W1-N11-WVM653 | 314691 | 3FARMVIL | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0013 | 0.877 | Yes
Active | 2026W1-N11-WVM654 | 314719 | 3S CREEK | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.98545 | 0.87748 | Yes
Active | 2026W1-N11-WVM655 | 313127 | 3CURDSVILLE | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99903 | 0.87901 | Yes
Active | 2026W1-N11-WVM656 | 314726 | 3WILLIS | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99998 | 0.88012 | Yes
Active | 2026W1-N11-WVM657 | 315822 | AE2-259_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99999 | 0.88013 | Yes
Active | 2026W1-N11-WVM658 | 314664 | 3REDH DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99219 | 0.88516 | Yes
Active | 2026W1-N11-WVM659 | 314663 | 3REDH TP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99235 | 0.88533 | Yes
Active | 2026W1-N11-WVM660 | 314707 | 3MORAN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0019 | 0.88759 | Yes
Active | 2026W1-N11-WVM661 | 314521 | 3PAMPL_1 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99541 | 0.88888 | Yes
Active | 2026W1-N11-WVM662 | 314713 | 3PAMPLIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99541 | 0.88888 | Yes
Active | 2026W1-N11-WVM663 | 314426 | 3FT PKET | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99963 | 0.89102 | Yes
Active | 2026W1-N11-WVM664 | 313156 | 3FT PIC DT T | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99964 | 0.89103 | Yes
Active | 2026W1-N11-WVM665 | 313755 | 3FLAT CREEK | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0049 | 0.89447 | Yes
Active | 2026W1-N11-WVM666 | 314429 | 3JTRSVLE | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0073 | 0.8995 | Yes
Active | 2026W1-N11-WVM667 | 314428 | 3HOOPERS | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.8995 | Yes
Active | 2026W1-N11-WVM668 | 314701 | 3LONEPN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.89957 | Yes
Active | 2026W1-N11-WVM669 | 314687 | 3CREWE | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.89971 | Yes
Active | 2026W1-N11-WVM670 | 314715 | 3MADSONV | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99905 | 0.89971 | Yes
Active | 2026W1-N11-WVM671 | 314519 | 3LONEPINE_1 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0076 | 0.90002 | Yes
Active | 2026W1-N11-WVM672 | 313853 | 3PONTONDP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0084 | 0.90058 | Yes
Active | 2026W1-N11-WVM673 | 313462 | 3AF1-294 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0085 | 0.90061 | Yes
Active | 2026W1-N11-WVM674 | 319063 | AF1-294_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0086 | 0.9007 | Yes
Active | 2026W1-N11-WVM675 | 314432 | 3MARTIN DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0074 | 0.90788 | Yes
Active | 2026W1-N11-WVM676 | 314706 | 3MARTIN TAP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0074 | 0.90793 | Yes
Active | 2026W1-N11-WVM677 | 970681 | AG2-440_POI | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0045 | 0.91639 | Yes
Active | 2026W1-N11-WVM678 | 81065 | AG2-440_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0046 | 0.91643 | Yes
Active | 2026W1-N11-WVM679 | 81080 | AG2-442_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0048 | 0.91662 | Yes
Active | 2026W1-N11-WVM680 | 313281 | 3VICTORIA DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0077 | 0.91931 | Yes
Active | 2026W1-N11-WVM681 | 314725 | 3VICTORIA TP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0078 | 0.91938 | Yes
Active | 2026W1-N11-WVM682 | 314723 | 3VICTRIA | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.008 | 0.92379 | Yes
Active | 2026W1-N11-WVM683 | 314719 | 3S CREEK | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 298_SRT-A | 0.98545 | 0.92695 | Yes
Active | 2026W1-N11-WVM684 | 313460 | 3BIRDSBRANCH | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0072 | 0.927 | Yes
Active | 2026W1-N11-WVM685 | 319088 | AF2-222_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0073 | 0.92701 | Yes
Active | 2026W1-N11-WVM686 | 314710 | 3NUTBUSH | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0077 | 0.92787 | Yes
Active | 2026W1-N11-WVM687 | 314695 | 3GARY DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.008 | 0.92806 | Yes
Active | 2026W1-N11-WVM688 | 971775 | AH1-396 GEN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.008 | 0.92806 | Yes
Active | 2026W1-N11-WVM689 | 314430 | 3KENBRDG | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0081 | 0.92819 | Yes
Active | 2026W1-N11-WVM690 | 970322 | AG2-213_POI | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0082 | 0.92827 | Yes
Active | 2026W1-N11-WVM691 | 314431 | 3KENB TP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0082 | 0.92829 | Yes
Active | 2026W1-N11-WVM692 | 970256 | AG2-171_POI | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0081 | 0.9283 | Yes
Active | 2026W1-N11-WVM693 | 80369 | AG2-171_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0081 | 0.9283 | Yes
Active | 2026W1-N11-WVM694 | 80472 | AG2-213_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0082 | 0.92833 | Yes
Active | 2026W1-N11-WVM695 | 314427 | 3LUNENBURG | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0083 | 0.92846 | Yes
Active | 2026W1-N11-WVM696 | 314677 | 6BUCKING | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.87097 | Yes
Active | 2026W1-N11-WVM697 | 316322 | AB2-045 | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.87097 | Yes
Active | 2026W1-N11-WVM698 | 971844 | AH1-439_POI | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.87106 | Yes
Active | 2026W1-N11-WVM699 | 82745 | AH1-439_MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.87106 | Yes
Active | 2026W1-N11-WVM700 | 314692 | 6FARMVIL | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0079 | 0.87144 | Yes
Active | 2026W1-N11-WVM701 | 972002 | AH1-546_POI | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0082 | 0.87152 | Yes
Active | 2026W1-N11-WVM702 | 82920 | AH1-546_MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0082 | 0.87154 | Yes
Active | 2026W1-N11-WVM703 | 314691 | 3FARMVIL | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0085 | 0.877 | Yes
Active | 2026W1-N11-WVM704 | 314719 | 3S CREEK | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 0.99092 | 0.87748 | Yes
Active | 2026W1-N11-WVM705 | 313127 | 3CURDSVILLE | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0058 | 0.87901 | Yes
Active | 2026W1-N11-WVM706 | 314726 | 3WILLIS | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0067 | 0.88012 | Yes
Active | 2026W1-N11-WVM707 | 315822 | AE2-259_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0067 | 0.88013 | Yes
Active | 2026W1-N11-WVM708 | 314664 | 3REDH DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 0.99761 | 0.88516 | Yes
Active | 2026W1-N11-WVM709 | 314663 | 3REDH TP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 0.99777 | 0.88533 | Yes
Active | 2026W1-N11-WVM710 | 314707 | 3MORAN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.008 | 0.88759 | Yes
Active | 2026W1-N11-WVM711 | 314521 | 3PAMPL_1 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0008 | 0.88888 | Yes
Active | 2026W1-N11-WVM712 | 314713 | 3PAMPLIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0008 | 0.88888 | Yes
Active | 2026W1-N11-WVM713 | 314426 | 3FT PKET | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0048 | 0.89102 | Yes
Active | 2026W1-N11-WVM714 | 313156 | 3FT PIC DT T | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0048 | 0.89103 | Yes
Active | 2026W1-N11-WVM715 | 313755 | 3FLAT CREEK | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0104 | 0.89447 | Yes
Active | 2026W1-N11-WVM716 | 314429 | 3JTRSVLE | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0124 | 0.8995 | Yes
Active | 2026W1-N11-WVM717 | 314428 | 3HOOPERS | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0122 | 0.8995 | Yes
Active | 2026W1-N11-WVM718 | 314701 | 3LONEPN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0122 | 0.89957 | Yes
Active | 2026W1-N11-WVM719 | 314687 | 3CREWE | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0122 | 0.89971 | Yes
Active | 2026W1-N11-WVM720 | 314715 | 3MADSONV | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0039 | 0.89971 | Yes
Active | 2026W1-N11-WVM721 | 314519 | 3LONEPINE_1 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0127 | 0.90002 | Yes
Active | 2026W1-N11-WVM722 | 313853 | 3PONTONDP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0135 | 0.90058 | Yes
Active | 2026W1-N11-WVM723 | 313462 | 3AF1-294 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0136 | 0.90061 | Yes
Active | 2026W1-N11-WVM724 | 319063 | AF1-294_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0136 | 0.9007 | Yes
Active | 2026W1-N11-WVM725 | 314432 | 3MARTIN DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0119 | 0.90788 | Yes
Active | 2026W1-N11-WVM726 | 314706 | 3MARTIN TAP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.012 | 0.90793 | Yes
Active | 2026W1-N11-WVM727 | 970681 | AG2-440_POI | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0086 | 0.91639 | Yes
Active | 2026W1-N11-WVM728 | 81065 | AG2-440_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0087 | 0.91643 | Yes
Active | 2026W1-N11-WVM729 | 81080 | AG2-442_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0089 | 0.91662 | Yes
Active | 2026W1-N11-WVM730 | 313281 | 3VICTORIA DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.91931 | Yes
Active | 2026W1-N11-WVM731 | 314725 | 3VICTORIA TP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0118 | 0.91938 | Yes
Active | 2026W1-N11-WVM732 | 314723 | 3VICTRIA | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.92379 | Yes
Active | 2026W1-N11-WVM733 | 313460 | 3BIRDSBRANCH | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0109 | 0.927 | Yes
Active | 2026W1-N11-WVM734 | 319088 | AF2-222_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0109 | 0.92701 | Yes
Active | 2026W1-N11-WVM735 | 314710 | 3NUTBUSH | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0112 | 0.92787 | Yes
Active | 2026W1-N11-WVM736 | 314695 | 3GARY DP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0115 | 0.92806 | Yes
Active | 2026W1-N11-WVM737 | 971775 | AH1-396 GEN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0115 | 0.92806 | Yes
Active | 2026W1-N11-WVM738 | 314430 | 3KENBRDG | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0116 | 0.92819 | Yes
Active | 2026W1-N11-WVM739 | 970322 | AG2-213_POI | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.92827 | Yes
Active | 2026W1-N11-WVM740 | 314431 | 3KENB TP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.92829 | Yes
Active | 2026W1-N11-WVM741 | 970256 | AG2-171_POI | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0116 | 0.9283 | Yes
Active | 2026W1-N11-WVM742 | 80369 | AG2-171_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0116 | 0.9283 | Yes
Active | 2026W1-N11-WVM743 | 80472 | AG2-213_MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.92833 | Yes
Active | 2026W1-N11-WVM744 | 314427 | 3LUNENBURG | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.92846 | Yes

## Volt Drop
PJM N-1-1 Voltage Drop Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | % Vdrop | Contingency 1 | Contingency 2 | BaseVolt | ContVolt | % Vdrop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2026-W1-N11-WVD1 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#5915_4306_SRT-A | AEP_P1-2_#16351_SRT-A | 0.98142 | 0.88002 | 10.14 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD2 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#5915_4306_SRT-A | AEP_P1-2_#16351_SRT-A | 0.98141 | 0.88002 | 10.139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD3 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.9749 | 0.81556 | 15.935 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD4 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.9749 | 0.81556 | 15.934 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD5 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 0.96688 | 0.81227 | 15.461 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD6 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 0.96689 | 0.81227 | 15.462 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD7 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#16352_SRT-A | 0.96688 | 0.86559 | 10.13 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD8 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#16352_SRT-A | 0.96689 | 0.86559 | 10.13 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD9 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5915_4306_SRT-A | 0.96688 | 0.87994 | 8.695 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD10 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5915_4306_SRT-A | 0.96689 | 0.87994 | 8.695 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD11 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#16352_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97918 | 0.86599 | 11.319 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD12 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#16352_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97917 | 0.86599 | 11.318 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD13 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.006 | 0.88309 | 12.29 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD14 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0057 | 0.8833 | 12.238 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD15 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0094 | 0.88622 | 12.322 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD16 | 313228 | 3PANTEGO DP | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 0.99279 | 0.89147 | 10.133 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD17 | 314592 | 3PANTEGO | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 0.99285 | 0.89152 | 10.132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD18 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0079 | 0.88307 | 12.487 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD19 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 1.0079 | 0.88307 | 12.487 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD20 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0107 | 0.88327 | 12.745 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD21 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 1.0107 | 0.88327 | 12.745 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD22 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0082 | 0.8862 | 12.203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD23 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 1.0082 | 0.8862 | 12.203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD24 | 313228 | 3PANTEGO DP | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 0.99632 | 0.89145 | 10.487 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD25 | 313228 | 3PANTEGO DP | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 0.99632 | 0.89145 | 10.487 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD26 | 314592 | 3PANTEGO | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 0.99637 | 0.8915 | 10.487 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD27 | 314592 | 3PANTEGO | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 0.99637 | 0.8915 | 10.487 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD28 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 168_SRT-A | 1.0079 | 0.89676 | 11.117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD29 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 167_SRT-A | 1.0079 | 0.89681 | 11.113 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD30 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 168_SRT-A | 1.0082 | 0.90006 | 10.817 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-WVD31 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-2: LN 167_SRT-A | 1.0082 | 0.9001 | 10.813 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVD32 | 314677 | 6BUCKING | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0009 | 0.85187 | 14.905 | Yes
Active | 2026W1-N11-WVD33 | 316322 | AB2-045 | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0009 | 0.85187 | 14.905 | Yes
Active | 2026W1-N11-WVD34 | 971844 | AH1-439_POI | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0006 | 0.85196 | 14.868 | Yes
Active | 2026W1-N11-WVD35 | 82745 | AH1-439_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0006 | 0.85197 | 14.868 | Yes
Active | 2026W1-N11-WVD36 | 314692 | 6FARMVIL | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.9994 | 0.85236 | 14.704 | Yes
Active | 2026W1-N11-WVD37 | 972002 | AH1-546_POI | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.85241 | 15.467 | Yes
Active | 2026W1-N11-WVD38 | 82920 | AH1-546_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.85242 | 15.467 | Yes
Active | 2026W1-N11-WVD39 | 314691 | 3FARMVIL | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0013 | 0.8582 | 14.31 | Yes
Active | 2026W1-N11-WVD40 | 314719 | 3S CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.98545 | 0.85902 | 12.643 | Yes
Active | 2026W1-N11-WVD41 | 313127 | 3CURDSVILLE | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99903 | 0.86032 | 13.872 | Yes
Active | 2026W1-N11-WVD42 | 314726 | 3WILLIS | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99998 | 0.86144 | 13.854 | Yes
Active | 2026W1-N11-WVD43 | 315822 | AE2-259_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99999 | 0.86145 | 13.854 | Yes
Active | 2026W1-N11-WVD44 | 314664 | 3REDH DP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99219 | 0.8668 | 12.539 | Yes
Active | 2026W1-N11-WVD45 | 314663 | 3REDH TP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99235 | 0.86698 | 12.537 | Yes
Active | 2026W1-N11-WVD46 | 314707 | 3MORAN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0019 | 0.86897 | 13.294 | Yes
Active | 2026W1-N11-WVD47 | 314521 | 3PAMPL_1 | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99541 | 0.87057 | 12.484 | Yes
Active | 2026W1-N11-WVD48 | 314713 | 3PAMPLIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99541 | 0.87057 | 12.484 | Yes
Active | 2026W1-N11-WVD49 | 314426 | 3FT PKET | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99963 | 0.87253 | 12.71 | Yes
Active | 2026W1-N11-WVD50 | 313156 | 3FT PIC DT T | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99964 | 0.87254 | 12.71 | Yes
Active | 2026W1-N11-WVD51 | 313755 | 3FLAT CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0049 | 0.87599 | 12.891 | Yes
Active | 2026W1-N11-WVD52 | 314429 | 3JTRSVLE | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0073 | 0.88109 | 12.625 | Yes
Active | 2026W1-N11-WVD53 | 314428 | 3HOOPERS | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.88112 | 12.603 | Yes
Active | 2026W1-N11-WVD54 | 314701 | 3LONEPN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.8812 | 12.592 | Yes
Active | 2026W1-N11-WVD55 | 314687 | 3CREWE | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.88135 | 12.575 | Yes
Active | 2026W1-N11-WVD56 | 314519 | 3LONEPINE_1 | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0076 | 0.88165 | 12.599 | Yes
Active | 2026W1-N11-WVD57 | 314715 | 3MADSONV | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99905 | 0.88169 | 11.736 | Yes
Active | 2026W1-N11-WVD58 | 313853 | 3PONTONDP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0084 | 0.88217 | 12.627 | Yes
Active | 2026W1-N11-WVD59 | 313462 | 3AF1-294 | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0085 | 0.8822 | 12.626 | Yes
Active | 2026W1-N11-WVD60 | 319063 | AF1-294_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0086 | 0.88229 | 12.626 | Yes
Active | 2026W1-N11-WVD61 | 314432 | 3MARTIN DP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0074 | 0.88986 | 11.75 | Yes
Active | 2026W1-N11-WVD62 | 314706 | 3MARTIN TAP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0074 | 0.8899 | 11.75 | Yes
Active | 2026W1-N11-WVD63 | 970681 | AG2-440_POI | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0045 | 0.89884 | 10.57 | Yes
Active | 2026W1-N11-WVD64 | 81065 | AG2-440_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0046 | 0.89887 | 10.57 | Yes
Active | 2026W1-N11-WVD65 | 81080 | AG2-442_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0048 | 0.89906 | 10.572 | Yes
Active | 2026W1-N11-WVD66 | 313281 | 3VICTORIA DP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0077 | 0.90176 | 10.6 | Yes
Active | 2026W1-N11-WVD67 | 314725 | 3VICTORIA TP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0078 | 0.90183 | 10.599 | Yes
Active | 2026W1-N11-WVD68 | 314723 | 3VICTRIA | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.008 | 0.90643 | 10.159 | Yes
Active | 2026W1-N11-WVD69 | 314677 | 6BUCKING | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.84779 | 15.978 | Yes
Active | 2026W1-N11-WVD70 | 316322 | AB2-045 | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.84779 | 15.978 | Yes
Active | 2026W1-N11-WVD71 | 971844 | AH1-439_POI | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.84789 | 15.974 | Yes
Active | 2026W1-N11-WVD72 | 82745 | AH1-439_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0076 | 0.84789 | 15.974 | Yes
Active | 2026W1-N11-WVD73 | 314692 | 6FARMVIL | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0079 | 0.84829 | 15.958 | Yes
Active | 2026W1-N11-WVD74 | 972002 | AH1-546_POI | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0082 | 0.84832 | 15.988 | Yes
Active | 2026W1-N11-WVD75 | 82920 | AH1-546_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0082 | 0.84834 | 15.988 | Yes
Active | 2026W1-N11-WVD76 | 314691 | 3FARMVIL | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0085 | 0.85433 | 15.415 | Yes
Active | 2026W1-N11-WVD77 | 314719 | 3S CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 0.99092 | 0.85534 | 13.557 | Yes
Active | 2026W1-N11-WVD78 | 313127 | 3CURDSVILLE | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0058 | 0.85651 | 14.927 | Yes
Active | 2026W1-N11-WVD79 | 314726 | 3WILLIS | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0067 | 0.85765 | 14.907 | Yes
Active | 2026W1-N11-WVD80 | 315822 | AE2-259_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0067 | 0.85766 | 14.907 | Yes
Active | 2026W1-N11-WVD81 | 314664 | 3REDH DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 0.99761 | 0.86323 | 13.439 | Yes
Active | 2026W1-N11-WVD82 | 314663 | 3REDH TP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 0.99777 | 0.86341 | 13.436 | Yes
Active | 2026W1-N11-WVD83 | 314707 | 3MORAN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.008 | 0.8653 | 14.271 | Yes
Active | 2026W1-N11-WVD84 | 314521 | 3PAMPL_1 | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0008 | 0.86706 | 13.376 | Yes
Active | 2026W1-N11-WVD85 | 314713 | 3PAMPLIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0008 | 0.86706 | 13.376 | Yes
Active | 2026W1-N11-WVD86 | 314426 | 3FT PKET | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0048 | 0.86905 | 13.572 | Yes
Active | 2026W1-N11-WVD87 | 313156 | 3FT PIC DT T | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0048 | 0.86906 | 13.571 | Yes
Active | 2026W1-N11-WVD88 | 313755 | 3FLAT CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0104 | 0.8725 | 13.787 | Yes
Active | 2026W1-N11-WVD89 | 314429 | 3JTRSVLE | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0124 | 0.87769 | 13.475 | Yes
Active | 2026W1-N11-WVD90 | 314428 | 3HOOPERS | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0122 | 0.87774 | 13.45 | Yes
Active | 2026W1-N11-WVD91 | 314701 | 3LONEPN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0122 | 0.87782 | 13.439 | Yes
Active | 2026W1-N11-WVD92 | 314687 | 3CREWE | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0122 | 0.87798 | 13.419 | Yes
Active | 2026W1-N11-WVD93 | 314519 | 3LONEPINE_1 | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0127 | 0.87827 | 13.446 | Yes
Active | 2026W1-N11-WVD94 | 314715 | 3MADSONV | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0039 | 0.8784 | 12.55 | Yes
Active | 2026W1-N11-WVD95 | 313853 | 3PONTONDP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0135 | 0.87877 | 13.476 | Yes
Active | 2026W1-N11-WVD96 | 313462 | 3AF1-294 | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0136 | 0.8788 | 13.475 | Yes
Active | 2026W1-N11-WVD97 | 319063 | AF1-294_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0136 | 0.87889 | 13.475 | Yes
Active | 2026W1-N11-WVD98 | 314432 | 3MARTIN DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0119 | 0.88673 | 12.52 | Yes
Active | 2026W1-N11-WVD99 | 314706 | 3MARTIN TAP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.012 | 0.88678 | 12.52 | Yes
Active | 2026W1-N11-WVD100 | 970681 | AG2-440_POI | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0086 | 0.89593 | 11.269 | Yes
Active | 2026W1-N11-WVD101 | 81065 | AG2-440_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0087 | 0.89596 | 11.27 | Yes
Active | 2026W1-N11-WVD102 | 81080 | AG2-442_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0089 | 0.89615 | 11.272 | Yes
Active | 2026W1-N11-WVD103 | 313281 | 3VICTORIA DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.89896 | 11.274 | Yes
Active | 2026W1-N11-WVD104 | 314725 | 3VICTORIA TP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0118 | 0.89903 | 11.273 | Yes
Active | 2026W1-N11-WVD105 | 314723 | 3VICTRIA | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.90376 | 10.798 | Yes
Active | 2026W1-N11-WVD106 | 313460 | 3BIRDSBRANCH | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0109 | 0.90713 | 10.375 | Yes
Active | 2026W1-N11-WVD107 | 319088 | AF2-222_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0109 | 0.90714 | 10.375 | Yes
Active | 2026W1-N11-WVD108 | 314710 | 3NUTBUSH | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0112 | 0.90815 | 10.305 | Yes
Active | 2026W1-N11-WVD109 | 314695 | 3GARY DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0115 | 0.90833 | 10.314 | Yes
Active | 2026W1-N11-WVD110 | 971775 | AH1-396 GEN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0115 | 0.90833 | 10.314 | Yes
Active | 2026W1-N11-WVD111 | 314430 | 3KENBRDG | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0116 | 0.90846 | 10.313 | Yes
Active | 2026W1-N11-WVD112 | 970322 | AG2-213_POI | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.90854 | 10.312 | Yes
Active | 2026W1-N11-WVD113 | 314431 | 3KENB TP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.90856 | 10.311 | Yes
Active | 2026W1-N11-WVD114 | 970256 | AG2-171_POI | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0116 | 0.90859 | 10.3 | Yes
Active | 2026W1-N11-WVD115 | 80369 | AG2-171_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0116 | 0.9086 | 10.3 | Yes
Active | 2026W1-N11-WVD116 | 80472 | AG2-213_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.9086 | 10.313 | Yes
Active | 2026W1-N11-WVD117 | 314427 | 3LUNENBURG | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0117 | 0.90876 | 10.297 | Yes

## Non-Convergence
PJM N-1-1 Non-Convergence Result (Winter Case)
FG # Status | FG # | Contingency 1 | Contingency 2 | Status | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2026W1-N11-WNC1 | COMED_P1-2_138-L0112__B-S_SRT-A | COMED_P1-2_138-L91907_-S_SRT-A | NotCnv | Yes

## Load Drop
PJM N-1-1 Load Drop Result (Winter 2031 Case)
FG # Status | FG# | Contingency 1 | Contingency 2 | MW Drop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational-Only | N/A | DVP_P1-2: LN 201_SRT-A | DVP_P1-2: LN 2311_SRT-A | 442.24 | No | To be resolved through the supplemental M3 process
Informational-Only | N/A | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 201_SRT-A | 442.24 | No | To be resolved through the supplemental M3 process