## Thermal
To be adressed through Interregional process.
PJM N-1-1 Thermal Result (Summer 2031 Case) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-N11-ST1 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 122.25 | 115.88 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST2 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 134.51 | 115.77 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST3 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 126.39 | 114.8 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST4 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 126.39 | 114.29 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST5 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 134.73 | 113.66 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST6 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 131.81 | 113.1 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST7 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 131.81 | 113.1 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST8 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 122.25 | 112.87 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST9 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12006_R-N_SRT-A | Base Case | 123.16 | 112.21 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST10 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 118.12 | 112.17 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST11 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 117.51 | 112.03 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST12 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | Base Case | 125.65 | 111.84 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST13 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L11120_R-N_SRT-A | Base Case | 119.11 | 111.35 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST14 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 118.57 | 111.22 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST15 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10806_R-S_SRT-A | Base Case | 122.44 | 111.15 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST16 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 132.02 | 111 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST17 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 132.02 | 111 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST18 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 118.57 | 110.33 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST19 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10807_R-S_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 114.89 | 110.25 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST20 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | Base Case | 115.6 | 110.13 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST21 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 118.42 | 110.05 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST22 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 117.5 | 109.95 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST23 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 112.76 | 109.94 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST24 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 126.09 | 109.43 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST25 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 111.18 | 109.31 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST26 | 270716 | DRESDEN ; B | 274702 | KENDALL ;BU | 1 | 345 | 222 | 1201 | 1201 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L93501_B-S_SRT-A | 119.97 | 109.29 | Yes |  |  | 1201 | 1201 | 1252 | 1367 | 1498 | 1498 | 1572 | 1730 | 1438 | 1438 | 1506 | 1655
Active | 2026W1-N11-ST27 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#18125_SRT-A | 126.09 | 109.03 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST28 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 111.2 | 108.86 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST29 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 113.58 | 108.14 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST30 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L10807_R-S_SRT-A | 114.89 | 108.08 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST31 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | DPL_P1_2_CKT 5025_SRT-A | 122.78 | 108 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST32 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | 125.04 | 107.94 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST33 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | DPL_P1_2_CKT 5025_SRT-A | 124.39 | 107.86 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST34 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 118.12 | 107.68 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST35 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 115.32 | 107.44 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST36 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 113.58 | 107.29 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST37 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L10806_R-S_SRT-A | 115.74 | 107.14 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST38 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | Base Case | 119.8 | 107.07 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST39 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 115.32 | 106.81 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST40 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 118.42 | 106.65 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST41 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L11120_R-N_SRT-A | Base Case | 114.15 | 106.57 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST42 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 112.76 | 106.5 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST43 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 106.43 | 106.42 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST44 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10806_R-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 115.73 | 106.4 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST45 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10801_B-S_SRT-A | Base Case | 106.5 | 106.28 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST46 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | 123.24 | 106.2 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST47 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 116.36 | 106.06 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST48 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 114.46 | 105.62 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST49 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | DPL_P1_2_CKT 5025_SRT-A | 120.11 | 105.35 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST50 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | DPL_P1_2_CKT 5025_SRT-A | 120.11 | 105.35 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST51 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | 122.37 | 105.3 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST52 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | 122.37 | 105.3 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST53 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | DPL_P1_2_CKT 5025_SRT-A | 121.72 | 105.21 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST54 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | DPL_P1_2_CKT 5025_SRT-A | 121.72 | 105.21 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST55 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10805_B-S_SRT-A | Base Case | 111.27 | 105.1 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST56 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 104.94 | 104.94 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST57 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 116.35 | 104.62 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST58 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 114.45 | 104.4 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST59 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#17431_SRT-A | AEP_P1-2_#6227_574_SRT-A | 113.36 | 104.4 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST60 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10805_B-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 115.59 | 104.17 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST61 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 105 | 103.91 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST62 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L2310___-S_SRT-A | Base Case | 105 | 103.82 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST63 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 110.78 | 103.81 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST64 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 113.28 | 103.75 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST65 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10805_B-S_SRT-A | 110.48 | 103.71 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST66 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | 120.57 | 103.55 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST67 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | 120.57 | 103.55 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST68 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 103.44 | 103.48 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST69 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10802_R-S_SRT-A | Base Case | 104.31 | 103.47 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST70 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L10805_B-S_SRT-A | 115.6 | 103.33 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST71 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L11617_B-S_SRT-A | Base Case | 103.44 | 103.23 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST72 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L11124_B-N_SRT-A | 109.51 | 103.22 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST73 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | Base Case | 110.1 | 102.96 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST74 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | 329 | 350 | AEP_P1-3_#18039_05CYPRUS 345_1_SRT-A | AEP_P1-3_#18040_05CYPRUS 345_2_SRT-A | 103.91 | 102.94 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Active | 2026W1-N11-ST75 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | 329 | 350 | AEP_P1-3_#18040_05CYPRUS 345_2_SRT-A | AEP_P1-3_#18039_05CYPRUS 345_1_SRT-A | 103.91 | 102.94 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Active | 2026W1-N11-ST76 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 107.62 | 102.78 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST77 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 109.5 | 102.7 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST78 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 113.28 | 102.62 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST79 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 121.29 | 102.55 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST80 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10806_R-S_SRT-A | 105.36 | 102.26 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Removed | 2026W1-N11-ST81 | 270725 | ELK GROVE; R | 270815 | LOMBARD ;1R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 108.55 | 102.24 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST82 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#6227_574_SRT-A | AEP_P1-2_#17431_SRT-A | 113.36 | 102.18 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Removed | 2026W1-N11-ST83 | 270725 | ELK GROVE; R | 270815 | LOMBARD ;1R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 108.17 | 102.15 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST84 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#18125_SRT-A | 121.29 | 102.13 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST85 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10805_B-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 110.42 | 102.03 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST86 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#727_573_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 117.19 | 101.98 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST87 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 109.34 | 101.81 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST88 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10807_R-S_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 109.49 | 101.79 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST89 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 108.56 | 101.7 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST90 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 111.19 | 101.67 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST91 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11120_R-N_SRT-A | Base Case | 106.65 | 101.6 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST92 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 111.67 | 101.4 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST93 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 111.67 | 101.38 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST94 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#17432_SRT-A | AEP_P1-2_#6227_574_SRT-A | 110.18 | 101.23 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST95 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10806_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 104.5 | 101.14 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST96 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 101.07 | 101.1 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST97 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 106.58 | 100.77 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST98 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L11124_B-N_SRT-A | 110.79 | 100.74 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST99 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L93502_R-S_SRT-A | 111.1 | 100.73 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST100 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L10806_R-S_SRT-A | Base Case | 104.33 | 100.73 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST101 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 106.27 | 100.52 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST102 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-2_GEN1-GSA_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.41 | 100.47 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST103 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L13821_R-R_SRT-A | Base Case | 110.82 | 100.35 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST104 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-2_GEN2-GSA_9-10_SUM_SRT-S | DPL_P1_2_CKT 5025_SRT-A | 107.27 | 100.33 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST105 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-2_GEN2-GSA_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.27 | 100.33 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST106 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-1_SALM_G1_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.15 | 100.19 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST107 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 200036 AH1-710 GEN1 25.0 N1_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.15 | 100.19 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST108 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 111.21 | 100.08 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST109 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | Base Case | 109.13 | 100.07 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST110 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 107.9 | 100.07 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST111 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-1_SALM_G2_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.01 | 100.04 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST112 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 200037 AH1-710 GEN2 25.0 N2_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.01 | 100.04 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST113 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | 1479 | COMED_P1-2_345-L11604_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 105.83 | 100.04 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST114 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L93502_R-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 111.11 | 100.03 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026-W1-N11-ST115 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 149.63 | 147.84 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-ST116 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 149.63 | 147.83 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-ST117 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069A_SRT-A | 147.44 | 145.65 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-ST118 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23069A_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 147.44 | 145.65 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026-W1-N11-ST119 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 143.11 | 133.68 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST120 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 143.11 | 133.23 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST121 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 141.76 | 132.36 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST122 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 141.76 | 131.86 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST123 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1607__B-N_SRT-A | 130.58 | 122.99 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST124 | 270998 | ANTIOCH ;BT | 272386 | ROUND LK ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1603__R-N_SRT-A | 130.11 | 122.3 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST125 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L4202__B-N_SRT-A | 127.62 | 122.18 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Active | 2026-W1-N11-ST126 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 123.13 | 117.69 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST127 | 272456 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18415_B-N_SRT-A | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | 124.82 | 116.02 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST128 | 270724 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18415_B-N_SRT-A | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | 123.77 | 114.96 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST129 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 123.14 | 114.79 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST130 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_138-L4202__B-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 127.62 | 114.64 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Active | 2026-W1-N11-ST131 | 272456 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 138 | 222 | 420 | 480 | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | COMED_P1-2_345-L18415_B-N_SRT-A | 124.82 | 114.43 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST132 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18415_B-N_SRT-A | COMED_P1-3_TR82_ELKGR_B-N_SRT-A | 122.34 | 114.08 | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Informational-Only | 2026-W1-N11-ST133 N/A | 270981 | ALPINE ;RT | 271083 | BELVIDERE; R | 1 | 138 | 222 | 329 | 372 | COMED_P1-2_345-L15616__-R_SRT-A | COMED_P1-2_138-L15624_B-R_SRT-A | 133.33 | 113.5 | No | To be adressed through supplemental process. | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-N11-ST134 | 270724 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | COMED_P1-2_345-L18415_B-N_SRT-A | 123.77 | 113.37 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST135 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR82_ELKGR_B-N_SRT-A | COMED_P1-2_345-L18415_B-N_SRT-A | 122.34 | 113.02 | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026-W1-N11-ST136 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 120.68 | 112.99 | No | Substation Equipment Exclusion |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026-W1-N11-ST137 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_138-L1607__B-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 130.58 | 112.75 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST138 | 271064 | BARTLETT ;BT | 272546 | SPAULDING;1B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 121.31 | 112.69 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST139 | 271555 | GLENDALE ;RT | 271923 | LOMBARD ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 123.19 | 112.43 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST140 | 270998 | ANTIOCH ;BT | 272386 | ROUND LK ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_138-L1603__R-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 130.11 | 112.16 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST141 | 271555 | GLENDALE ;RT | 271923 | LOMBARD ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 123.18 | 111.79 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST142 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 112.1 | 110.95 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026-W1-N11-ST143 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 112.1 | 110.95 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026-W1-N11-ST144 | 271064 | BARTLETT ;BT | 272546 | SPAULDING;1B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L14401_R-N_SRT-A | 121.31 | 110.82 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST145 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_138-L7915__R-N_SRT-A | 118.17 | 110.65 | No | Substation Equipment Exclusion |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026-W1-N11-ST146 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 116.97 | 110.43 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST147 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_138-L7915__R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 118.17 | 110.17 | No | Substation Equipment Exclusion |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026-W1-N11-ST148 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 118.87 | 109.58 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST149 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069A_SRT-A | 110.38 | 109.23 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026-W1-N11-ST150 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23069A_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 110.38 | 109.23 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026-W1-N11-ST151 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10321_B-S_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 111.71 | 109.18 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST152 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 111.52 | 108.92 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST153 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 116.17 | 108.04 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST154 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 117.94 | 108 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST155 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 110.55 | 107.98 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST156 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 111.97 | 107.05 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Active | 2026-W1-N11-ST157 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 115.07 | 106.68 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST158 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12003_B-C_SRT-A | 106.58 | 106.34 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST159 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12003_B-C_SRT-A | 106.51 | 106.34 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST160 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OEC-345-813_SRT-A | ATSI_P1-2_CEI-345-714_SRT-A | 124.64 | 106.2 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026-W1-N11-ST161 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_CEI-345-714_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 124.65 | 106.19 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026-W1-N11-ST162 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | Base Case | 115.91 | 106.16 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST163 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 116.16 | 106.05 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST164 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 113.44 | 105.67 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST165 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L18502AB-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 117.26 | 105.46 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST166 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 113.85 | 105.34 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST167 | 272387 | ROUND LK ; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L4202__B-N_SRT-A | 110.11 | 104.65 | Yes |  |  | 298.0617 | 298.0617 | 298.7788 | 305.7104 | 322.9201 | 322.9201 | 323.8762 | 332.9591 | 317.6616 | 317.6616 | 318.6177 | 326.9835
Active | 2026-W1-N11-ST168 | 275213 | SILVER LK;2M | 272464 | SILVER LK; B | 1 | 138 | 222 | 400 | 465 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-3_TR83_SILVEGR-R_SRT-A | 106.19 | 104.63 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026-W1-N11-ST169 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | Base Case | 110.6 | 104.35 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST170 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | Base Case | 111.12 | 104.18 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST171 | 271052 | BEDFORD P;4B | 271216 | CLEARING ;BT | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L11604_R-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 115.33 | 104.16 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST172 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 117.94 | 103.72 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST173 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | Base Case | 109.87 | 103.63 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST174 | 270781 | ITASCA ; R | 271735 | ITASCA ;3R | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR84_ITASC_B-N_SRT-A | COMED_P1-2_138-L12015_R-N_SRT-A | 106.47 | 103.6 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST175 | 270781 | ITASCA ; R | 271735 | ITASCA ;3R | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_138-L12015_R-N_SRT-A | COMED_P1-3_TR84_ITASC_B-N_SRT-A | 106.47 | 103.51 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST176 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 113.86 | 103.31 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST177 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 113.44 | 103.31 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST178 | 270883 | SILVER LK; R | 275213 | SILVER LK;2M | 1 | 345/138 | 222 | 400 | 465 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-3_TR83_SILVEGR-R_SRT-A | 104.91 | 103.29 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026-W1-N11-ST179 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L18502AB-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 112.14 | 103.23 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Active | 2026-W1-N11-ST180 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 115.06 | 103.16 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST181 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-1_CEI-345-711_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 104.82 | 103.06 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026-W1-N11-ST182 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | 239035 02PERRG1 22.0 1 _SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 104.82 | 103.06 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026-W1-N11-ST183 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 106.65 | 103 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST184 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 106.65 | 102.97 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST185 | 270999 | ANTIOCH ;RT | 272389 | RL BEACH ; R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1607__B-N_SRT-A | 110.34 | 102.8 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST186 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 106.1 | 102.51 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST187 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | AEP_P1-2_#775_563_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 106.74 | 102.49 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026-W1-N11-ST188 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 106.1 | 102.43 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST189 | 270998 | ANTIOCH ;BT | 272388 | RL BEACH ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1603__R-N_SRT-A | 109.78 | 102.01 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST190 | 270998 | ANTIOCH ;BT | 272386 | ROUND LK ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 108.9 | 101.96 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST191 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 106.2 | 101.89 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST192 | 232118 | NSEAFORD | 232136 | CONAWAY | 1 | 138 | 235 | 167 | 241 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 101.33 | 101.52 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 167 | 241 | N/A | 264 | 231 | 308 | N/A | 338 | 218 | 294 | N/A | 323
Active | 2026-W1-N11-ST193 | 232118 | NSEAFORD | 232136 | CONAWAY | 1 | 138 | 235 | 167 | 241 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 101.33 | 101.52 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 167 | 241 | N/A | 264 | 231 | 308 | N/A | 338 | 218 | 294 | N/A | 323
Active | 2026-W1-N11-ST194 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 107.89 | 101.36 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026-W1-N11-ST195 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 105.48 | 101.17 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST196 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L10321_B-S_SRT-A | 111.71 | 101.13 | Yes |  | Limited by line equipment, not within the substation | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST197 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_138-L10301_B-S_SRT-A | 103.84 | 101.07 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Removed | 2026-W1-N11-ST198 | 271668 | VETERANS ;BT | 272782 | WILL CNTY; B | 1 | 138 | 222 | 292 | 321 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_138-L5103__B-S_SRT-A | 105.46 | 101.04 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 310.0129 | 396.7782 | 403.9489 | 433.5877 | 371.9198 | 440.9975 | 450.0803 | 484.7387 | 359.2516 | 431.6756 | 440.2804 | 473.7436
Active | 2026-W1-N11-ST199 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11604_R-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 104.12 | 101.03 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026-W1-N11-ST200 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_138-L10301_B-S_SRT-A | 103.62 | 100.92 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Removed | 2026-W1-N11-ST201 | 271668 | VETERANS ;BT | 272782 | WILL CNTY; B | 1 | 138 | 222 | 292 | 321 | COMED_P1-2_345-L11604_R-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 103.92 | 100.82 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 310.0129 | 396.7782 | 403.9489 | 433.5877 | 371.9198 | 440.9975 | 450.0803 | 484.7387 | 359.2516 | 431.6756 | 440.2804 | 473.7436
Active | 2026-W1-N11-ST202 | 271555 | GLENDALE ;RT | 272109 | NORDIC ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 111.5 | 100.8 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST203 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 103.54 | 100.77 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST204 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OEC-345-820_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 102.39 | 100.73 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026-W1-N11-ST205 | 243472 | 05BEXLEY | 243592 | 05YEARLG | 1 | 138 | 205 | 196 | 247 | AEP_P1-2_#6793_13398_SRT-A | AEP_P1-2_#13640_27882_SRT-A | 100.62 | 100.62 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 277 | 277 | N/A | N/A | 350 | 350 | N/A | N/A | 213 | 260 | N/A | N/A
Active | 2026-W1-N11-ST206 | 243472 | 05BEXLEY | 243592 | 05YEARLG | 1 | 138 | 205 | 196 | 247 | AEP_P1-2_#13640_27882_SRT-A | AEP_P1-2_#6793_13398_SRT-A | 100.62 | 100.62 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 277 | 277 | N/A | N/A | 350 | 350 | N/A | N/A | 213 | 260 | N/A | N/A
Active | 2026-W1-N11-ST207 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 100.62 | 100.6 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026-W1-N11-ST208 | 271052 | BEDFORD P;4B | 271216 | CLEARING ;BT | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L11604_R-S_SRT-A | 115.33 | 100.51 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST209 | 270781 | ITASCA ; R | 998462 | ITASCA 84 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR82_ITASC_R-N_SRT-A | COMED_P1-2_138-L12015_R-N_SRT-A | 103.36 | 100.49 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST210 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L10112AR-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 106.3 | 100.48 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST211 | 270781 | ITASCA ; R | 998462 | ITASCA 84 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_138-L12015_R-N_SRT-A | COMED_P1-3_TR82_ITASC_R-N_SRT-A | 103.36 | 100.44 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST212 | 270999 | ANTIOCH ;RT | 272389 | RL BEACH ; R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 106.94 | 100.36 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026-W1-N11-ST213 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 103.21 | 100.31 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST214 | 271739 | ITASCA ;4R | 998462 | ITASCA 84 | 1 | 138 | 222 | 420 | 480 | COMED_P1-3_TR82_ITASC_R-N_SRT-A | COMED_P1-2_138-L12015_R-N_SRT-A | 103.14 | 100.29 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST215 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 103 | 100.25 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST216 | 271739 | ITASCA ;4R | 998462 | ITASCA 84 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_138-L12015_R-N_SRT-A | COMED_P1-3_TR82_ITASC_R-N_SRT-A | 103.14 | 100.23 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST217 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 103.53 | 100.21 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026-W1-N11-ST218 | 271555 | GLENDALE ;RT | 272109 | NORDIC ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 111.5 | 100.17 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N11-ST219 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 |  | 1528 | 'AEP_P1-2_#18202_SRT-A' | 'COMED_P1-2_345-L10805_B-S_SRT-A' | 115.28 | 110.36 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 138.33 | 127.29 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 138.33 | 127.28 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 138.1 | 127.08 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 138.09 | 127.07 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 137.98 | 126.82 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 137.97 | 126.81 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 137.74 | 126.6 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 137.74 | 126.59 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 275198 | LOMBARD ;2M | 271925 | LOMBARD ;2R | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 119.43 | 116.1 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270813 | LOMBARD ;2R | 275198 | LOMBARD ;2M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 118.99 | 115.59 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 275228 | WAYNE ;1M | 272740 | WAYNE ; B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L14401_R-N_SRT-A | 119.98 | 114.8 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270916 | WAYNE ; B | 275228 | WAYNE ;1M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L14401_R-N_SRT-A | 119.98 | 114.8 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 275198 | LOMBARD ;2M | 271925 | LOMBARD ;2R | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 119.43 | 114.02 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270813 | LOMBARD ;2R | 275198 | LOMBARD ;2M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 118.99 | 113.51 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 275228 | WAYNE ;1M | 272740 | WAYNE ; B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 119.98 | 111.86 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270916 | WAYNE ; B | 275228 | WAYNE ;1M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 119.98 | 111.86 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only Active | 2026W1-N11-ST220 | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_138-L10117_R-N_SRT-A | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | 118.63 | 110.78 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only Active | 2026W1-N11-ST221 | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | COMED_P1-2_138-L10117_R-N_SRT-A | 118.63 | 110.74 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only Active | 2026W1-N11-ST222 | 271342 | DIERKING ; B | 272146 | GREENLEAF; B | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10111AB-N_SRT-A | 119.26 | 109.48 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only Active | 2026W1-N11-ST223 | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L15616__-R_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 112.69 | 109.48 | Yes |  |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only Active | 2026W1-N11-ST224 | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L97104__-R_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 112.57 | 109.34 | Yes |  |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only Active | 2026W1-N11-ST225 | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L15616__-R_SRT-A | 112.7 | 106.37 | Yes |  |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only Active | 2026W1-N11-ST226 | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L97104__-R_SRT-A | 112.58 | 106.24 | Yes |  |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only Active | 2026W1-N11-ST227 | 271342 | DIERKING ; B | 272146 | GREENLEAF; B | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L10111AB-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 119.26 | 105.99 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only Active | 2026W1-N11-ST228 | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_138-L10117_R-N_SRT-A | 113.03 | 104.87 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only Active | 2026W1-N11-ST229 | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_138-L10117_R-N_SRT-A | Base Case | 113.86 | 104.13 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 105.5 | 104.07 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only Active | 2026W1-N11-ST230 | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L10112AR-N_SRT-A | 114.62 | 104 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 105.35 | 103.95 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 105.32 | 103.9 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 105.18 | 103.77 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 104.58 | 103.12 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 104.58 | 103.12 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 104.43 | 103 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 104.43 | 103 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 104.4 | 102.95 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 104.4 | 102.95 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only Active | 2026W1-N11-ST231 | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L10112AR-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 114.62 | 102.87 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only Active | 2026W1-N11-ST232 | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_138-L10117_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 113.03 | 102.87 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 104.25 | 102.83 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 104.25 | 102.83 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only Active | 2026W1-N11-ST233 | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 466 | 588 | COMED_P1-2_138-L10117_R-N_SRT-A | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | 107.5 | 102.05 | Yes |  |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640
Informational-Only Active | 2026W1-N11-ST234 | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 466 | 588 | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | COMED_P1-2_138-L10117_R-N_SRT-A | 107.5 | 102 | Yes |  |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640
Informational-Only Active | 2026W1-N11-ST235 | 271342 | DIERKING ; B | 272146 | GREENLEAF; B | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_138-L10118_B-N_SRT-A | 109.7 | 101.91 | Yes |  |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only Active | 2026W1-N11-ST236 | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L15616__-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 104.87 | 101.66 | Yes |  |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only | N/A | 270773 | GRAYSLAKE; B | 270900 | TOLLWAY ; B | 1 | 345 | 222 | 1202 | 1387 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 102.77 | 101.58 | No | To be adressed through supplemental process. |  | 1201.0906 | 1201.0906 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only Active | 2026W1-N11-ST237 | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L97104__-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 104.76 | 101.53 | Yes |  |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only Active | 2026W1-N11-ST238 | 271436 | PINE ; B | 271736 | ITASCA ;12 | 1 | 138 | 222 | 466 | 588 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10111AB-N_SRT-A | 107.87 | 101.42 | Yes |  |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640
Informational-Only | N/A | 270774 | GRAYSLAKE; R | 270883 | SILVER LK; R | 1 | 345 | 222 | 1449 | 1864 | COMED_P1-2_345-L18502AB-N_SRT-A | Base Case | 110.35 | 101.41 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270981 | ALPINE ;RT | 271083 | BELVIDERE; R | 1 | 138 | 222 | 329 | 372 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_138-L15624_B-R_SRT-A | 103.12 | 101.26 | No | To be adressed through supplemental process. | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270773 | GRAYSLAKE; B | 270900 | TOLLWAY ; B | 1 | 345 | 222 | 1202 | 1387 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 106.67 | 100.98 | No | To be adressed through supplemental process. |  | 1201.0906 | 1201.0906 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only | N/A | 270773 | GRAYSLAKE; B | 270900 | TOLLWAY ; B | 1 | 345 | 222 | 1202 | 1387 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 106.44 | 100.58 | No | To be adressed through supplemental process. |  | 1201.0906 | 1201.0906 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only Active | 2026W1-N11-ST239 | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 466 | 588 | COMED_P1-2_138-L10117_R-N_SRT-A | Base Case | 106.94 | 100.47 | Yes |  |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640

## Volt Mag
PJM N-1-1 Voltage Magnitude Result (Summer 2031 Case)
FG # Status | FG # | Bus # | Name | KV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026-W1-N11-SVM1 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1 | 0.91506 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM2 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1206__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0006 | 0.91726 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM3 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99521 | 0.89213 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM4 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0021 | 0.89818 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM5 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0077 | 0.90094 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM6 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0042 | 0.91307 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM7 | 970832 | AG2-524 TAP | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99599 | 0.91998 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM8 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L7719__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0008 | 0.91447 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM9 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_DRESD_B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0004 | 0.91634 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM10 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.92061 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM11 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.92061 | 0.89286 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM12 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.9269 | 0.89746 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM13 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.9269 | 0.89892 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM14 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93031 | 0.90024 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM15 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93031 | 0.90174 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM16 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93856 | 0.91214 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM17 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93856 | 0.91343 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM18 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.92061 | 0.91408 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM19 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR81_DRESD_B-S_SRT-A | 0.92061 | 0.91534 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM20 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L1206__R-S_SRT-A | 0.92061 | 0.91691 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM21 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-1_DR-3U_______-S_SRT-A | 0.92061 | 0.91817 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM22 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 274659 DRESDEN ;3U 18.0 3 _SRT-A | 0.92061 | 0.91817 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM23 | 970832 | AG2-524 TAP | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.95408 | 0.9195 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM24 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.9961 | 0.89354 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM25 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.003 | 0.8996 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM26 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0086 | 0.9024 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM27 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0048 | 0.91429 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM28 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-1_DR-3U_______-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0007 | 0.9185 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM29 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L7404___-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.001 | 0.82171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM30 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L7404___-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.0086 | 0.85377 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM31 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L7404___-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.0097 | 0.90195 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM32 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | 274659 DRESDEN ;3U 18.0 3 _SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0007 | 0.9185 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM33 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99902 | 0.91124 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVM34 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0065 | 0.91801 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## Volt Drop
PJM N-1-1 Voltage Drop Result (Summer 2031 Case)
FG # Status | FG # | Bus # | Name | KV | Area | % Vdrop | Contingency 1 | Contingency 2 | BaseVolt | ContVolt | % Vdrop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2026-W1-N11-SVD1 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 1.001 | 0.91868 | 8.236 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD2 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 1.001 | 0.91868 | 8.236 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD3 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | 1.0106 | 0.88813 | 12.247 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD4 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | 1.0122 | 0.88985 | 12.237 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD5 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | 1.0106 | 0.88813 | 12.247 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD6 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | 1.0122 | 0.88985 | 12.237 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD7 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0079 | 0.88808 | 11.98 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD8 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 1.0079 | 0.88808 | 11.98 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD9 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0095 | 0.88981 | 11.971 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026-W1-N11-SVD10 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: TX2_TROWBRIDGE_SRT-A | DVP_P1-3: TX1_TROWBRIDGE_SRT-A | 1.0095 | 0.88981 | 11.971 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## Non-Convergence
PJM N-1-1 Non-Convergence Result (Summer 2031 Case)
FG # Status | FG # | Contingency 1 | Contingency 2 | Status | PJM Accepting Proposals | Reasons for Exclusions | Comment
Removed | 2026W1-N11-SNCV1 | COMED_P1-2_138-L13701GR-C_SRT-A | COMED_P1-2_138-L17404GB-C_SRT-A | NotCnv | Yes

## Load Drop
PJM N-1-1 Load Drop Result (Summer 2031 Case)
FG # Status | FG# | Contingency 1 | Contingency 2 | MW Drop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational Only |  | DVP_P1-2: LN 201_SRT-A | DVP_P1-2: LN 2311_SRT-A | 405.84 | No | Will be addressed through the supplemental process
Informational Only |  | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 201_SRT-A | 405.84 | No | Will be addressed through the supplemental process