## N-1 Thermal
PJM N-1 Thermal Result (Light Load 2031 Case) | [16 empty] | Conductor/Transformer Limit
FG # Status | FG# | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Light Load 2031 Case)
| FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
244904AEP_P7-1_#10881___SRT-A | Active | 2026-W1-N1-SVM1 | 244904 | 05FIELDALE4 | 138 | 205 | 1.0623 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
244390AEP_P7-1_#10881___SRT-A | Active | 2026-W1-N1-SVM2 | 244390 | 05FIELDALE3 | 138 | 205 | 1.0623 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
243799AEP_P7-1_#10881___SRT-A | Active | 2026-W1-N1-SVM3 | 243799 | 05FIELDALE2 | 138 | 205 | 1.0623 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
243655AEP_P7-1_#10881___SRT-A | Active | 2026-W1-N1-SVM4 | 243655 | 05STONELEIGH | 138 | 205 | 1.061 | 1.035 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
243652AEP_P7-1_#10881___SRT-A | Active | 2026-W1-N1-SVM5 | 243652 | 05SMITHRIVER | 138 | 205 | 1.0587 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
242638AEP_P7-1_#10881___SRT-A | Active | 2026-W1-N1-SVM6 | 242638 | 05FIELDALE1 | 138 | 205 | 1.0623 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
| Active | 2026-W1-N1-SVM7 | 288720 | 05PATRCKHNRY | 138 | 205 | 1.0517 | 1.035 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
| Active | 2026-W1-N1-SVM8 | 244904 | 05FIELDALE4 | 138 | 205 | 1.0506 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10880___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
| Active | 2026-W1-N1-SVM9 | 244390 | 05FIELDALE3 | 138 | 205 | 1.0506 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10880___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
| Active | 2026-W1-N1-SVM10 | 243799 | 05FIELDALE2 | 138 | 205 | 1.0505 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10880___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
| Active | 2026-W1-N1-SVM11 | 242736 | 05OAKLEV | 138 | 205 | 1.0551 | 1.0314 | 1.05 | Tower | AEP_P7-1_#10881___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
| Active | 2026-W1-N1-SVM12 | 242638 | 05FIELDALE1 | 138 | 205 | 1.0506 | 1.0351 | 1.05 | Tower | AEP_P7-1_#10880___SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Light Load 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment

## N-1 Load Drop
PJM N-1 Load Drop Result (Light Load 2031 Case)
FG # Status | FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational-Only | N/A | DVP_P7-1: LN 2165-2170_SRT-A | Tower | 345 | 0.0 | 373.9 | 373.9 | No | To be adressed through supplemental process.