## Light Load GenDeliv
Will be addressed through the interregional process
2031 RTEP PJM Generator Deliverability Result (Light Load) | [19 empty] | Conductor/Transformer Limit
FG # Status | FG # | FG Index | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | PJM Accepting Proposals | Reason For Exclusion | Comment | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-GD-LL66 | 66 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 664.8 | 665.5 | 132.97 | 133.11 | COMED_P4-6_111-345-B______SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL67 | 67 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 647.7 | 648.2 | 132.45 | 132.56 | COMED_P4-6_111-345-B______SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL1 | 1 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 657.8 | 660.7 | 131.57 | 132.15 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL2 | 2 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 640.7 | 643.4 | 131.01 | 131.57 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL69 | 69 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 652 | 655.6 | 130.4 | 131.12 | COMED_P4_111-45-L30003__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL70 | 70 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 652 | 655.6 | 130.4 | 131.12 | COMED_P4_111-45-L11124__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL68 | 68 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 652 | 655.6 | 130.4 | 131.12 | COMED_P4_111-45-TR81____SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL142 | 142 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 652 | 655.6 | 130.4 | 131.12 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL73 | 73 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 634.8 | 638.3 | 129.82 | 130.52 | COMED_P4_111-45-TR81____SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL143 | 143 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 634.8 | 638.3 | 129.82 | 130.52 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL72 | 72 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 634.8 | 638.3 | 129.82 | 130.52 | COMED_P4_111-45-L11124__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL71 | 71 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 634.8 | 638.3 | 129.82 | 130.52 | COMED_P4_111-45-L30003__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL156 | 156 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 557 | 656.3 | 659.6 | 117.83 | 118.42 | COMED_P7-1_345-L30003_B-R_+_138-L11104_R-R_SRT-A | Tower | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL157 | 157 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 544 | 639.1 | 642.3 | 117.49 | 118.06 | COMED_P7-1_345-L30003_B-R_+_138-L11104_R-R_SRT-A | Tower | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL158 | 158 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 557 | 653.9 | 656.2 | 117.39 | 117.81 | COMED_P7-1_345-L30003_B-R_+_345-L16703_R-S_SRT-A | Tower | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL159 | 159 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 544 | 636.7 | 638.9 | 117.04 | 117.44 | COMED_P7-1_345-L30003_B-R_+_345-L16703_R-S_SRT-A | Tower | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL74 | 74 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1898.6 | 1885 | 117.78 | 116.94 | COMED_P4_144-45-BT7-8___SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL75 | 75 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1891.9 | 1885 | 117.36 | 116.93 | COMED_P4_144-45-BT7-8___SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL76 | 76 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1895 | 1881.1 | 117.56 | 116.69 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL77 | 77 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1888.3 | 1881 | 117.14 | 116.69 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL78 | 78 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1893.7 | 1879.4 | 117.48 | 116.59 | COMED_P4_175-45-BT2122__SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL5 | 5 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1893.7 | 1879.4 | 117.48 | 116.59 | COMED_P1-2_345-L14427__B-R_SRT-A | Single | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL79 | 79 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1897.6 | 1879.4 | 117.72 | 116.59 | COMED_P4_175-45-BT2126__SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL80 | 80 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1897.6 | 1879.4 | 117.72 | 116.59 | COMED_P4_175-45-BT2526__SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL6 | 6 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1897.6 | 1879.4 | 117.72 | 116.59 | COMED_P1-2_345-L0626__B-R_SRT-A | Single | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL81 | 81 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1887 | 1879.4 | 117.06 | 116.59 | COMED_P4_175-45-BT2122__SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL7 | 7 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1887 | 1879.3 | 117.06 | 116.58 | COMED_P1-2_345-L14427__B-R_SRT-A | Single | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL82 | 82 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1890.9 | 1879.3 | 117.3 | 116.58 | COMED_P4_175-45-BT2126__SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL8 | 8 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1890.9 | 1879.3 | 117.3 | 116.58 | COMED_P1-2_345-L0626__B-R_SRT-A | Single | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL83 | 83 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1890.9 | 1879.3 | 117.3 | 116.58 | COMED_P4_175-45-BT2526__SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | N/A | 9 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 561.1 | 560.3 | 114.74 | 114.59 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 86 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 555.2 | 554.6 | 113.55 | 113.42 | COMED_P4_111-45-L11124__SRT-A | Breaker | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 87 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 555.2 | 554.6 | 113.55 | 113.42 | COMED_P4_111-45-L30003__SRT-A | Breaker | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 85 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 555.2 | 554.6 | 113.55 | 113.42 | COMED_P4_111-45-TR81____SRT-A | Breaker | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 144 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 555.2 | 554.6 | 113.55 | 113.42 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-LL15 | 15 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 550.3 | 550.5 | 110.07 | 110.1 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL145 | 145 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 544.5 | 544.8 | 108.9 | 108.95 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL91 | 91 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 544.5 | 544.8 | 108.9 | 108.95 | COMED_P4_111-45-L11124__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL89 | 89 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 544.5 | 544.8 | 108.9 | 108.95 | COMED_P4_111-45-TR81____SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL90 | 90 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 544.5 | 544.8 | 108.9 | 108.95 | COMED_P4_111-45-L30003__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL16 | 16 | 271241 | CRESCENT ; R | 348935 | 4CORBIN | 1 | 138 | 222/357 | 179 | 195 | 194.9 | 108.91 | 108.87 | COMED_P1-2_138-L7404___-S_SRT-A | Single | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 268 | 269 | 280 | 252 | 298 | 300 | 313 | 243 | 291 | 293 | 306

## Light Load IPD
To be addressed through the interregional process
2031 RTEP PJM Individual Plant Deliverability Result (Light Load) | [18 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comment | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-IPD-LL1 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 121.5 | 113.37 | 116.41 | AE2-185 | DVP_P1-2: LN 173_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL2 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 119.3 | 111.42 | 114.34 | AE2-283 | DVP_P1-2: LN 173_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL3 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 118.6 | 111.15 | 113.67 | AC1-145 | DVP_P1-2: LN 173_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL4 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 116.8 | 109.12 | 111.95 | AF2-404 | DVP_P1-2: LN 173_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL5 | 200716 | 26PHILIPSB | 200727 | 26SHAW. 2 | 1 | 115 | 226 | 202 | 202.6 | 101.59 | 100.29 | AD2-133 | PN_P1-2_PN-115-052A_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 167 | 202 | N/A | 227 | 188 | 239 | N/A | 239 | 167 | 202 | N/A | 227
Active | 2026W1-IPD-LL6 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 115.2 | 107.82 | 110.36 | AC1-042 | DVP_P1-2: LN 173_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL7 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 135.4 | 147.4 | 108.34 | 108.93 | AC2-079 | DVP_P1-2: LN 23_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026W1-IPD-LL8 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 103.71 | 106.89 | AE2-185 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL9 | 314691 | 3FARMVIL | 314726 | 3WILLIS | 1 | 115 | 345 | 242.5 | 257.7 | 109.15 | 106.27 | AF2-222 | DVP_P1-2: LN 9607_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026W1-IPD-LL10 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 101.83 | 104.9 | AE2-283 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL11 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 83 | - | 101.97 | 104.52 | AE2-185 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026W1-IPD-LL12 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 101.57 | 104.34 | AC1-145 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL13 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 135.4 | 141.1 | 102.88 | 104.24 | AD1-082 | DVP_P1-2: LN 23_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026W1-IPD-LL14 | 314273 | 3BAKRS P | 314280 | 3NEWBOHE | 1 | 115 | 345 | 135.4 | 139.2 | 101.42 | 102.85 | AC2-079 | DVP_P1-2: LN 23_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026W1-IPD-LL15 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 99.6 | 102.6 | AF2-404 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-LL16 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 86 | - | 99.57 | 102.05 | AE2-185 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026W1-IPD-LL17 | 314532 | 3OAKRI23 | 314536 | 3SUFFOLK | 1 | 115 | 345 | 135.4 | 137.9 | 100.09 | 101.84 | AC2-079 | DVP_P1-2: LN 106_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026W1-IPD-LL18 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 83 | - | 99.43 | 101.82 | AE2-283 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026W1-IPD-LL19 | 314670 | 2ALTVSTA | 314667 | 4ALTVSTA | 1 | 69/138 | 345 | 124.1 | 126.1 | 95.07 | 101.63 | AE2-185 | DVP_P1-2: LN 173_SRT-A |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 104 | 108 | 108 | 124 | 132 | 136 | 136 | 157 | 128 | 132 | 132 | 152
Active | 2026W1-IPD-LL20 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 98.35 | 101.1 | AC1-042 | Base Case |  | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Informational-Only | N/A | 314667 | 4ALTVSTA | 314666 | 3ALTVSTA | 1 | 138/115 | 345 | 139.1 | 140.1 | 99.74 | 100.7 | AE2-291 | DVP_P1-3: 2-WDG 2 4ALTVSTA_SRT-A |  | No | Resolved with HVDC solution in Dominion |  | 127 | 131 | 131 | 141 | 156 | 159 | 159 | 165 | 145 | 148 | 148 | 156
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 304.5 | 100.68 | 102.52 | AB1-160 | PN_P1-3_PN-115-007_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 304.5 | 100.68 | 102.52 | AB1-160 | PN_P2-3_PN-230-997-DRT-056_SRT-SL |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 304.1 | 100.58 | 102.39 | AB1-160 | PN_P2-3_PN-115-19C_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 299 | 100.54 | 100.69 | AB1-160 | PN_P2-3_PN-115-19B_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 323.6 | 107.16 | 108.94 | AE2-139 | PN_P1-3_PN-115-007_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 323.6 | 107.16 | 108.94 | AE2-139 | PN_P2-3_PN-230-997-DRT-056_SRT-SL |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 323.2 | 107.05 | 108.82 | AE2-139 | PN_P2-3_PN-115-19C_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 318.1 | 107.02 | 107.1 | AE2-139 | PN_P2-3_PN-115-19B_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 321.8 | 106.56 | 108.37 | K02 | PN_P1-3_PN-115-007_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 321.8 | 106.56 | 108.37 | K02 | PN_P2-3_PN-230-997-DRT-056_SRT-SL |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 321.5 | 106.46 | 108.24 | K02 | PN_P2-3_PN-115-19C_SRT-A |  | No | To be addressed through the interregional process
|  | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 316.4 | 106.42 | 106.52 | K02 | PN_P2-3_PN-115-19B_SRT-A |  | No | To be addressed through the interregional process