## Summer GenDeliv
2034 RTEP PJM Generator Deliverability Result (Summer) | [19 empty] | Conductor/Transformer Limit
FG # Status | FG # | FG Index # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Cont Name | ContType | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-2034GD-LL93 | 93 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P4_144-45-BT7-8___SRT-A | Breaker | 1612 | 2160.4 | 2154.2 | 134.02 | 133.63 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL94 | 94 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P4_144-45-BT7-8___SRT-A | Breaker | 1612 | 2152.1 | 2154.1 | 133.5 | 133.63 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL95 | 95 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | 1612 | 2155.9 | 2148.3 | 133.74 | 133.27 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL96 | 96 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | 1612 | 2147.5 | 2148.2 | 133.22 | 133.26 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL97 | 97 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P4_175-45-BT2122__SRT-A | Breaker | 1612 | 2155.4 | 2147.7 | 133.71 | 133.23 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL98 | 98 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P4_175-45-BT2126__SRT-A | Breaker | 1612 | 2160.2 | 2147.6 | 134.01 | 133.23 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL99 | 99 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P4_175-45-BT2122__SRT-A | Breaker | 1612 | 2147 | 2147.6 | 133.19 | 133.22 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL100 | 100 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P4_175-45-BT2126__SRT-A | Breaker | 1612 | 2151.9 | 2147.5 | 133.49 | 133.22 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL101 | 101 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P4_175-45-BT2526__SRT-A | Breaker | 1612 | 2160.2 | 2147.5 | 134.01 | 133.22 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL102 | 102 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P4_175-45-BT2526__SRT-A | Breaker | 1612 | 2151.9 | 2147.3 | 133.49 | 133.21 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL333 | 333 | 270855 | POWERTON ; R | 349662 | 7TAZEWELL | 1 | 345 | 222/357 | COMED_P7-1_345-L9806__R-S_+_345-L19601_B-S_SRT-A | Tower | 1489 | 1930.8 | 1904.4 | 129.67 | 127.9 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL8 | 8 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P1-2_345-L14427__B-R_SRT-A | Single | 1612 | 2060.4 | 2052.6 | 127.82 | 127.34 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL9 | 9 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P1-2_345-L14427__B-R_SRT-A | Single | 1612 | 2052.1 | 2052.6 | 127.3 | 127.33 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL10 | 10 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P1-2_345-L0626__B-R_SRT-A | Single | 1612 | 2065.3 | 2052.5 | 128.12 | 127.32 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL11 | 11 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P1-2_345-L0626__B-R_SRT-A | Single | 1612 | 2056.9 | 2052.3 | 127.6 | 127.32 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL291 | 291 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | 1612 | 1845.9 | 1834.8 | 114.51 | 113.82 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL292 | 292 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | 1612 | 1837.5 | 1834.7 | 113.99 | 113.81 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL14 | 14 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | COMED_P1-2_345-L30003_B-R_SRT-A_+_COMED_P1-2_345-L93407_B-R_SRT-A | Single | 1612 | 1798.8 | 1785.1 | 111.59 | 110.74 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL15 | 15 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | COMED_P1-2_345-L30003_B-R_SRT-A_+_COMED_P1-2_345-L93407_B-R_SRT-A | Single | 1612 | 1790.5 | 1784.9 | 111.07 | 110.72 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL138 | 138 | 272148 | KESLINGER; R | 270732 | ELECT JCT;1B | 1 | 345 | 222 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | 1856 | 1963.4 | 1983.8 | 105.78 | 106.88 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL139 | 139 | 272148 | KESLINGER; R | 270732 | ELECT JCT;1B | 1 | 345 | 222 | COMED_P4_175-45-BT2526__SRT-A | Breaker | 1856 | 1960.8 | 1978.9 | 105.65 | 106.62 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL140 | 140 | 272148 | KESLINGER; R | 270732 | ELECT JCT;1B | 1 | 345 | 222 | COMED_P4_175-45-BT2126__SRT-A | Breaker | 1856 | 1960.8 | 1978.9 | 105.65 | 106.62 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL141 | 141 | 272148 | KESLINGER; R | 270732 | ELECT JCT;1B | 1 | 345 | 222 | COMED_P4_175-45-BT2122__SRT-A | Breaker | 1856 | 1958.1 | 1978.8 | 105.5 | 106.62 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL24 | 24 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | Base Case | Single | 1441 | 1546.4 | 1535.2 | 107.32 | 106.53 | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-2034GD-LL25 | 25 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | Base Case | Single | 1441 | 1538.1 | 1535 | 106.74 | 106.52 | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-LL155 | 155 | 970168 | AG2-114 TAP | 270709 | COAL CITY; R | 1 | 345 | 222 | COMED_P4_907-45-BT2-3___SRT-A | Breaker | 1826 | 1930 | 1918 | 105.7 | 105.04 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL154 | 154 | 970168 | AG2-114 TAP | 270709 | COAL CITY; R | 1 | 345 | 222 | COMED_P4_905-45-BT3-4___SRT-A | Breaker | 1826 | 1930 | 1918 | 105.7 | 105.04 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL157 | 157 | 270853 | PONTIAC ; R | 970168 | AG2-114 TAP | 1 | 345 | 222 | COMED_P4_905-45-BT3-4___SRT-A | Breaker | 1826 | 1936.8 | 1917.7 | 106.07 | 105.02 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL156 | 156 | 270853 | PONTIAC ; R | 970168 | AG2-114 TAP | 1 | 345 | 222 | COMED_P4_907-45-BT2-3___SRT-A | Breaker | 1826 | 1936.8 | 1917.7 | 106.07 | 105.02 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL158 | 158 | 970168 | AG2-114 TAP | 270709 | COAL CITY; R | 1 | 345 | 222 | COMED_P4_905-45-BT2-3___SRT-A | Breaker | 1826 | 1927.2 | 1915.9 | 105.54 | 104.92 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | 2026W1-2034GD-LL159 | 159 | 270853 | PONTIAC ; R | 970168 | AG2-114 TAP | 1 | 345 | 222 | COMED_P4_905-45-BT2-3___SRT-A | Breaker | 1826 | 1934 | 1915.5 | 105.92 | 104.9 | Yes |  | The conductor limits for ComEd were not available at the time of window opening - please contact PJM if specific ratings are needed.