## Summary
2031 RTEP Short Circuit Result
Flowgate # | TO | BUS_NO | BUS | BREAKER | RATINGTYPE | Notes | DUTY_P | DUTY_A | BKR_CAPA | PJM Accepting Proposals | Reason for Exclusion | Comments
2026-W1-SC-1 | AEP | 243481 | 05CANAL 138.kV | 5 | S | 40kA | 107 | 42782.7 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-2 | AEP | 243511 | 05GAY 138.kV | 101 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-3 | AEP | 243511 | 05GAY 138.kV | 102 | S | 40kA | 122.7 | 49090.3 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-4 | AEP | 243511 | 05GAY 138.kV | 103 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-5 | AEP | 243511 | 05GAY 138.kV | 104 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-6 | AEP | 243511 | 05GAY 138.kV | 105 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-7 | AEP | 243532 | 05KIRK 138.kV | CAP BANK #2 AA | S | 40kA | 107.7 | 43072.1 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-8 | AEP | 243034 | 05MARQUI 138.kV | CAP BK SWR 1 Q1 | S | 31.5kA | 111.5 | 35136.6 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-9 | AEP | 243034 | 05MARQUI 138.kV | 138KV CAP BK Q2 | S | 31.5kA | 111.5 | 35136.6 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-10 | AEP | 243547 | 05MORSE 138.kV | AA | S | 45kA | 100.2 | 45097.9 | 45000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-11 | AEP | 243366 | 05ROB PK12 138.kV | AA CAP-145-150 | S | 40kA | 101.7 | 40690.8 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-12 | AEP | 242808 | 05SPORNS 138.kV | CS-EE | S | 31.5kA | 169.6 | 53423.2 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-13 | AEP | 242808 | 05SPORNS 138.kV | CS-FF | S | 31.5kA | 169.6 | 53423.2 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-14 | AEP | 242807 | 05SPORN 138.kV | CS-HH | S | 40kA | 129.4 | 51747.1 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-15 | AEP | 243575 | 05ST.CLR 138.kV | FF | S | 40kA | 117.1 | 46841.5 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-16 | AEP | 243127 | 05TIDD 1-2 138.kV | CS-EE | S | 31.5kA | 140.3 | 44196.8 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-17 | AEP | 243584 | 05VINE 138.kV | 105 | S | 40kA | 102.7 | 41065.8 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-18 | AEP | 243584 | 05VINE 138.kV | 108 | S | 40kA | 102.7 | 41065.8 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-19 | FE-APS | 235459 | DOUBS 230.kV | DJ1 | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-20 | FE-APS | 235459 | DOUBS 230.kV | DJ10 | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-21 | FE-APS | 235459 | DOUBS 230.kV | DJ11 | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-22 | FE-APS | 235459 | DOUBS 230.kV | DJ14_Prelim | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-23 | FE-APS | 235459 | DOUBS 230.kV | DJ15_Prelim | S | 63kA | 106.5 | 67066.1 | 63000 | Yes
2026-W1-SC-24 | FE-APS | 235459 | DOUBS 230.kV | DJ16_Prelim | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-25 | FE-APS | 235459 | DOUBS 230.kV | DJ4 | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-26 | FE-APS | 235459 | DOUBS 230.kV | DJ5 | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-27 | FE-APS | 235459 | DOUBS 230.kV | DJ6 | S | 63kA | 101.4 | 63890.1 | 63000 | Yes
2026-W1-SC-28 | FE-APS | 235481 | LIME KLN 230.kV | DOUBS 207_Pr | S | 40kA | 106.2 | 42497.4 | 40000 | Yes
2026-W1-SC-29 | FE-APS | 235481 | LIME KLN 230.kV | DOUBS 231_Pr | S | 40kA | 106.2 | 42497.4 | 40000 | Yes
2026-W1-SC-30 | FE-APS | 235481 | LIME KLN 230.kV | MCCAIN 232 | S | 40kA | 104.1 | 41637.9 | 40000 | Yes
2026-W1-SC-31 | FE-APS | 235481 | LIME KLN 230.kV | MONTGOMERY 2 | S | 40kA | 103.5 | 41403.4 | 40000 | Yes
2026-W1-SC-32 | FE-APS | 235481 | LIME KLN 230.kV | MONOCACY 222 | S | 40kA | 102.1 | 40840.7 | 40000 | Yes
2026-W1-SC-36 | FE-PN | 204539 | HUNTERTN 115.kV | B392 | T | 25.1kA | 140.3 | 35208.1 | 25102.2 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-38 | BGE | 220941 | H.RDGE 230.kV | 230-1 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-39 | BGE | 220941 | H.RDGE 230.kV | 230-2 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-40 | BGE | 220941 | H.RDGE 230.kV | 230-4 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-41 | BGE | 220941 | H.RDGE 230.kV | 230-5 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-42 | BGE | 220941 | H.RDGE 230.kV | 2312-A | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-43 | BGE | 220941 | H.RDGE 230.kV | 2312A/Future | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-44 | BGE | 220941 | H.RDGE 230.kV | 2314-A | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-45 | BGE | 220941 | H.RDGE 230.kV | 2316 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-46 | BGE | 220941 | H.RDGE 230.kV | 2318 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-47 | BGE | 220941 | H.RDGE 230.kV | 2332-A | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-48 | BGE | 220941 | H.RDGE 230.kV | 2334-A | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-49 | BGE | 220941 | H.RDGE 230.kV | 2338 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-50 | BGE | 220941 | H.RDGE 230.kV | Future | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-51 | BGE | 220941 | H.RDGE 230.kV | 230-1/2316 | S | 63kA | 102.7 | 64693.4 | 63000 | Yes
2026-W1-SC-52 | BGE | 220941 | H.RDGE 230.kV | 230-5/2332-A | S | 63kA | 102.7 | 64675.3 | 63000 | Yes
2026-W1-SC-53 | BGE | 220941 | H.RDGE 230.kV | 2334-A/230-2 | S | 63kA | 102.7 | 64679.3 | 63000 | Yes
2026-W1-SC-54 | BGE | 220941 | H.RDGE 230.kV | 2314-A/230-4 | S | 63kA | 102.6 | 64645 | 63000 | Yes
2026-W1-SC-55 | BGE | 220941 | H.RDGE 230.kV | 2318/2338 | S | 63kA | 102.6 | 64651.9 | 63000 | Yes
2026-W1-SC-63 | DOM | 313827 | EVRGRN MILLS 230.kV | 217232 | S | 63kA | 105.5 | 66463.1 | 63000 | Yes
2026-W1-SC-64 | DOM | 313827 | EVRGRN MILLS 230.kV | 218332 | S | 63kA | 105.5 | 66463.1 | 63000 | Yes
2026-W1-SC-65 | DOM | 313827 | EVRGRN MILLS 230.kV | 220932 | S | 63kA | 105.5 | 66463.1 | 63000 | Yes
2026-W1-SC-66 | DOM | 313827 | EVRGRN MILLS 230.kV | 221032 | S | 63kA | 105.5 | 66463.1 | 63000 | Yes
2026-W1-SC-67 | DOM | 313827 | EVRGRN MILLS 230.kV | H332 | S | 63kA | 105.5 | 66463.1 | 63000 | Yes
2026-W1-SC-68 | DOM | 313827 | EVRGRN MILLS 230.kV | H432 | S | 63kA | 105.5 | 66463.1 | 63000 | Yes
2026-W1-SC-69 | DOM | 313827 | EVRGRN MILLS 230.kV | H3T2183 | S | 63kA | 100 | 62986 | 63000 | Yes
2026-W1-SC-77 | DOM | 313815 | SPRINGHILL 230.kV | 201002 | S | 40kA | 103.5 | 41403.1 | 40000 | Yes
2026-W1-SC-78 | DOM | 313815 | SPRINGHILL 230.kV | 224702 | S | 40kA | 103.5 | 41403.1 | 40000 | Yes
2026-W1-SC-79 | DOM | 313815 | SPRINGHILL 230.kV | W02 | S | 40kA | 103.5 | 41403.1 | 40000 | Yes
2026-W1-SC-80 | DOM | 313815 | SPRINGHILL 230.kV | Y02 | S | 40kA | 103.5 | 41403.1 | 40000 | Yes
2026-W1-SC-81 | DOM | 313396 | SYCOLIN 230.kV | 231652 | S | 63kA | 104.4 | 65757.9 | 63000 | Yes
2026-W1-SC-82 | DOM | 313396 | SYCOLIN 230.kV | 231752 | S | 63kA | 104.4 | 65757.9 | 63000 | Yes
2026-W1-SC-83 | DOM | 313396 | SYCOLIN 230.kV | 233452 | S | 63kA | 104.4 | 65757.9 | 63000 | Yes
2026-W1-SC-84 | DOM | 313396 | SYCOLIN 230.kV | 233552 | S | 63kA | 104.4 | 65757.9 | 63000 | Yes
2026-W1-SC-85 | DOM | 313396 | SYCOLIN 230.kV | 2316T2334 | S | 63kA | 104.4 | 65757.9 | 63000 | Yes
2026-W1-SC-86 | DOM | 313396 | SYCOLIN 230.kV | 2317T2335 | S | 63kA | 104.4 | 65757.9 | 63000 | Yes
2026-W1-SC-87 | DOM | 313911 | TWINCREEK 230.kV | 20312 | S | 63kA | 107.6 | 67799.6 | 63000 | Yes
2026-W1-SC-88 | DOM | 313911 | TWINCREEK 230.kV | 231612 | S | 63kA | 107.6 | 67799.6 | 63000 | Yes
2026-W1-SC-89 | DOM | 313911 | TWINCREEK 230.kV | 231712 | S | 63kA | 107.6 | 67799.6 | 63000 | Yes
2026-W1-SC-90 | DOM | 313911 | TWINCREEK 230.kV | 232012 | S | 63kA | 107.6 | 67799.6 | 63000 | Yes
2026-W1-SC-91 | DOM | 313911 | TWINCREEK 230.kV | 203T2316 | S | 63kA | 106.5 | 67107.9 | 63000 | Yes
2026-W1-SC-92 | DOM | 313911 | TWINCREEK 230.kV | 2317T2320 | S | 63kA | 106.5 | 67107.9 | 63000 | Yes
2026-W1-SC-93 | DOM | 313751 | STRATUS 230.kV | 203152 | S | 63kA | 99.4 | 62617.2 | 63000 | Yes |  | Identified with 2030 base case. Verified attribed to 2024W1
2026-W1-SC-94 | DOM | 313751 | STRATUS 230.kV | 218852 | S | 63kA | 99.4 | 62617.2 | 63000 | Yes |  | Identified with 2030 base case. Verified attribed to 2024W1
2026-W1-SC-95 | DOM | 313751 | STRATUS 230.kV | 231052 | S | 63kA | 99.4 | 62617.2 | 63000 | Yes |  | Identified with 2030 base case. Verified attribed to 2024W1
2026-W1-SC-96 | DOM | 313751 | STRATUS 230.kV | 231252 | S | 63kA | 99.4 | 62617.2 | 63000 | Yes |  | Identified with 2030 base case. Verified attribed to 2024W1
2026-W1-SC-97 | DOM | 313751 | STRATUS 230.kV | 2188T2310 | S | 63kA | 98.7 | 62164.9 | 63000 | Yes |  | Identified with 2030 base case. Verified attribed to 2024W1
2026-W1-SC-98 | DOM | 313751 | STRATUS 230.kV | 2031T2312 | S | 63kA | 98.6 | 62099 | 63000 | Yes |  | Identified with 2030 base case. Verified attribed to 2024W1

## Substations
2031 RTEP Short Circuit Result
Flowgate # | TO | BUS_NO | BUS | BREAKER | RATINGTYPE | Notes | DUTY_P | DUTY_A | BKR_CAPA | PJM Accepting Proposals | Reason for Exclusion | Comments
2026-W1-SC-1 | AEP | 243481 | 05CANAL 138.kV | 5 | S | 40kA | 107 | 42782.7 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-2 | AEP | 243511 | 05GAY 138.kV | 101 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-3 | AEP | 243511 | 05GAY 138.kV | 102 | S | 40kA | 122.7 | 49090.3 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-4 | AEP | 243511 | 05GAY 138.kV | 103 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-5 | AEP | 243511 | 05GAY 138.kV | 104 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-6 | AEP | 243511 | 05GAY 138.kV | 105 | S | 40kA | 136.9 | 54769.2 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-7 | AEP | 243532 | 05KIRK 138.kV | CAP BANK #2 AA | S | 40kA | 107.7 | 43072.1 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-8 | AEP | 243034 | 05MARQUI 138.kV | CAP BK SWR 1 Q1 | S | 31.5kA | 111.5 | 35136.6 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-9 | AEP | 243034 | 05MARQUI 138.kV | 138KV CAP BK Q2 | S | 31.5kA | 111.5 | 35136.6 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-10 | AEP | 243547 | 05MORSE 138.kV | AA | S | 45kA | 100.2 | 45097.9 | 45000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-11 | AEP | 243366 | 05ROB PK12 138.kV | AA CAP-145-150 | S | 40kA | 101.7 | 40690.8 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-12 | AEP | 242808 | 05SPORNS 138.kV | CS-EE | S | 31.5kA | 169.6 | 53423.2 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-13 | AEP | 242808 | 05SPORNS 138.kV | CS-FF | S | 31.5kA | 169.6 | 53423.2 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-14 | AEP | 242807 | 05SPORN 138.kV | CS-HH | S | 40kA | 129.4 | 51747.1 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-15 | AEP | 243575 | 05ST.CLR 138.kV | FF | S | 40kA | 117.1 | 46841.5 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-16 | AEP | 243127 | 05TIDD 1-2 138.kV | CS-EE | S | 31.5kA | 140.3 | 44196.8 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-17 | AEP | 243584 | 05VINE 138.kV | 105 | S | 40kA | 102.7 | 41065.8 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-18 | AEP | 243584 | 05VINE 138.kV | 108 | S | 40kA | 102.7 | 41065.8 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-19 | FE-APS | 235459 | DOUBS 230.kV | DJ1 | S | 63kA | 106.5 | 67121.8 | 63000 | Yes
2026-W1-SC-28 | FE-APS | 235481 | LIME KLN 230.kV | DOUBS 207_Pr | S | 40kA | 106.2 | 42497.4 | 40000 | Yes
2026-W1-SC-33 | FE-APS | 235512 | STONEWAL 138.kV | STM_Prelim | T | 20kA | 167.2 | 33752 | 20189.2 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-34 | FE-APS | 235416 | UNION RD 138.kV | No. 1 XFMR C | S | 7kA | 133.7 | 9357.3 | 7000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-35 | FE-ATSI | 238685 | EASTLK138SYN 138.kV | 46-B-30 | S | 56.5A | 137 | 77428 | 56532 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-36 | FE-PN | 204539 | HUNTERTN 115.kV | B392 | T | 25.1kA | 140.3 | 35208.1 | 25102.2 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-37 | FE-PN | 204619 | PORTLAND 115.kV | B12 | T | 25.1kA | 120.4 | 30225.9 | 25102.2 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2026-W1-SC-38 | BGE | 220941 | H.RDGE 230.kV | 230-1 | S | 63kA | 103 | 64859.1 | 63000 | Yes
2026-W1-SC-56 | DOM | 313859 | BELMONT 230.kV | 231112 | S | 63kA | 107.1 | 67493.1 | 63000 | Yes
2026-W1-SC-59 | DOM | 314171 | BRAMBLETON 230.kV | 222702 | S | 63kA | 113.6 | 71538.4 | 63000 | Yes
2026-W1-SC-63 | DOM | 313827 | EVRGRN MILLS 230.kV | 217232 | S | 63kA | 105.5 | 66463.1 | 63000 | Yes
2026-W1-SC-69 | DOM | 313731 | PARAGON PARK 230.kV | 234832 | S | 63kA | 111.6 | 70288.4 | 63000 | Yes
2026-W1-SC-73 | DOM | 314072 | PLEASANTVIEW 230.kV | 2098T2377 | S | 63kA | 112.4 | 70828.1 | 63000 | Yes
2026-W1-SC-76 | DOM | 313815 | SPRINGHILL 230.kV | 201002 | S | 40kA | 103.5 | 41403.1 | 40000 | Yes
2026-W1-SC-80 | DOM | 313396 | SYCOLIN 230.kV | 231652 | S | 63kA | 104.4 | 65757.9 | 63000 | Yes
2026-W1-SC-86 | DOM | 313911 | TWINCREEK 230.kV | 20312 | S | 63kA | 107.6 | 67799.6 | 63000 | Yes