## N-0 Thermal
To be addressed through the interregional process
PJM N-0 Thermal Result (Summer 2031 Case) | [16 empty] | Conductor/Transformer Limit
FG # Status | FG# | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1201 | 111.1574 | 111.77 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1201 | 111.1574 | 111.76 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1201 | 109.2256 | 110.04 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N0-ST1 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345/345 | 222/222 | 1334 | 103.6507 | 103.36 | Single | 'BASE CASE' | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-N0-ST2 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345/345 | 222/222 | 1334 | 101.1694 | 102.78 | Single | 'BASE CASE' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N0-ST3 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345/345 | 222/222 | 1201 | 99.9584 | 100.33 | Single | 'BASE CASE' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 546 | 106.6117 | 106.62 | Single | 'BASE CASE' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 546 | 104.9817 | 105.03 | Single | 'BASE CASE' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## N-1 Thermal
To be addressed through the interregional process
PJM N-1 Thermal Result (Summer 2031 Case) | [16 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-N1-ST6 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 100 | 100.13 | Line_FB | 'AEP_P4_#5096_05HAYDEN 345_C2_SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST35 | 998470 | ELK GROVE 81 | 272457 | ELK GROVE; R | 1 | 138/138 | 222/222 | 480 | 99.4792 | 100.19 | Bus | 'COMED_P2-2_046_DP-345R__1_SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST33 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345/345 | 222/222 | 1201 | 99.9584 | 100.33 | Single | 'BASE CASE' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST23 | 270810 | LOCKPORT ; B | 270780 | ITASCA ; B | 1 | 345/345 | 222/222 | 1528 | 97.9843 | 100.45 | Line_FB | 'COMED_P4_120-45-L12002__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST34 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345/345 | 222/222 | 1726 | 100.6199 | 101.12 | Line_FB | 'COMED_P4_935-45-BT1-5___SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 99.9053 | 101.35 | Single | 'COMED_P1-2_345-L13821_R-R_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 100.6356 | 101.36 | Single | 'COMED_P1-2_345-L14419_R-N_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST22 | 270810 | LOCKPORT ; B | 270780 | ITASCA ; B | 1 | 345/345 | 222/222 | 1528 | 99.1754 | 101.63 | Line_FB | 'COMED_P4_120-45-L10322__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST24 | 270810 | LOCKPORT ; B | 270780 | ITASCA ; B | 1 | 345/345 | 222/222 | 1528 | 99.1754 | 101.63 | Bus | 'COMED_P2-2_120_LO-345R__2_SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST21 | 270810 | LOCKPORT ; B | 270780 | ITASCA ; B | 1 | 345/345 | 222/222 | 1528 | 99.1754 | 101.65 | Line_FB | 'COMED_P4_120-45-L11120__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST9 | 247896 | 05BOLTON | 243519 | 05HALLRD | 1 | 138/138 | 205/205 | 223 | 101.2556 | 101.89 | Tower | 'AEP_P7-1_#17439___SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 999901 | 6POSSUM1 | 314029 | 6DUMFRES TAP | 1 | 230/230 | 345/345 | 671 | 99.3145 | 101.94 | Line_FB | 'DVP_P4-2: 237T2001_SRT-S' | No | Dominions HVDC solution resolves this flowgate |  | 605 | 671 | N/A | 701 | 769 | 818 | N/A | 840 | 743 | 793 | N/A | 818
Informational-Only | N/A | 314286 | 6CHESTF A | 314284 | 3CHESTFLD | 1 | 230/115 | 345/345 | 267 | 98.0899 | 102.17 | Tower | 'DVP_P7-1: LN 208-259_SRT-SL' | No | Dominions HVDC solution resolves this flowgate |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST5 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 102.287 | 102.47 | Line_FB | 'AEP_P4_#10715_05COLE 345_C_SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 101.4672 | 102.75 | Single | 'COMED_P1-2_345-L13821_R-R_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 101.4672 | 102.76 | Single | 'COMED_P1-2_345-L13821_R-R_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 102.1974 | 102.77 | Single | 'COMED_P1-2_345-L14419_R-N_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST32 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345/345 | 222/222 | 1334 | 101.1694 | 102.78 | Single | 'BASE CASE' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230/230 | 226/226 | 666 | 103.2733 | 103.01 | Line_FB | 'PL_02_P42_001063_SRT-A' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST31 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345/345 | 222/222 | 1334 | 103.6507 | 103.36 | Single | 'BASE CASE' | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 103.0899 | 103.66 | Single | 'COMED_P1-2_345-L14419_R-N_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 102.3529 | 103.77 | Bus | 'COMED_P2-2_111_EJ-345B__1_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 102.4206 | 103.98 | Bus | 'COMED_P2-2_120_LO-345B__4_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 666 | 104.5946 | 104.37 | Line_FB | 'PL_02_P42_001063_SRT-A' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST25 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345/345 | 222/222 | 1656 | 102.5604 | 104.41 | Single | 'COMED_P1-2_345-L10807_R-S_SRT-A' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST29 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345/345 | 222/222 | 1656 | 102.6449 | 104.51 | Line_FB | 'COMED_P4_108-45-BT2-3___SRT-A' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 103.9148 | 105.18 | Bus | 'COMED_P2-2_111_EJ-345B__1_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 103.9148 | 105.19 | Bus | 'COMED_P2-2_111_EJ-345B__1_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST4 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138/138 | 205/205 | 223 | 104.843 | 105.32 | Tower | 'AEP_P7-1_#17440___SRT-A' | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230/230 | 345/345 | 355 | 104 | 105.34 | Line_FB | 'DVP_P4-2: ARL_250T258_SRT-A' | No | Dominions HVDC solution resolves this flowgate |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Active | 2026W1-N1-ST2 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138/138 | 205/205 | 350 | 103.8857 | 105.36 | Tower | 'AEP_P7-1_#18058___SRT-A' | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 103.9824 | 105.39 | Bus | 'COMED_P2-2_120_LO-345B__4_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 103.9824 | 105.4 | Bus | 'COMED_P2-2_120_LO-345B__4_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 104.1176 | 105.55 | Single | 'COMED_P1-2_345-L11124_B-N_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST15 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 105.5039 | 105.75 | Single | 'COMED_P1-2_345-L93505_B-S_SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 104.4895 | 106.13 | Line_FB | 'COMED_P4_108-45-BT5-6___SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 105.2062 | 106.17 | Single | 'COMED_P1-2_345-L10322_R-S_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST14 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 106.2107 | 106.32 | Single | 'COMED_P1-2_345-L11604_R-S_SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 105.7201 | 106.72 | Line_FB | 'COMED_P4_103-45-TR83____SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 105.7201 | 106.72 | Line_FB | 'COMED_P4_103-45-L10322__SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1479 | 105.7201 | 106.72 | Bus | 'COMED_P2-2_103_LS-345R__3_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 105.6795 | 106.96 | Single | 'COMED_P1-2_345-L11124_B-N_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 105.6795 | 106.97 | Single | 'COMED_P1-2_345-L11124_B-N_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST41 | 270810 | LOCKPORT ; B | 270808 | LISLE ; B | 1 | 345/345 | 222/222 | 1528 | 105.7461 | 107.2 | Line_FB | 'COMED_P4_108-45-BT7-12__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 106.0514 | 107.55 | Line_FB | 'COMED_P4_108-45-BT5-6___SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 106.0514 | 107.55 | Line_FB | 'COMED_P4_108-45-BT5-6___SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 106.7681 | 107.58 | Single | 'COMED_P1-2_345-L10322_R-S_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 106.7681 | 107.58 | Single | 'COMED_P1-2_345-L10322_R-S_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 107.2819 | 108.12 | Line_FB | 'COMED_P4_103-45-L10322__SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 107.2819 | 108.12 | Line_FB | 'COMED_P4_103-45-TR83____SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1479 | 107.2819 | 108.12 | Bus | 'COMED_P2-2_103_LS-345R__3_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 107.2819 | 108.13 | Line_FB | 'COMED_P4_103-45-L10322__SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 107.2819 | 108.13 | Line_FB | 'COMED_P4_103-45-TR83____SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1479 | 107.2819 | 108.13 | Bus | 'COMED_P2-2_103_LS-345R__3_SRT-A' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST46 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222/222 | 465 | 106.8817 | 108.36 | Line_FB | 'COMED_P4_120-45-L12005__SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST47 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222/222 | 465 | 106.8817 | 108.36 | Line_FB | 'COMED_P4_120-45-L12003__SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST49 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222/222 | 465 | 106.8817 | 108.36 | Bus | 'COMED_P2-2_120_LO-345B__3_SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST3 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138/138 | 205/205 | 223 | 107.8027 | 108.37 | Tower | 'AEP_P7-1_#17439___SRT-A' | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST42 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138/138 | 222/222 | 465 | 106.8387 | 108.46 | Line_FB | 'COMED_P4_120-45-L12003__SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST43 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138/138 | 222/222 | 465 | 106.8387 | 108.46 | Line_FB | 'COMED_P4_120-45-L12005__SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST45 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138/138 | 222/222 | 465 | 106.8387 | 108.46 | Bus | 'COMED_P2-2_120_LO-345B__3_SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST40 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 105.9424 | 108.83 | Tower | 'COMED_P7-1_345-L13821_R-R_+_345-L18502AB-N_SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST20 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 108.9856 | 109.54 | Line_FB | 'COMED_P4_935-45-BT1-9___SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST8 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 109.6861 | 109.99 | Tower | 'AEP_P7-1_#17440___SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1201 | 109.2256 | 110.04 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST48 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222/222 | 465 | 108.7097 | 110.24 | Bus | 'COMED_P2-2_120_LO-345B__6_SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N1-ST44 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138/138 | 222/222 | 465 | 108.6667 | 110.28 | Bus | 'COMED_P2-2_120_LO-345B__6_SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1201 | 111.1574 | 111.76 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1201 | 111.1574 | 111.77 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N1-ST52 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 110.7163 | 111.87 | Line_FB | 'COMED_P4_120-45-L10322__SRT-A' | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N1-ST53 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 110.7163 | 111.87 | Bus | 'COMED_P2-2_120_LO-345R__2_SRT-A' | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N1-ST51 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 110.5731 | 111.89 | Line_FB | 'COMED_P4_120-45-L11120__SRT-A' | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N1-ST7 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 112.7354 | 113.16 | Tower | 'AEP_P7-1_#17439___SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST28 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345/345 | 222/222 | 1656 | 111.7452 | 114.15 | Line_FB | 'COMED_P4_120-45-L12002__SRT-A' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST38 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 111.7801 | 114.38 | Line_FB | 'COMED_P4_120-45-L12002__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST27 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345/345 | 222/222 | 1656 | 111.9988 | 114.45 | Line_FB | 'COMED_P4_120-45-L10322__SRT-A' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST30 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345/345 | 222/222 | 1656 | 111.9988 | 114.45 | Bus | 'COMED_P2-2_120_LO-345R__2_SRT-A' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST26 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345/345 | 222/222 | 1656 | 111.9988 | 114.46 | Line_FB | 'COMED_P4_120-45-L11120__SRT-A' | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST37 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 112.5393 | 115.15 | Line_FB | 'COMED_P4_120-45-L10322__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST39 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 112.5393 | 115.15 | Bus | 'COMED_P2-2_120_LO-345R__2_SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST36 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 112.5524 | 115.17 | Line_FB | 'COMED_P4_120-45-L11120__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345/345 | 937 | 117.5347 | 115.95 | Line_FB | 'DVP_P4-2: ELM_H1T574_SRT-A' | No |  | M-3 project already in place to address the violation (DOM-2023-0023) | 887 | 937 | N/A | 1053 | 1139 | 1191 | N/A | 1312 | 1056 | 1101 | N/A | 1205
Active | 2026W1-N1-ST50 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 115.7593 | 116.76 | Line_FB | 'COMED_P4_120-45-L12002__SRT-A' | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N1-ST13 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 116.8914 | 117.52 | Single | 'COMED_P1-2_345-L10805_B-S_SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST19 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 116.8914 | 117.52 | Line_FB | 'COMED_P4_935-45-BT6-8___SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST18 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 117.0092 | 117.78 | Line_FB | 'COMED_P4_935-45-BT6-10__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST12 | 272393 | ROUND LK ;5R | 270999 | ANTIOCH ;RT | 1 | 138/138 | 222/222 | 223 | 117.13 | 120.01 | Tower | 'COMED_P7-1_345-L13821_R-R_+_345-L18502AB-N_SRT-A' | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N1-ST17 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 120.6937 | 121.38 | Line_FB | 'COMED_P4_935-45-BT9-10__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST10 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222/222 | 480 | 122.0208 | 123.56 | Line_FB | 'COMED_P4_184-45-BT16-17_SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-N1-ST11 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222/222 | 480 | 122.0208 | 123.56 | Line_FB | 'COMED_P4_184-45-BT22-23_SRT-A' | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-N1-ST16 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345/345 | 222/222 | 1528 | 123.5929 | 124.74 | Line_FB | 'COMED_P4_108-45-BT5-6___SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Summer 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026W1-N1-SVM1 | 271588 | GR 138 | 138 | 222 | 0.91883 | 1.001 | 0.92 | Line_FB | COMED_P4_001-45-BT1-2___SRT-A | Yes
Active | 2026W1-N1-SVM2 | 271588 | GR 138 | 138 | 222 | 0.91867 | 1.001 | 0.92 | Line_FB | COMED_P4_001-45-BT1-9___SRT-A | Yes

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Summer 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment

## N-1 Load Drop
PJM N-1 Load Drop Result (Summer 2031 Case)
FG # Status | FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational-Only | N/A | DVP_P7-1: LN 2165-2170_SRT-A | Tower | 345 | 0.0 | 415.5 | 415.5 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P1-2: LN 9812_SRT-S | Single | 345 | 0.0 | 305.0 | 305.0 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P1-2: LN 2375_SRT-A | Single | 345, None | 0.0 | 305.0 | 305.0 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: AE1157_256T9812_SRT-S | Line_FB | 345 | 0.0 | 305.0 | 305.0 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: FOU_2061T9812_SRT-S | Line_FB | 345 | 0.0 | 305 | 305.0 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: FOU_2125T9812_SRT-S | Line_FB | 345 | 0.0 | 305.0 | 305.0 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: 2375T9500_SRT-A | Line_FB | 345 | 0 | 305.0 | 305 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P2-1: LN 9812_SRT-A | P2_1 | 345 | 0.0 | 305.0 | 305.0 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-3: WSH_L142_SRT-A | Line_FB | 345 | 0.0 | 495.9 | 495.9 | No | Will be addressed through the supplemental process