## Summer GenDeliv
To be addressed through the interregional process
2031 RTEP PJM Generator Deliverability Result (Summer) | [19 empty] | Conductor/Transformer Limit
FG # Status | FG # | FG Index | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Cont Name | ContType | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-GD-S11 | 11 | 316479 | 3CHILTON | 314178 | 3LANCAST | 1 | 115 | 345 | DVP_P1-2: LN 1059_SRT-A | Single | 203 | 226.9 | 223.7 | 111.74 | 110.15 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | N/A | 248 | 232 | 240 | N/A | 276 | 229 | 236 | N/A | 271
Active | 2026W1-GD-S19 | 19 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | Base Case | Single | 1334 | 1437.5 | 1430 | 107.76 | 107.19 | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-GD-S39 | 39 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | Base Case | Single | 1334 | 1352.8 | 1371.2 | 101.41 | 102.79 | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S48 | 48 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | Base Case | Single | 1334 | 1362.5 | 1356.7 | 102.14 | 101.7 | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-GD-S49 | 49 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | Base Case | Single | 1201 | 1218 | 1218.9 | 101.41 | 101.49 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-GD-S53 | 53 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | Base Case | Single | 1334 | 1351.6 | 1345.3 | 101.32 | 100.85 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-GD-S179 | 179 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | COMED_P4_108-45-BT5-6___SRT-A | Breaker | 1528 | 1942.6 | 1950.3 | 127.13 | 127.64 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 236 | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | DVP_P4-2: ELM_H1T574_SRT-A | Breaker | 1053 | 1160.2 | 1143.9 | 110.18 | 108.64 | No |  | M-3 project already in place to address the violation (DOM-2023-0023) | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Active | 2026W1-GD-S181 | 181 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | COMED_P4_184-45-BT16-17_SRT-A | Breaker | 480 | 587.5 | 597.5 | 122.4 | 124.48 | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Informational-Only | N/A | 246 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | DVP_P4-2: ARL_250T258_SRT-A | Breaker | 355 | 378.5 | 383.2 | 106.61 | 107.95 | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Active | 2026W1-GD-S182 | 182 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | COMED_P4_184-45-BT22-23_SRT-A | Breaker | 480 | 587.5 | 597.5 | 122.4 | 124.48 | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-GD-S186 | 186 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | COMED_P4_935-45-BT9-10__SRT-A | Breaker | 1528 | 1886.7 | 1887.7 | 123.47 | 123.54 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-GD-S191 | 191 | 316479 | 3CHILTON | 314178 | 3LANCAST | 1 | 115 | 345 | DVP_P4-2: NRT_105952_SRT-S | Breaker | 248 | 303.9 | 300.7 | 122.52 | 121.23 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | N/A | 248 | 232 | 240 | N/A | 276 | 229 | 236 | N/A | 271
Active | 2026W1-GD-S192 | 192 | 316479 | 3CHILTON | 314178 | 3LANCAST | 1 | 115 | 345 | DVP_P4-2: NRT_L4T1059_SRT-S | Breaker | 248 | 303.9 | 300.7 | 122.52 | 121.23 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | N/A | 248 | 232 | 240 | N/A | 276 | 229 | 236 | N/A | 271
Active | 2026W1-GD-S208 | 208 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P4_120-45-L11120__SRT-A | Breaker | 1656 | 1859.9 | 1894.1 | 112.31 | 114.38 | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S209 | 209 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P4_120-45-L10322__SRT-A | Breaker | 1656 | 1859.9 | 1894 | 112.31 | 114.37 | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 304 | 999901 | 6POSSUM1 | 314029 | 6DUMFRES TAP | 1 | 230 | 345 | DVP_P4-2: 237T2001_SRT-S | Breaker | 701 | 694.5 | 714.2 | 99.08 | 101.89 | No | Violation resolved with Dominion's HVDC line |  | 605 | 671 | N/A | 701 | 769 | 818 | N/A | 840 | 743 | 793 | N/A | 818
Active | 2026W1-GD-S210 | 210 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P4_120-45-L12002__SRT-A | Breaker | 1656 | 1855.6 | 1890.5 | 112.05 | 114.16 | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S234 | 234 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P4_120-45-L12005__SRT-A | Breaker | 465 | 497.6 | 505.2 | 107.01 | 108.65 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S235 | 235 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P4_120-45-L12003__SRT-A | Breaker | 465 | 497.6 | 505.2 | 107.01 | 108.65 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S241 | 241 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P4_120-45-L12003__SRT-A | Breaker | 465 | 497.4 | 504.1 | 106.97 | 108.41 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 309 | 314820 | 6BALLSTN | 314120 | 6CLRNDNC | 1 | 230 | 345 | DVP_P4-2: ARL_250T258_SRT-A | Breaker | 301 | 284.1 | 305.5 | 94.39 | 101.49 | No | Violation resolved with Dominion's HVDC line |  | 301 | 301 | N/A | 301 | 301 | 301 | N/A | 301 | 301 | 301 | N/A | 301
Informational-Only | N/A | 44 | 231000 | CLAY_230 | 214235 | LINWOOD84 | 1 | 230 | 230/235 | PECO_P1-2_220-85_SRT-A/* $ DELCO $ PECO_P1-2_220-85 $ L | Single | 809 | 839.7 | 826.3 | 103.8 | 102.14 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Active | 2026W1-GD-S242 | 242 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P4_120-45-L12005__SRT-A | Breaker | 465 | 497.4 | 504.1 | 106.97 | 108.41 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 45 | 231001 | EDGEMR 5 | 231000 | CLAY_230 | 1 | 230 | 235 | PECO_P1-2_220-85_SRT-A/* $ DELCO $ PECO_P1-2_220-85 $ L | Single | 800 | 830.2 | 815.2 | 103.78 | 101.9 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 654 | 809 | N/A | 900 | 753 | 911 | N/A | 1017 | 732 | 890 | N/A | 992
Active | 2026W1-GD-S260 | 260 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P4_#10715_05COLE 345_C_SRT-A | Breaker | 223 | 236.5 | 237 | 106.06 | 106.26 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S263 | 263 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_105012_SRT-S | Breaker | 228 | 248 | 241.4 | 108.77 | 105.86 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026W1-GD-S264 | 264 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_102712_SRT-S | Breaker | 228 | 248 | 241.3 | 108.76 | 105.85 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Informational-Only | N/A | 325 | 231001 | EDGEMR 5 | 214236 | LINWOOD85 | 1 | 230 | 230/235 | DPL_P4_2_DPEM231_SRT-A | Breaker | 809 | 831.4 | 816.7 | 102.77 | 100.95 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Active | 2026W1-GD-S265 | 265 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_17112_SRT-SL | Breaker | 228 | 248 | 241.3 | 108.76 | 105.85 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026W1-GD-S266 | 266 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_4012_SRT-S | Breaker | 228 | 247.9 | 241.3 | 108.75 | 105.84 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026W1-GD-S287 | 287 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Breaker | 223 | 230.8 | 231.1 | 103.49 | 103.62 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S288 | 288 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P4_#10715_05COLE 345_C_SRT-A | Breaker | 223 | 229.3 | 230.1 | 102.83 | 103.2 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S311 | 311 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P4_#5097_05HAYDEN 345_D1_SRT-A | Breaker | 223 | 226 | 226.1 | 101.35 | 101.39 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S321 | 321 | 314178 | 3LANCAST | 313813 | 3OCRAN | 1 | 115 | 345 | DVP_P4-2: NRT_105952_SRT-S | Breaker | 268 | 276.2 | 270.8 | 103.04 | 101.03 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 226 | 233 | N/A | 268 | 321 | 331 | N/A | 381 | 306 | 316 | N/A | 363
Active | 2026W1-GD-S322 | 322 | 314178 | 3LANCAST | 313813 | 3OCRAN | 1 | 115 | 345 | DVP_P4-2: NRT_L4T1059_SRT-S | Breaker | 268 | 276.2 | 270.8 | 103.04 | 101.03 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 226 | 233 | N/A | 268 | 321 | 331 | N/A | 381 | 306 | 316 | N/A | 363
Informational-Only | N/A | 54 | 314286 | 6CHESTF A | 314338 | 6SOUWEST | 1 | 230 | 345 | DVP_P1-2: LN 563_SRT-S | Single | 662.7 | 670.5 | 667.8 | 101.18 | 100.77 | No | Violation resolved with Dominion's HVDC line |  | 684 | 705 | N/A | 811 | 758 | 781 | N/A | 899 | 745 | 768 | N/A | 883
Informational-Only | N/A | 60 | 231001 | EDGEMR 5 | 214236 | LINWOOD85 | 1 | 230 | 230/235 | PECO_P1-2_220-84_SRT-A/* $ DELCO $ PECO_P1-2_220-84 $ L | Single | 809 | 824 | 809.2 | 101.85 | 100.02 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Active | 2026W1-GD-S328 | 328 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH045_SRT-A/* $ DELCO $ PECO_P4_CHICH045 $ STBK | Breaker | 796 | 812.7 | 801.6 | 102.1 | 100.7 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Informational-Only | N/A | 6 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | Base Case | Single | 1201 | 1337.9 | 1339.9 | 111.4 | 111.56 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 7 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | Base Case | Single | 1201 | 1337.9 | 1339.8 | 111.4 | 111.56 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 12 | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | Base Case | Single | 1201 | 1314.8 | 1319.2 | 109.48 | 109.84 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 574 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | COMED_P2-2_103_LS-345R__3_SRT-A | Bus | 1479 | 1590.4 | 1593.6 | 107.53 | 107.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 575 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | COMED_P2-2_103_LS-345R__3_SRT-A | Bus | 1479 | 1590.4 | 1593.6 | 107.53 | 107.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 17 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | COMED_P1-2_345-L10322_R-S_SRT-A | Single | 1479 | 1582.8 | 1585.7 | 107.02 | 107.21 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 18 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | COMED_P1-2_345-L10322_R-S_SRT-A | Single | 1479 | 1582.8 | 1585.7 | 107.02 | 107.21 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-S329 | 329 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH365_SRT-A/* $ DELCO $ PECO_P4_CHICH365 $ STBK | Breaker | 796 | 811.5 | 801.6 | 101.94 | 100.7 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Informational-Only | N/A | 24 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | COMED_P1-2_345-L11124_B-N_SRT-A | Single | 1479 | 1566.3 | 1574.9 | 105.91 | 106.48 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 25 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | COMED_P1-2_345-L11124_B-N_SRT-A | Single | 1479 | 1566.3 | 1574.8 | 105.91 | 106.48 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 577 | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | COMED_P2-2_103_LS-345R__3_SRT-A | Bus | 1479 | 1567.3 | 1572.9 | 105.97 | 106.35 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 578 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | COMED_P2-2_120_LO-345B__4_SRT-A | Bus | 1479 | 1554.8 | 1568.9 | 105.12 | 106.08 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 579 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | COMED_P2-2_120_LO-345B__4_SRT-A | Bus | 1479 | 1554.8 | 1568.7 | 105.12 | 106.07 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-S330 | 330 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH195_SRT-A/* $ DELCO $ PECO_P4_CHICH195 $ STBK | Breaker | 796 | 812.7 | 801.5 | 102.1 | 100.7 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Active | 2026W1-GD-S331 | 331 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH435_SRT-A/* $ DELCO $ PECO_P4_CHICH435 $ STBK | Breaker | 796 | 811.8 | 801.3 | 101.99 | 100.67 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Active | 2026W1-GD-S336 | 336 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Breaker | 223 | 223.4 | 223.9 | 100.17 | 100.42 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 196 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_02_P42_001063_SRT-A | Breaker | 666 | 779 | 776.9 | 116.96 | 116.66 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 2 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | Base Case | Single | 546 | 637 | 635.7 | 116.67 | 116.44 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 198 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_02_P42_001063_SRT-A | Breaker | 666 | 770.1 | 767.9 | 115.63 | 115.29 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 3 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | Base Case | Single | 546 | 628.1 | 627 | 115.04 | 114.84 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 211 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P2-3_PN-115-0272-A_SRT-A | Breaker | 666 | 754.2 | 753.1 | 113.24 | 113.07 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 215 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P2-3_PN-115-19E_SRT-A | Breaker | 666 | 751.3 | 750.9 | 112.81 | 112.75 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 216 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P2-3_PN-115-0272-10_SRT-A | Breaker | 666 | 750.3 | 748.8 | 112.65 | 112.43 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 219 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P2-3_PN-115-0272-A_SRT-A | Breaker | 666 | 745.3 | 744.3 | 111.91 | 111.75 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 222 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P2-3_PN-115-19E_SRT-A | Breaker | 666 | 742.5 | 742.2 | 111.48 | 111.44 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 225 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P2-3_PN-115-0272-10_SRT-A | Breaker | 666 | 741.4 | 740 | 111.32 | 111.11 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 228 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-997-DRT-055_SRT-SL | Breaker | 180 | 197.7 | 196.8 | 109.84 | 109.34 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 229 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-3C_SRT-A | Breaker | 180 | 197.7 | 196.8 | 109.84 | 109.34 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 230 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-997-DRT-068_SRT-SL | Breaker | 180 | 200.7 | 196.8 | 111.51 | 109.34 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 231 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-020-DRT_SRT-SL | Breaker | 180 | 198.5 | 196 | 110.29 | 108.91 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 247 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P42_100926_SRT-A | Breaker | 666 | 720 | 718.8 | 108.1 | 107.92 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 674 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P71_102649_SRT-A | Tower | 666 | 718.6 | 717.3 | 107.89 | 107.71 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 576 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | AP_P2-2_WP-230-005T_SRT-A | Bus | 666 | 714.7 | 714 | 107.31 | 107.2 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 21 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P1-2_PN-115-037_SRT-A | Single | 666 | 713.7 | 712.4 | 107.16 | 106.96 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 257 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P42_100926_SRT-A | Breaker | 666 | 711.1 | 710 | 106.77 | 106.6 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 677 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P71_102649_SRT-A | Tower | 666 | 709.7 | 708.5 | 106.56 | 106.38 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 580 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_08_P22_102801_SRT-A | Bus | 666 | 706.7 | 705.2 | 106.1 | 105.89 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 581 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | AP_P2-2_WP-230-005T_SRT-A | Bus | 666 | 705.8 | 705.2 | 105.98 | 105.89 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 27 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P1-2_PN-115-037_SRT-A | Single | 666 | 704.8 | 703.6 | 105.83 | 105.65 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 586 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_08_P22_102801_SRT-A | Bus | 666 | 697.8 | 696.5 | 104.77 | 104.57 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 29 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_40_P11_001448_SRT-A | Single | 666 | 688.5 | 694.9 | 103.37 | 104.34 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 30 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_40_P11_001449_SRT-A | Single | 666 | 688.2 | 694.6 | 103.33 | 104.3 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 588 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_08_P22_102799_SRT-A | Bus | 666 | 693.2 | 692.3 | 104.09 | 103.95 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 34 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 208918 SUSQ 1 24.0 1 _SRT-A | Single | 666 | 689.9 | 687.4 | 103.59 | 103.22 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 35 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P12_000189_SRT-A | Single | 666 | 688.6 | 686.8 | 103.39 | 103.12 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 36 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_40_P11_001448_SRT-A | Single | 666 | 679.6 | 686.1 | 102.04 | 103.01 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 590 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | AP_P2-2_WP-230-004_SRT-A | Bus | 666 | 686.6 | 685.8 | 103.1 | 102.97 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 37 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_40_P11_001449_SRT-A | Single | 666 | 679.3 | 685.8 | 102 | 102.97 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 592 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_11_P22_000176_SRT-A | Bus | 666 | 684.5 | 684.1 | 102.78 | 102.72 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 686 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_08_P71_101751_SRT-A | Tower | 666 | 683.9 | 683.8 | 102.68 | 102.67 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 593 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_08_P22_102799_SRT-A | Bus | 666 | 684.4 | 683.5 | 102.76 | 102.63 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 687 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P71_101752_SRT-A | Tower | 666 | 682.7 | 682.5 | 102.51 | 102.48 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 688 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_18_P71_103518_SRT-A | Tower | 666 | 683.2 | 682 | 102.58 | 102.4 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 689 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PECO_P7-1_220-0607_SRT-A/* $ CHESCO $ PECO_P7-1_220-0607 $ DCT | Tower | 666 | 680.7 | 680.5 | 102.21 | 102.18 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 46 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | 208918 SUSQ 1 24.0 1 _SRT-A | Single | 666 | 681 | 678.6 | 102.26 | 101.9 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 303 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-3C_SRT-A | Breaker | 297 | 301.2 | 302.6 | 101.41 | 101.89 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 301 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-997-DRT-055_SRT-SL | Breaker | 297 | 301.2 | 302.6 | 101.41 | 101.89 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 302 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-997-DRT-068_SRT-SL | Breaker | 297 | 305.5 | 302.6 | 102.86 | 101.89 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 47 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P12_000189_SRT-A | Single | 666 | 679.8 | 678 | 102.07 | 101.8 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 596 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | AP_P2-2_WP-230-004_SRT-A | Bus | 666 | 677.8 | 677.1 | 101.77 | 101.66 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 597 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_11_P22_000176_SRT-A | Bus | 666 | 675.7 | 675.4 | 101.45 | 101.41 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 693 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_08_P71_101751_SRT-A | Tower | 666 | 675 | 675.1 | 101.35 | 101.36 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 694 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P71_101752_SRT-A | Tower | 666 | 673.8 | 673.8 | 101.18 | 101.17 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 313 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-020-DRT_SRT-SL | Breaker | 297 | 299.6 | 300.4 | 100.87 | 101.15 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 695 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_18_P71_103518_SRT-A | Tower | 666 | 674.3 | 673.3 | 101.25 | 101.09 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 696 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PECO_P7-1_220-0607_SRT-A/* $ CHESCO $ PECO_P7-1_220-0607 $ DCT | Tower | 666 | 671.8 | 671.8 | 100.88 | 100.86 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S567 | 567 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P2-2_120_LO-345R__2_SRT-A | Bus | 1656 | 1859.9 | 1894 | 112.31 | 114.37 | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S569 | 569 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P2-2_120_LO-345B__6_SRT-A | Bus | 465 | 506.1 | 513.9 | 108.84 | 110.52 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S570 | 570 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P2-2_120_LO-345B__6_SRT-A | Bus | 465 | 505.9 | 512.5 | 108.8 | 110.21 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S571 | 571 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P2-2_120_LO-345B__3_SRT-A | Bus | 465 | 497.6 | 505.2 | 107.01 | 108.65 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S573 | 573 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P2-2_120_LO-345B__3_SRT-A | Bus | 465 | 497.4 | 504.1 | 106.97 | 108.41 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S599 | 599 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P2-2_CHI230B1_SRT-A/* $ DELCO $ PECO_P2-2_CHI230B1 $ B | Bus | 796 | 811.5 | 801.6 | 101.94 | 100.7 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Active | 2026W1-GD-S666 | 666 | 272393 | ROUND LK ;5R | 270999 | ANTIOCH ;RT | 1 | 138 | 222 | COMED_P7-1_345-L13821_R-R_+_345-L18502AB-N_SRT-A | Tower | 230 | 260.4 | 268.3 | 113.22 | 116.64 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-GD-S667 | 667 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P7-1_#17439___SRT-A | Tower | 223 | 258.1 | 259 | 115.72 | 116.13 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S668 | 668 | 342559 | 4BOONE CO | 250054 | 08LONGBR | 1 | 138 | 212/320 | 34541 34553_SRT-A | Tower | 230 | 267.1 | 263.7 | 116.14 | 114.67 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 230 | N/A | 247 | 343 | 354 | N/A | 364 | 211 | 230 | N/A | 247
Active | 2026W1-GD-S669 | 669 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P7-1_#17440___SRT-A | Tower | 223 | 251.2 | 251.9 | 112.66 | 112.96 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S670 | 670 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P7-1_#17439___SRT-A | Tower | 223 | 247.9 | 249.2 | 111.18 | 111.75 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S672 | 672 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P7-1_#17440___SRT-A | Tower | 223 | 241.3 | 242.4 | 108.21 | 108.7 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S676 | 676 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | AEP_P7-1_#18058___SRT-A | Tower | 350 | 367.6 | 372.7 | 105.02 | 106.5 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Active | 2026W1-GD-S679 | 679 | 247896 | 05BOLTON | 243519 | 05HALLRD | 1 | 138 | 205 | AEP_P7-1_#17439___SRT-A | Tower | 223 | 232.4 | 233.8 | 104.22 | 104.85 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S685 | 685 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P7-1_#16019___SRT-A | Tower | 223 | 229 | 229.2 | 102.7 | 102.76 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S692 | 692 | 247896 | 05BOLTON | 243519 | 05HALLRD | 1 | 138 | 205 | AEP_P7-1_#17440___SRT-A | Tower | 223 | 225.6 | 226.8 | 101.16 | 101.71 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 248 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | COMED_P4_103-45-TR83____SRT-A | Breaker | 1479 | 1590.4 | 1593.6 | 107.53 | 107.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 249 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | COMED_P4_103-45-L10322__SRT-A | Breaker | 1479 | 1590.4 | 1593.6 | 107.53 | 107.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 250 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | COMED_P4_103-45-L10322__SRT-A | Breaker | 1479 | 1590.4 | 1593.6 | 107.53 | 107.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 251 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | COMED_P4_103-45-TR83____SRT-A | Breaker | 1479 | 1590.4 | 1593.6 | 107.53 | 107.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 254 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | COMED_P4_108-45-BT5-6___SRT-A | Breaker | 1479 | 1571.5 | 1584.2 | 106.25 | 107.11 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 255 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | COMED_P4_108-45-BT5-6___SRT-A | Breaker | 1479 | 1571.5 | 1584.1 | 106.25 | 107.11 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 259 | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | COMED_P4_103-45-TR83____SRT-A | Breaker | 1479 | 1567.3 | 1572.9 | 105.97 | 106.35 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 258 | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | COMED_P4_103-45-L10322__SRT-A | Breaker | 1479 | 1567.3 | 1572.9 | 105.97 | 106.35 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-S698 | 698 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P7-1_#16019___SRT-A | Tower | 223 | 223.4 | 224 | 100.19 | 100.44 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A

## Summer IPD
Will be addressed through the interregional process
2031 RTEP PJM Individual Plant Deliverability Result (Summer) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-IPD-S1 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 68 | - | 119.92 | 124.4 | AE2-283 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026W1-IPD-S2 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 68 | - | 117.65 | 122.06 | AE2-185 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026W1-IPD-S3 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 70 | - | 116.46 | 120.81 | AE2-283 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026W1-IPD-S4 | 250054 | 08LONGBR | 342559 | 4BOONE CO | 1 | 138 | 212/320 | 230 | 230.7 | 101.93 | 100.3 | AC2-075 | 34541 34553_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 230 | N/A | 247 | 343 | 354 | N/A | 364 | 211 | 230 | N/A | 247
Active | 2026W1-IPD-S5 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 110 | 131.2 | 119.64 | 119.26 | AC2-079 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026W1-IPD-S6 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 70 | - | 114.25 | 118.55 | AE2-185 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026W1-IPD-S7 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 258.5 | 115.47 | 115.92 | AD1-081 | AEP_P7-1_#17439___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S8 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 251.4 | 112.41 | 112.75 | AD1-081 | AEP_P7-1_#17440___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S9 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 248.6 | 110.87 | 111.48 | AD1-081 | AEP_P7-1_#17439___SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S10 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 241.8 | 107.91 | 108.44 | AD1-081 | AEP_P7-1_#17440___SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S11 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 235.8 | 105.51 | 105.75 | AD1-081 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S12 | 243519 | 05HALLRD | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 233.4 | 103.96 | 104.65 | AD1-081 | AEP_P7-1_#17439___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S13 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 230.3 | 103.09 | 103.26 | AD1-081 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S14 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 228.9 | 102.2 | 102.63 | AD1-081 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S15 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 228.1 | 102.19 | 102.29 | AD1-081 | AEP_P7-1_#16019___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S16 | 243519 | 05HALLRD | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 226.4 | 100.89 | 101.51 | AD1-081 | AEP_P7-1_#17440___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S17 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 68 | - | 112.45 | 116.62 | AF2-404 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026W1-IPD-S18 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 70 | - | 109.2 | 113.27 | AF2-404 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026W1-IPD-S19 | 314691 | 3FARMVIL | 314726 | 3WILLIS | 1 | 115 | 345 | 204.9 | 226.4 | 114.61 | 110.46 | AF2-222 | DVP_P1-2: LN 9607_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026W1-IPD-S20 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 85.5 | 93.2 | 105.97 | 108.99 | AC1-145 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 355 | 381.6 | 106.49 | 107.5 | AF1-124 | DVP_P4-2: ARL_250T258_SRT-A | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Active | 2026W1-IPD-S21 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 235.2 | 105.33 | 105.49 | AE2-148 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S22 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 229.2 | 102.67 | 102.76 | AE2-148 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S23 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 228.1 | 101.92 | 102.27 | AE2-148 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S24 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 227.4 | 101.95 | 101.97 | AE2-148 | AEP_P7-1_#16019___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S25 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 224.2 | 100.53 | 100.54 | AE2-148 | AEP_P4_#5097_05HAYDEN 345_D1_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 355 | 381.6 | 106.48 | 107.49 | AF1-123 | DVP_P4-2: ARL_250T258_SRT-A | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 355 | 381.5 | 106.45 | 107.46 | AF1-125 | DVP_P4-2: ARL_250T258_SRT-A | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Active | 2026W1-IPD-S26 | 314273 | 3BAKRS P | 314280 | 3NEWBOHE | 1 | 115 | 345 | 110 | 116.4 | 104.5 | 105.85 | AC2-079 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1109.5 | 106.71 | 105.37 | AF1-124 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1109.4 | 106.7 | 105.36 | AF1-123 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1109.2 | 106.67 | 105.33 | AF1-125 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1101.3 | 105.97 | 104.59 | LTFIMP_O-066 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Active | 2026W1-IPD-S27 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 110 | 114.5 | 103.21 | 104.13 | AD1-082 | DVP_P1-2: LN 23_SRT-A | No |  |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1096.8 | 105.52 | 104.16 | AE1-173 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1085.2 | 104.47 | 103.06 | AD1-105 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Active | 2026W1-IPD-S28 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 85.5 | 88.3 | 99.91 | 103.22 | AC1-042 | DVP_P1-2: LN 173_SRT-A | No |  |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1084.2 | 104.35 | 102.97 | AC1-158 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1084.2 | 104.36 | 102.96 | AC1-191 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Active | 2026W1-IPD-S29 | 314532 | 3OAKRI23 | 314536 | 3SUFFOLK | 1 | 115 | 345 | 110 | 112.7 | 101.12 | 102.47 | AC2-079 | DVP_P1-2: LN 106_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026W1-IPD-S30 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 85.5 | 87.2 | 97.87 | 102 | AE2-283 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026W1-IPD-S31 | 250054 | 08LONGBR | 342559 | 4BOONE CO | 1 | 138 | 212/320 | 230 | 232.4 | 102.81 | 101.04 | AF1-233 | 34541 34553_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 230 | N/A | 247 | 343 | 354 | N/A | 364 | 211 | 230 | N/A | 247
Active | 2026W1-IPD-S32 | 250054 | 08LONGBR | 342559 | 4BOONE CO | 1 | 138 | 212/320 | 230 | 234.6 | 103.84 | 101.99 | AF2-111 | 34541 34553_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 230 | N/A | 247 | 343 | 354 | N/A | 364 | 211 | 230 | N/A | 247
Active | 2026W1-IPD-S33 | 314691 | 3FARMVIL | 314726 | 3WILLIS | 1 | 115 | 345 | 204.9 | 207.4 | 106.07 | 101.2 | AG1-285 | DVP_P1-2: LN 9607_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026W1-IPD-S34 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 110 | 111 | 100.26 | 100.9 | AB2-161 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026W1-IPD-S35 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1878.7 | 121.91 | 122.95 | AB2-132 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S36 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1903.4 | 112.36 | 114.94 | AB2-132 | COMED_P4_120-45-L11120__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S37 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1903.2 | 112.36 | 114.93 | AB2-132 | COMED_P2-2_120_LO-345R__2_SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S38 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1903.2 | 112.36 | 114.93 | AB2-132 | COMED_P4_120-45-L10322__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S39 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1897.2 | 112.1 | 114.56 | AB2-132 | COMED_P4_120-45-L12002__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1591.1 | 106.35 | 107.58 | AB2-132 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1591 | 106.35 | 107.57 | AB2-132 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1570.2 | 104.78 | 106.16 | AB2-132 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1570.1 | 104.65 | 106.16 | AB2-132 | COMED_P2-2_120_LO-345B__4_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1570.1 | 104.65 | 106.16 | AB2-132 | COMED_P4_120-45-L11124__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1570.1 | 104.65 | 106.16 | AB2-132 | COMED_P4_120-45-L10321__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1570 | 104.65 | 106.15 | AB2-132 | COMED_P4_120-45-L10321__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1570 | 104.65 | 106.15 | AB2-132 | COMED_P4_120-45-L11124__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1570 | 104.65 | 106.15 | AB2-132 | COMED_P2-2_120_LO-345B__4_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S40 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1895.6 | 122.95 | 124.06 | AD1-067 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S41 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1847.3 | 120.25 | 120.9 | AD1-067 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S42 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1918.8 | 124.49 | 125.57 | AD1-100 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S43 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1866 | 121.38 | 122.12 | AD1-100 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S44 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1897.5 | 111.92 | 114.58 | AD1-100 | COMED_P4_120-45-L12002__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S45 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1882.5 | 122.14 | 123.2 | AD2-134 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S46 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1837.9 | 119.67 | 120.28 | AD2-134 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S47 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1901.6 | 112.25 | 114.83 | AD2-134 | COMED_P4_120-45-L11120__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S48 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1901.5 | 112.25 | 114.82 | AD2-134 | COMED_P4_120-45-L10322__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S49 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1901.5 | 112.25 | 114.82 | AD2-134 | COMED_P2-2_120_LO-345R__2_SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S50 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1895.4 | 111.99 | 114.46 | AD2-134 | COMED_P4_120-45-L12002__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1590.1 | 106.27 | 107.51 | AD2-134 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1589.9 | 106.27 | 107.5 | AD2-134 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1569.1 | 104.7 | 106.09 | AD2-134 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1569 | 104.57 | 106.09 | AD2-134 | COMED_P4_120-45-L11124__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1569 | 104.57 | 106.09 | AD2-134 | COMED_P4_120-45-L10321__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1569 | 104.57 | 106.09 | AD2-134 | COMED_P2-2_120_LO-345B__4_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1568.9 | 104.57 | 106.08 | AD2-134 | COMED_P4_120-45-L10321__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1568.9 | 104.57 | 106.08 | AD2-134 | COMED_P2-2_120_LO-345B__4_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1568.9 | 104.57 | 106.08 | AD2-134 | COMED_P4_120-45-L11124__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S51 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1888.6 | 122.53 | 123.6 | AE1-114 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S52 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1841.9 | 119.92 | 120.54 | AE1-114 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S53 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1895.4 | 122.95 | 124.05 | AE2-035 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S54 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1846.9 | 120.22 | 120.87 | AE2-035 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S55 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1884.8 | 122.19 | 123.35 | AE2-255 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S56 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1897.2 | 123.05 | 124.16 | AE2-341 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S57 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1880.2 | 122.01 | 123.05 | AF1-280 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S58 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1888.5 | 122.52 | 123.6 | AF1-296 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S59 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1842.1 | 119.93 | 120.56 | AF1-296 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S60 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1889.6 | 122.77 | 123.66 | AF2-027 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S61 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1843.5 | 120.06 | 120.65 | AF2-027 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S62 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1888.4 | 111.52 | 114.03 | AF2-027 | COMED_P4_120-45-L11120__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S63 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1888.2 | 111.52 | 114.02 | AF2-027 | COMED_P2-2_120_LO-345R__2_SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S64 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1888.2 | 111.52 | 114.02 | AF2-027 | COMED_P4_120-45-L10322__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S65 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1882.2 | 111.27 | 113.66 | AF2-027 | COMED_P4_120-45-L12002__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1592.2 | 106.9 | 107.65 | AF2-027 | COMED_P2-2_103_LS-345R__3_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1592.2 | 106.9 | 107.65 | AF2-027 | COMED_P4_103-45-L10322__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1592.2 | 106.9 | 107.65 | AF2-027 | COMED_P4_103-45-TR83____SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1592.1 | 106.9 | 107.65 | AF2-027 | COMED_P2-2_103_LS-345R__3_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1592.1 | 106.9 | 107.65 | AF2-027 | COMED_P4_103-45-TR83____SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1592.1 | 106.9 | 107.65 | AF2-027 | COMED_P4_103-45-L10322__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1571.3 | 105.34 | 106.24 | AF2-027 | COMED_P4_103-45-TR83____SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1571.3 | 105.34 | 106.24 | AF2-027 | COMED_P4_103-45-L10322__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1571.3 | 105.34 | 106.24 | AF2-027 | COMED_P2-2_103_LS-345R__3_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S66 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1865.3 | 121.32 | 122.08 | AF2-182 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1588.1 | 106.16 | 107.37 | AF2-182 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1587.9 | 106.16 | 107.36 | AF2-182 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S67 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1875.9 | 121.7 | 122.77 | AF2-200 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S68 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1902.7 | 112.28 | 114.9 | AF2-200 | COMED_P4_120-45-L11120__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S69 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1902.6 | 112.28 | 114.89 | AF2-200 | COMED_P2-2_120_LO-345R__2_SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S70 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1902.6 | 112.28 | 114.89 | AF2-200 | COMED_P4_120-45-L10322__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S71 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1896.5 | 112.02 | 114.52 | AF2-200 | COMED_P4_120-45-L12002__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1590.2 | 106.27 | 107.52 | AF2-200 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1590.1 | 106.27 | 107.51 | AF2-200 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1569.2 | 104.71 | 106.1 | AF2-200 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1569.2 | 104.58 | 106.1 | AF2-200 | COMED_P2-2_120_LO-345B__4_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1569.2 | 104.58 | 106.1 | AF2-200 | COMED_P4_120-45-L11124__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1569.2 | 104.58 | 106.1 | AF2-200 | COMED_P4_120-45-L10321__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1569 | 104.58 | 106.09 | AF2-200 | COMED_P2-2_120_LO-345B__4_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1569 | 104.58 | 106.09 | AF2-200 | COMED_P4_120-45-L10321__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1569 | 104.58 | 106.09 | AF2-200 | COMED_P4_120-45-L11124__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S72 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1908 | 123.74 | 124.87 | AF2-226 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S73 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1857.9 | 120.92 | 121.59 | AF2-226 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S74 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1908 | 123.74 | 124.87 | AF2-319 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S75 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1857.9 | 120.92 | 121.59 | AF2-319 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S76 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 480 | 587 | 120.72 | 122.29 | AF2-349 | COMED_P4_184-45-BT16-17_SRT-A | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-IPD-S77 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 480 | 587 | 120.72 | 122.29 | AF2-349 | COMED_P4_184-45-BT22-23_SRT-A | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-IPD-S78 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1855.5 | 120.58 | 121.43 | AF2-349 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S79 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 230 | 277.1 | 117.53 | 120.48 | AF2-349 | COMED_P7-1_345-L13821_R-R_+_345-L18502AB-N_SRT-A | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-IPD-S80 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1880.5 | 111.14 | 113.56 | AF2-349 | COMED_P4_120-45-L11120__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S81 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1880.3 | 111.14 | 113.55 | AF2-349 | COMED_P2-2_120_LO-345R__2_SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S82 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1880.3 | 111.14 | 113.55 | AF2-349 | COMED_P4_120-45-L10322__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S83 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1877 | 110.88 | 113.34 | AF2-349 | COMED_P4_120-45-L12002__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1591.7 | 106.94 | 107.62 | AF2-349 | COMED_P4_103-45-TR83____SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1591.7 | 106.94 | 107.62 | AF2-349 | COMED_P4_103-45-L10322__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1591.7 | 106.94 | 107.62 | AF2-349 | COMED_P2-2_103_LS-345R__3_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1591.6 | 106.94 | 107.61 | AF2-349 | COMED_P4_103-45-L10322__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1591.6 | 106.94 | 107.61 | AF2-349 | COMED_P4_103-45-TR83____SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1591.6 | 106.94 | 107.61 | AF2-349 | COMED_P2-2_103_LS-345R__3_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1570.8 | 105.38 | 106.21 | AF2-349 | COMED_P4_103-45-L10322__SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1570.8 | 105.38 | 106.21 | AF2-349 | COMED_P4_103-45-TR83____SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1479 | 1570.8 | 105.38 | 106.21 | AF2-349 | COMED_P2-2_103_LS-345R__3_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S84 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1910.2 | 123.9 | 125.01 | AF2-441 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S85 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1858.5 | 120.98 | 121.63 | AF2-441 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S86 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1887.8 | 122.47 | 123.55 | AG1-118 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S87 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1841.7 | 119.9 | 120.53 | AG1-118 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S88 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1901.4 | 112.24 | 114.82 | AG1-118 | COMED_P4_120-45-L10322__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S89 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1901.4 | 112.24 | 114.82 | AG1-118 | COMED_P2-2_120_LO-345R__2_SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S90 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1895.4 | 111.98 | 114.46 | AG1-118 | COMED_P4_120-45-L12002__SRT-A | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1588 | 106.12 | 107.37 | AG1-118 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1587.8 | 106.12 | 107.36 | AG1-118 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S91 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1893.9 | 122.85 | 123.94 | AG1-462 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S92 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1846 | 120.17 | 120.81 | AG1-462 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S93 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1879.7 | 121.98 | 123.02 | AG1-553 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S94 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1897 | 123.03 | 124.15 | L05_CE22 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S95 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1897.4 | 123.06 | 124.18 | NQ71 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S96 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1887.4 | 122.44 | 123.52 | O09 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S97 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1841.4 | 119.88 | 120.51 | O09 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S98 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1927.1 | 124.82 | 126.12 | O22 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S99 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1878 | 122.06 | 122.91 | O22 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1584.3 | 105.67 | 107.12 | O22 | COMED_P4_108-45-BT5-6___SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1584.2 | 105.67 | 107.11 | O22 | COMED_P4_108-45-BT5-6___SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | 1479 | 1576.1 | 105.34 | 106.57 | O22 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | 1479 | 1576 | 105.34 | 106.56 | O22 | COMED_P1-2_345-L11124_B-N_SRT-A | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-IPD-S100 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1885.2 | 122.31 | 123.38 | O29 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S101 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1839.9 | 119.79 | 120.41 | O29 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S102 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1894 | 122.79 | 123.95 | O50 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S103 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1894.3 | 122.86 | 123.97 | P11 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S104 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1847.2 | 120.23 | 120.89 | P11 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S105 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1879.1 | 121.95 | 122.98 | P36 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S106 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1892.3 | 122.76 | 123.84 | P46 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S107 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1844.6 | 120.08 | 120.72 | P46 | COMED_P4_935-45-BT9-10__SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S108 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1908 | 123.84 | 124.87 | Q03 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S109 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1528 | 1895.9 | 122.96 | 124.08 | LTFIMP_O-066 | COMED_P4_108-45-BT5-6___SRT-A | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 101.18 | 101.01 | AB1-160 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 100.33 | 100.13 | AD2-133 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 308.9 | 103.56 | 104.01 | AE2-139 | PN_P2-3_PN-230-3C_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 308.9 | 103.56 | 104.01 | AE2-139 | PN_P1-2_PN-230-013A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 308.9 | 104.87 | 104.01 | AE2-139 | PN_P2-3_PN-230-997-DRT-068_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 308.9 | 103.56 | 104.01 | AE2-139 | PN_P2-3_PN-230-997-DRT-055_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 306.7 | 102.99 | 103.28 | AE2-139 | PN_P2-3_PN-230-020-DRT_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 102.48 | 102.34 | AE2-139 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 671 | 101.19 | 100.75 | AE2-139 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 100.86 | 100.75 | AE2-139 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 100.3 | 100.1 | AE2-299 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 100.81 | 100.62 | AG1-090 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 100.29 | 100.09 | AG1-090/AG1-377/AG1-378 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 100.3 | 100.11 | AG1-548 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 309.4 | 103.62 | 104.16 | K02 | PN_P2-3_PN-230-3C_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 309.4 | 103.62 | 104.16 | K02 | PN_P1-2_PN-230-013A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 309.4 | 103.62 | 104.16 | K02 | PN_P2-3_PN-230-997-DRT-055_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 309.4 | 104.95 | 104.16 | K02 | PN_P2-3_PN-230-997-DRT-068_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200674 | 26TOWANDA | 200675 | 26E.TWANDA | 3 | 115/230 | 226 | 297 | 307.2 | 103.06 | 103.42 | K02 | PN_P2-3_PN-230-020-DRT_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 102.8 | 102.66 | K02 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 101.18 | 101.07 | K02 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 672.6 | 101.45 | 100.99 | K02 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 103.18 | 103.05 | V2-019 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 101.56 | 101.46 | V2-019 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 675 | 101.76 | 101.36 | V2-019 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.1 | 100.43 | 100.01 | V2-019 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 102.76 | 102.63 | LTFIMP_O-066 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 673.6 | 101.5 | 101.14 | LTFIMP_O-066 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 101.14 | 101.04 | LTFIMP_O-066 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S110 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.13 | 101.9 | AA1-018 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S111 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1726 | - | 100.58 | 100.43 | AA1-018 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-IPD-S112 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.03 | 102.75 | AB2-047 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S113 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 101.78 | 103.37 | AB2-132 | Base Case | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S114 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 101.99 | 102.36 | AB2-132 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S115 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.58 | 102.24 | AB2-132 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S116 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 100.57 | 100.94 | AD1-067 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S117 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 104.98 | 104.72 | AD1-100 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S118 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | 1726 | - | 100.72 | 100.62 | AD1-100 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S119 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1726 | - | 100.64 | 100.48 | AD1-100 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-IPD-S120 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.38 | 102.13 | AD2-038 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S121 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1726 | - | 100.29 | 100.13 | AD2-038 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-IPD-S122 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 104.06 | 103.76 | AD2-047 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S123 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 101.62 | 103.22 | AD2-134 | Base Case | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S124 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.7 | 102.37 | AD2-134 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S125 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 101.55 | 101.91 | AD2-134 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S126 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.93 | 102.61 | AE1-114 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S127 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 100.61 | 100.96 | AE1-114 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S128 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 101.66 | 101.43 | AE2-255 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S129 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1726 | - | 101.03 | 100.93 | AE2-281 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-IPD-S130 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 100.68 | 100.53 | AE2-281 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S131 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 100.46 | 100.83 | AE2-341 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S132 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.6 | 102.26 | AF1-280 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S133 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 101.02 | 101.38 | AF1-280 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S134 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.84 | 102.52 | AF1-296 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S135 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 100.63 | 100.99 | AF1-296 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S136 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 100.82 | 102.37 | AF2-027 | Base Case | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S137 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.83 | 102.58 | AF2-142 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S138 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.93 | 102.66 | AF2-143 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S139 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 101.51 | 101.86 | AF2-182 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S140 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.17 | 101.81 | AF2-182 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S141 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 101.74 | 103.37 | AF2-200 | Base Case | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S142 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 102.1 | 102.52 | AF2-200 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S143 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.42 | 102.09 | AF2-200 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S144 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.07 | 102.78 | AF2-252 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S145 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 100.72 | 102.2 | AF2-349 | Base Case | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S146 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 101.95 | 101.55 | AF2-349 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S147 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 101.02 | 101.29 | AF2-349 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S148 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 101.58 | 103.17 | AG1-118 | Base Case | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S149 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.91 | 102.59 | AG1-118 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S150 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 101.31 | 101.68 | AG1-118 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S151 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.06 | 102.75 | AG1-462 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S152 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.43 | 102.1 | AG1-553 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S153 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 100.98 | 101.34 | AG1-553 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S154 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.03 | 102.74 | L05_CE22 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S155 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.78 | 102.46 | O09 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S156 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 100.76 | 101.13 | O09 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S157 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.13 | 101.9 | O22 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S158 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.69 | 102.37 | O29 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S159 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 100.86 | 101.23 | O29 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S160 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.54 | 102.29 | O50 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S161 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.9 | 102.6 | P11 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S162 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.57 | 102.23 | P36 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S163 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1479 | - | 101.01 | 101.37 | P36 | Base Case | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-IPD-S164 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.08 | 102.77 | P46 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S165 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.86 | 103.58 | Q03 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S166 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.96 | 103.67 | S36 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S167 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 103.97 | 103.68 | S37 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-IPD-S168 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 1726 | - | 102.97 | 102.69 | W4-005 | Base Case | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425