## Thermal
To be adressed through Interregional process.
PJM N-1-1 Thermal Result (Summer 2031 Case) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 225/230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 138.77 | 130.43 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 225/230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 138.76 | 130.41 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 225/230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 138.54 | 130.21 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 225/230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 138.53 | 130.2 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 225/230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 104.99 | 104.46 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 225/230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 104.82 | 104.29 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 225/230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 104.06 | 103.51 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999050 | LIMERICK 4B | 4B | 500/230 | 225/230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 104.06 | 103.51 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 225/230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 103.89 | 103.34 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 214341 | LIM4AB HS LD | 999051 | LIMERICK 4A | 4A | 500/230 | 225/230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 103.89 | 103.34 | No |  | M3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Active | 2026W1-N11-ST1 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 156.27 | 155.23 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-ST2 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 156.27 | 155.13 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-ST3 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069A_SRT-A | 153.58 | 152.53 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-ST4 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 165 | 186 | DPL_P1_2_CKT 23069A_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 153.58 | 152.22 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-ST5 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 113.69 | 113 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026W1-N11-ST6 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 113.69 | 112.9 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026W1-N11-ST7 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069A_SRT-A | 111.7 | 110.9 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026W1-N11-ST8 | 232119 | NELSON | 232121 | INDRV2&3 | 1 | 138 | 235 | 139 | 193 | DPL_P1_2_CKT 23069A_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 111.7 | 110.84 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 139 | 193 | N/A | 201 | 171 | 228 | N/A | 239 | 165 | 221 | N/A | 221
Active | 2026W1-N11-ST9 | 232121 | INDRV2&3 | 232805 | ROBINSON | 1 | 138 | 235 | 244 | 287 | DPL_P1_3_BETHANY AT1_SRT-A | DPL_P1_2_CKT 6714_SRT-A | 103.87 | 103.87 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 272 | 347 | N/A | 373 | 314 | 391 | N/A | 423 | 305 | 382 | N/A | 412
Active | 2026W1-N11-ST10 | 232121 | INDRV2&3 | 232805 | ROBINSON | 1 | 138 | 235 | 244 | 287 | DPL_P1_2_CKT 6714_SRT-A | DPL_P1_3_BETHANY AT1_SRT-A | 103.66 | 103.66 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 272 | 347 | N/A | 373 | 314 | 391 | N/A | 423 | 305 | 382 | N/A | 412
Active | 2026W1-N11-ST11 | 232118 | NSEAFORD | 232136 | CONAWAY | 1 | 138 | 235 | 167 | 241 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 101.57 | 101.81 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 167 | 241 | N/A | 264 | 231 | 308 | N/A | 338 | 218 | 294 | N/A | 323
Active | 2026W1-N11-ST12 | 232118 | NSEAFORD | 232136 | CONAWAY | 1 | 138 | 235 | 167 | 241 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 101.57 | 101.4 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 167 | 241 | N/A | 264 | 231 | 308 | N/A | 338 | 218 | 294 | N/A | 323
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 138.41 | 130.01 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 138.41 | 130 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 138.18 | 129.79 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 138.17 | 129.78 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Active | 2026W1-N11-ST13 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 134.84 | 123.26 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST14 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 132.13 | 120.57 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST15 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 132.13 | 120.57 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST16 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 135.21 | 119.05 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST17 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 132.5 | 116.38 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST18 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 132.5 | 116.38 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST19 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | DPL_P1_2_CKT 5025_SRT-A | 122.72 | 113.72 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST20 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | DPL_P1_2_CKT 5025_SRT-A | 124.3 | 113.27 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST21 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | 125.29 | 112.01 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST22 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | DPL_P1_2_CKT 5025_SRT-A | 120.05 | 111.07 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST23 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | DPL_P1_2_CKT 5025_SRT-A | 120.05 | 111.07 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST24 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | DPL_P1_2_CKT 5025_SRT-A | 121.63 | 110.61 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST25 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | DPL_P1_2_CKT 5025_SRT-A | 121.63 | 110.61 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST26 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | 123.47 | 110.26 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST27 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | 122.61 | 109.36 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST28 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | 122.61 | 109.36 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST29 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | 120.8 | 107.61 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST30 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | 120.8 | 107.61 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 105.16 | 104.62 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | Base Case | 104.98 | 104.44 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 104.23 | 103.66 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999050 | LIMERICK 4B | 4B | 230 | 230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 104.23 | 103.66 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | Base Case | 104.05 | 103.49 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Informational-Only | N/A | 213770 | LMRK 4AB | 999051 | LIMERICK 4A | 4A | 230 | 230 | 387 | 541 | 213742 LIMERCK1 22.0 1 _SRT-A | Base Case | 104.05 | 103.49 | No |  | M-3 project already in place to address the violation (PE-2025-008) | 398 | 594 | N/A | 649 | 472 | 659 | N/A | 715 | 456 | 645 | N/A | 709
Active | 2026W1-N11-ST31 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | Base Case | 117.03 | 103.42 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Informational-Only | N/A | 213770 | LMRK 4AB | 214301 | LIMERICK4T | 1 | 230 | 230 | 1266 | 1352 | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | 108.86 | 102.24 | No |  | M-3 project already in place to address the violation (PE-2025-008) | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | N/A | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | N/A | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | N/A | Not provided - transformer lead lines. Refer to transformer conductor limit.
Informational-Only | N/A | 213770 | LMRK 4AB | 214301 | LIMERICK4T | 1 | 230 | 230 | 1266 | 1352 | PECO_P1-2_5030_SRT-A/* $ MONTCO $ PECO_P1-2_5030 $ L | PECO_P1-2_5031_SRT-A/* $ MONTCO $ PECO_P1-2_5031 $ L | 108.86 | 102.23 | No |  | M-3 project already in place to address the violation (PE-2025-008) | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | N/A | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | N/A | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | Not provided - transformer lead lines. Refer to transformer conductor limit. | N/A | Not provided - transformer lead lines. Refer to transformer conductor limit.
Active | 2026W1-N11-ST32 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-1_HOPC_G1_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 106.3 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST33 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-1_SALM_G1_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.21 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST34 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-1_SALM_G2_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.08 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST35 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-2_GEN1-GHC_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 106.54 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST36 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-2_GEN1-GSA_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.37 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST37 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-2_GEN2-GSA_9-10_SUM_SRT-S | DPL_P1_2_CKT 5025_SRT-A | 107.23 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST38 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1-2_GEN2-GSA_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.23 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST39 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PJM500_PS_P1_2_GHC-GSA-SUM_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 106.54 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST40 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 200036 AH1-710 GEN1 25.0 N1_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.21 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST41 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 200037 AH1-710 GEN2 25.0 N2_SRT-A | DPL_P1_2_CKT 5025_SRT-A | 107.08 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST42 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 200039 HOPE CG1 25.0 1 _SRT-A | DPL_P1_2_CKT 5025_SRT-A | 106.3 | 101.64 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST43 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | 106.58 | 100.84 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST44 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-06_SRT-A/* $ CHESCO $ PECO_P1-2_220-06 $ L | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 104.71 | 100.37 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST45 | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | Base Case | 113.75 | 100.15 | Yes |  |  | 569 | 653 | N/A | 764 | 640 | 715 | N/A | 818 | 625 | 702 | N/A | 806
Active | 2026W1-N11-ST46 | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 578 | DPL_P1_2_CKT 5025_SRT-A | Base Case | 113.75 | 100.15 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST47 | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | PECO_P1-2_220-34_SRT-A/* $ CHESCO $ PECO_P1-2_220-34 $ L | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 106.04 | 100.05 | Yes |  |  | 463 | 578 | N/A | 621 | 521 | 639 | N/A | 690 | 508 | 627 | N/A | 676
Active | 2026W1-N11-ST48 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 144.48 | 136.26 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST49 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 144.48 | 133.86 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST50 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 143.17 | 134.89 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST51 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 143.17 | 132.41 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST52 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_138-L1607__B-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 132.76 | 119.6 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST53 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1607__B-N_SRT-A | 132.18 | 125.82 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST54 | 270998 | ANTIOCH ;BT | 272386 | ROUND LK ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1603__R-N_SRT-A | 131.59 | 125.08 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST55 | 270998 | ANTIOCH ;BT | 272386 | ROUND LK ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_138-L1603__R-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 131.59 | 118.87 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST56 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_138-L4202__B-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 130.5 | 119.73 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Active | 2026W1-N11-ST57 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L4202__B-N_SRT-A | 129.99 | 125.06 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Active | 2026W1-N11-ST58 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | Base Case | 129.64 | 116.82 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST59 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 127.9 | 115.05 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST60 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 127.89 | 115.72 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST61 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10806_R-S_SRT-A | Base Case | 126.53 | 113.69 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST62 | 272456 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18415_B-N_SRT-A | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | 126.08 | 117.96 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST63 | 272456 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 138 | 222 | 420 | 480 | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | COMED_P1-2_345-L18415_B-N_SRT-A | 126.07 | 116.21 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST64 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12006_R-N_SRT-A | Base Case | 125.1 | 114.81 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST65 | 271555 | GLENDALE ;RT | 271923 | LOMBARD ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 125.04 | 113.99 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST66 | 271555 | GLENDALE ;RT | 271923 | LOMBARD ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 125.04 | 114.85 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST67 | 270724 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18415_B-N_SRT-A | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | 125.04 | 116.9 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST68 | 270724 | ELK GROVE; B | 998471 | ELK GROVE 82 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR83_ELKGR_R-N_SRT-A | COMED_P1-2_345-L18415_B-N_SRT-A | 125.04 | 115.15 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST69 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 124.89 | 116.76 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST70 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 124.89 | 117.4 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST71 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 124.12 | 116.59 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST72 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 124.12 | 115.33 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST73 | 271064 | BARTLETT ;BT | 272546 | SPAULDING;1B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 124.08 | 115.6 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST74 | 271064 | BARTLETT ;BT | 272546 | SPAULDING;1B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L14401_R-N_SRT-A | 124.08 | 114.19 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST75 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | Base Case | 124 | 107.67 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST76 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 123.56 | 116.16 | Yes |  |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026W1-N11-ST77 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L14401_R-N_SRT-A | 123.56 | 115.31 | Yes |  |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026W1-N11-ST78 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18415_B-N_SRT-A | COMED_P1-3_TR82_ELKGR_B-N_SRT-A | 123.54 | 115.94 | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-N11-ST79 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR82_ELKGR_B-N_SRT-A | COMED_P1-2_345-L18415_B-N_SRT-A | 123.54 | 114.62 | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Informational-Only | N/A | 275228 | WAYNE ;1M | 272740 | WAYNE ; B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 122.86 | 118.11 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270916 | WAYNE ; B | 275228 | WAYNE ;1M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L14401_R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 122.86 | 118.11 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 275228 | WAYNE ;1M | 272740 | WAYNE ; B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L14401_R-N_SRT-A | 122.86 | 122.1 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270916 | WAYNE ; B | 275228 | WAYNE ;1M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L14401_R-N_SRT-A | 122.86 | 122.1 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST80 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 122.67 | 111.3 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST81 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 122.66 | 111.12 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST82 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11602SR-S_SRT-A | Base Case | 122.11 | 100.18 | Yes |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Informational-Only | N/A | 275198 | LOMBARD ;2M | 271925 | LOMBARD ;2R | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 121.1 | 120.47 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 275198 | LOMBARD ;2M | 271925 | LOMBARD ;2R | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 121.1 | 114.87 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST83 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_138-L7915__R-N_SRT-A | 121.06 | 113.26 | Yes |  |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026W1-N11-ST84 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_138-L7915__R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 121.06 | 115.47 | Yes |  |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Informational-Only | N/A | 270813 | LOMBARD ;2R | 275198 | LOMBARD ;2M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 120.72 | 120.18 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 271342 | DIERKING ; B | 272146 | GREENLEAF; B | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10111AB-N_SRT-A | 120.72 | 110.39 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only | N/A | 270813 | LOMBARD ;2R | 275198 | LOMBARD ;2M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 120.72 | 114.51 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 271342 | DIERKING ; B | 272146 | GREENLEAF; B | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L10111AB-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 120.71 | 107.33 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Active | 2026W1-N11-ST85 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 120.52 | 111.14 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Informational-Only | N/A | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_138-L10117_R-N_SRT-A | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | 120.33 | 112.69 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only | N/A | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | COMED_P1-2_138-L10117_R-N_SRT-A | 120.33 | 112.64 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Active | 2026W1-N11-ST86 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 120.27 | 110.67 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST87 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 120.26 | 110.35 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST88 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L10806_R-S_SRT-A | 120.08 | 108.61 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST89 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10806_R-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 120.07 | 108.52 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST90 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 120.03 | 114.05 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST91 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 120.03 | 110.4 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST92 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 119.78 | 110.83 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST93 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 119.77 | 107.22 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST94 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 119.59 | 109.5 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST95 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 119.58 | 105.32 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST96 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 119.35 | 113.45 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST97 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L10805_B-S_SRT-A | 118.98 | 105.29 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST98 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10805_B-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 118.97 | 106.1 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST99 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L18502AB-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 118.84 | 107.74 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST100 | 271052 | BEDFORD P;4B | 271216 | CLEARING ;BT | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L11604_R-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 118.17 | 101.75 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST101 | 271052 | BEDFORD P;4B | 271216 | CLEARING ;BT | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L11604_R-S_SRT-A | 118.17 | 102.1 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST102 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 118.08 | 106.98 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST103 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 118.07 | 106.1 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST104 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 117.72 | 107.04 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST105 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 117.72 | 108.16 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST106 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | Base Case | 117.43 | 107.36 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST107 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | Base Case | 117.35 | 110.83 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST108 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L10807_R-S_SRT-A | 117.22 | 105.72 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST109 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10807_R-S_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 117.22 | 104.26 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST110 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 117.09 | 109.17 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST111 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 117.08 | 107.03 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST112 | 270716 | DRESDEN ; B | 274702 | KENDALL ;BU | 1 | 345 | 222 | 1201 | 1201 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_345-L93501_B-S_SRT-A | 117.06 | 110.57 | Yes |  |  | 1201 | 1201 | 1252 | 1367 | 1498 | 1498 | 1572 | 1730 | 1438 | 1438 | 1506 | 1655
Active | 2026W1-N11-ST113 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 116.76 | 104.18 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST114 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 116.76 | 108.36 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST115 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 116.24 | 106.79 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST116 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 116.23 | 105.61 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST117 | 270809 | LISLE ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1656 | COMED_P1-2_345-L11120_R-N_SRT-A | Base Case | 115.91 | 106.16 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Informational-Only | N/A | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L10112AR-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 115.89 | 104.67 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only | N/A | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L10112AR-N_SRT-A | 115.89 | 105.54 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Active | 2026W1-N11-ST118 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 115.45 | 103.62 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST119 | 271554 | GLENDALE ;BT | 271924 | LOMBARD ;6B | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 115.45 | 106.47 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST120 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 115.37 | 108.09 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST121 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 115.37 | 109.29 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_138-L10117_R-N_SRT-A | Base Case | 115.24 | 105.82 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Active | 2026W1-N11-ST122 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 115.08 | 104.63 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST123 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 115.08 | 106.89 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST124 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 115.04 | 106.51 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST125 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 115.03 | 104.71 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST126 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 114.99 | 104.81 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST127 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 114.99 | 107.37 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L15616__-R_SRT-A | 114.74 | 109.35 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L15616__-R_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 114.73 | 111.56 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST128 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L93502_R-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 114.68 | 104.36 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST129 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L93502_R-S_SRT-A | 114.66 | 104.98 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_345-L97104__-R_SRT-A | 114.63 | 109.24 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L97104__-R_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 114.62 | 111.48 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST130 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 114.52 | 110.03 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Informational-Only | N/A | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_138-L10117_R-N_SRT-A | 114.49 | 106.9 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Informational-Only | N/A | 271343 | DIERKING ; R | 272147 | GREENLEAF; R | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_138-L10117_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 114.48 | 104.64 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Active | 2026W1-N11-ST131 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L18502AB-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 113.69 | 105.47 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Active | 2026W1-N11-ST132 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 113.51 | 103.39 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST133 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 113.5 | 103.14 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST134 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10805_B-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 113.27 | 103.56 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST135 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L10805_B-S_SRT-A | 113.27 | 103.55 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST136 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 113.19 | 111.15 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST137 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L10321_B-S_SRT-A | 113.11 | 102.15 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST138 | 271131 | BUTTERFIE; R | 272855 | YORK ;RT | 1 | 138 | 222 | 269 | 349 | COMED_P1-2_345-L10321_B-S_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 113.1 | 106.04 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST139 | 271555 | GLENDALE ;RT | 272109 | NORDIC ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 112.97 | 101.91 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST140 | 271555 | GLENDALE ;RT | 272109 | NORDIC ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12006_R-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 112.97 | 102.85 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST141 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 112.57 | 103.03 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST142 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 112.56 | 105.9 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST143 | 272387 | ROUND LK ; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_138-L4202__B-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 112.46 | 101.78 | Yes |  |  | 298.0617 | 298.0617 | 298.7788 | 305.7104 | 322.9201 | 322.9201 | 323.8762 | 332.9591 | 317.6616 | 317.6616 | 318.6177 | 326.9835
Active | 2026W1-N11-ST144 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | Base Case | 112.4 | 106.57 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST145 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L11124_B-N_SRT-A | 112.3 | 103.01 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST146 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 112.29 | 105.69 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST147 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | Base Case | 112.27 | 100.28 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST148 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 112.25 | 110.25 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST149 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 112.16 | 101.14 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST150 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 112.16 | 105.48 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST151 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 112.12 | 103.53 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST152 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L11124_B-N_SRT-A | 112.12 | 102.36 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Informational-Only | N/A | 270774 | GRAYSLAKE; R | 270883 | SILVER LK; R | 1 | 345 | 222 | 1449 | 1864 | COMED_P1-2_345-L18502AB-N_SRT-A | Base Case | 112.04 | 104.89 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N11-ST153 | 272387 | ROUND LK ; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L4202__B-N_SRT-A | 112 | 107.1 | Yes |  |  | 298.0617 | 298.0617 | 298.7788 | 305.7104 | 322.9201 | 322.9201 | 323.8762 | 332.9591 | 317.6616 | 317.6616 | 318.6177 | 326.9835
Active | 2026W1-N11-ST154 | 270694 | CHERRY VA; B | 275166 | CHERRY VA;2M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | COMED_P1-2_138-L15622_R-R_SRT-A | 111.86 | 103.61 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST155 | 275166 | CHERRY VA;2M | 271192 | CHERRY VA;3B | 1 | 138 | 222 | 420 | 480 | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | COMED_P1-2_138-L15622_R-R_SRT-A | 111.86 | 103.61 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST156 | 275166 | CHERRY VA;2M | 271192 | CHERRY VA;3B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_138-L15622_R-R_SRT-A | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | 111.85 | 103.9 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST157 | 270694 | CHERRY VA; B | 275166 | CHERRY VA;2M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_138-L15622_R-R_SRT-A | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | 111.85 | 103.9 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST158 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L11124_B-N_SRT-A | 111.84 | 102.14 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST159 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 111.83 | 105.06 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST160 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | Base Case | 111.69 | 104.96 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST161 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10322_R-S_SRT-A | Base Case | 111.64 | 100.3 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST162 | 270999 | ANTIOCH ;RT | 272389 | RL BEACH ; R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1607__B-N_SRT-A | 111.45 | 105.12 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST163 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 111.33 | 101.28 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST164 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 111.32 | 103.37 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Informational-Only | N/A | 271342 | DIERKING ; B | 272146 | GREENLEAF; B | 1 | 138 | 222 | 300 | 400 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_138-L10118_B-N_SRT-A | 111.03 | 102.94 | No | To be adressed through supplemental process. |  | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600 | 300 | 400 | 500 | 600
Active | 2026W1-N11-ST165 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | Base Case | 110.98 | 104.24 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST166 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L10807_R-S_SRT-A | 110.96 | 101.44 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST167 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10807_R-S_SRT-A | COMED_P1-2_345-L10802_R-S_SRT-A | 110.96 | 101.11 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST168 | 270998 | ANTIOCH ;BT | 272386 | ROUND LK ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 110.82 | 104.69 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST169 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | Base Case | 110.76 | 101.21 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST170 | 270998 | ANTIOCH ;BT | 272388 | RL BEACH ; B | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_138-L1603__R-N_SRT-A | 110.76 | 104.27 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST171 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10802_R-S_SRT-A | Base Case | 110.71 | 100.13 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST172 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L2310___-S_SRT-A | COMED_P1-2_345-L1311__R-C_SRT-A | 110.71 | 101 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST173 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10806_R-S_SRT-A | COMED_P1-2_345-L10805_B-S_SRT-A | 110.59 | 100.72 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST174 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10805_B-S_SRT-A | COMED_P1-2_345-L10806_R-S_SRT-A | 110.49 | 100.82 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST175 | 270808 | LISLE ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 110.37 | 103.69 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST176 | 270725 | ELK GROVE; R | 270815 | LOMBARD ;1R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 110.21 | 102.85 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST177 | 270725 | ELK GROVE; R | 270815 | LOMBARD ;1R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 110.2 | 101.65 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST178 | 270725 | ELK GROVE; R | 270815 | LOMBARD ;1R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 109.86 | 101.1 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST179 | 270725 | ELK GROVE; R | 270815 | LOMBARD ;1R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 109.86 | 103.65 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST180 | 270809 | LISLE ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_345-L10801_B-S_SRT-A | 109.78 | 100.51 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2013.1713 | 1602.6493 | 1920.5499 | 2050.8174 | 2262.3528 | 1547.0764 | 1879.3184 | 2005.4031 | 2207.9751
Active | 2026W1-N11-ST181 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L10806_R-S_SRT-A | 109.49 | 100.92 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST182 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L12005_B-N_SRT-A | Base Case | 109.37 | 104.58 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST183 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 109.24 | 100.67 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Informational-Only | N/A | 271436 | PINE ; B | 271736 | ITASCA ;12 | 1 | 138 | 222 | 466 | 588 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10111AB-N_SRT-A | 109.02 | 101.99 | No | To be adressed through supplemental process. |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640
Active | 2026W1-N11-ST184 | 270999 | ANTIOCH ;RT | 272389 | RL BEACH ; R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 108.98 | 103.1 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Informational-Only | N/A | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 466 | 588 | COMED_P1-2_138-L10117_R-N_SRT-A | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | 108.83 | 103.49 | No | To be adressed through supplemental process. |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640
Informational-Only | N/A | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 466 | 588 | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | COMED_P1-2_138-L10117_R-N_SRT-A | 108.83 | 103.45 | No | To be adressed through supplemental process. |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640
Active | 2026W1-N11-ST185 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L10806_R-S_SRT-A | 108.65 | 100.56 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST186 | 270724 | ELK GROVE; B | 270812 | LOMBARD ;3B | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 108.62 | 100.53 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST187 | 275213 | SILVER LK;2M | 272464 | SILVER LK; B | 1 | 138 | 222 | 400 | 465 | COMED_P1-3_TR83_SILVEGR-R_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 108.51 | 100.9 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST188 | 275213 | SILVER LK;2M | 272464 | SILVER LK; B | 1 | 138 | 222 | 400 | 465 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-3_TR83_SILVEGR-R_SRT-A | 108.44 | 107.23 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST189 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 108.18 | 101.33 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 270773 | GRAYSLAKE; B | 270900 | TOLLWAY ; B | 1 | 345 | 222 | 1202 | 1387 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 108.16 | 103.17 | No | To be adressed through supplemental process. |  | 1201.0906 | 1201.0906 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST190 | 271668 | VETERANS ;BT | 272782 | WILL CNTY; B | 1 | 138 | 222 | 292 | 321 | COMED_P1-2_345-L11617_B-S_SRT-A | COMED_P1-2_138-L5103__B-S_SRT-A | 108.13 | 102.25 | Yes |  |  | 310.0129 | 396.7782 | 403.9489 | 433.5877 | 371.9198 | 440.9975 | 450.0803 | 484.7387 | 359.2516 | 431.6756 | 440.2804 | 473.7436
Active | 2026W1-N11-ST191 | 271668 | VETERANS ;BT | 272782 | WILL CNTY; B | 1 | 138 | 222 | 292 | 321 | COMED_P1-2_138-L5103__B-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 108.12 | 101.42 | Yes |  |  | 310.0129 | 396.7782 | 403.9489 | 433.5877 | 371.9198 | 440.9975 | 450.0803 | 484.7387 | 359.2516 | 431.6756 | 440.2804 | 473.7436
Active | 2026W1-N11-ST192 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 108.1 | 104.7 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST193 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 108.1 | 105.01 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST194 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12003_B-C_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 108.08 | 101.41 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST195 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12003_B-C_SRT-A | 108.08 | 108.17 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 466 | 588 | COMED_P1-2_138-L10117_R-N_SRT-A | Base Case | 108.04 | 101.75 | No | To be adressed through supplemental process. |  | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640 | 466 | 588 | 620 | 640
Active | 2026W1-N11-ST196 | 271097 | BLACKHAWK;RT | 271193 | CHERRY VA;2R | 1 | 138 | 222 | 314 | 386 | COMED_P1-3_TR82_CHERR_B-R_SRT-A | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | 108.04 | 104.02 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST197 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12003_B-C_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 108.02 | 101.24 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST198 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12003_B-C_SRT-A | 108.02 | 108.21 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST199 | 270781 | ITASCA ; R | 270813 | LOMBARD ;2R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L12006_R-N_SRT-A | 108.01 | 102.3 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST200 | 275166 | CHERRY VA;2M | 271192 | CHERRY VA;3B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L97104__-R_SRT-A | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | 107.85 | 100.3 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST201 | 270694 | CHERRY VA; B | 275166 | CHERRY VA;2M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L97104__-R_SRT-A | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | 107.85 | 100.3 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST202 | 270694 | CHERRY VA; B | 275166 | CHERRY VA;2M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L15616__-R_SRT-A | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | 107.83 | 100.29 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST203 | 275166 | CHERRY VA;2M | 271192 | CHERRY VA;3B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L15616__-R_SRT-A | COMED_P1-3_TR84_WEMPL_B-R_SRT-A | 107.83 | 100.29 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Informational-Only | N/A | 270773 | GRAYSLAKE; B | 270900 | TOLLWAY ; B | 1 | 345 | 222 | 1202 | 1387 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 107.74 | 106.17 | No | To be adressed through supplemental process. |  | 1201.0906 | 1201.0906 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST204 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L10322_R-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 107.62 | 104.26 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST205 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10322_R-S_SRT-A | 107.62 | 104.5 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST206 | 270781 | ITASCA ; R | 271735 | ITASCA ;3R | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_138-L12015_R-N_SRT-A | COMED_P1-3_TR84_ITASC_B-N_SRT-A | 107.52 | 104.75 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST207 | 270781 | ITASCA ; R | 271735 | ITASCA ;3R | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR84_ITASC_B-N_SRT-A | COMED_P1-2_138-L12015_R-N_SRT-A | 107.52 | 104.66 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST208 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_138-L96001_B-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 107.36 | 100.71 | Yes |  |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026W1-N11-ST209 | 272486 | S ELGIN ;BT | 272740 | WAYNE ; B | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_138-L96001_B-N_SRT-A | 107.35 | 101.27 | Yes |  |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026W1-N11-ST210 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L10112AR-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 107.3 | 101.82 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST211 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | COMED_P1-2_345-L10112AR-N_SRT-A | 107.3 | 100.14 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST212 | 270883 | SILVER LK; R | 275213 | SILVER LK;2M | 1 | 345/138 | 222 | 400 | 465 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-3_TR83_SILVEGR-R_SRT-A | 107.28 | 106.02 | Yes |  |  | 420 | 480 | 500 | 515 | 450 | 490 | 508 | 524 | 440 | 487 | 506 | 522
Active | 2026W1-N11-ST213 | 271002 | ARCHER ; B | 271078 | BELL ROAD;BT | 1 | 138 | 222 | 310 | 397 | COMED_P1-2_345-L11617_B-S_SRT-A | Base Case | 107.23 | 101.07 | Yes |  |  | 310.0129 | 396.7782 | 403.9489 | 433.5877 | 371.9198 | 440.9975 | 450.0803 | 484.7387 | 359.2516 | 431.6756 | 440.2804 | 473.7436
Active | 2026W1-N11-ST214 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 107.22 | 103.25 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST215 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L18417_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 107.22 | 100.45 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST216 | 271555 | GLENDALE ;RT | 271923 | LOMBARD ; R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 106.74 | 100.07 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270847 | PLANO ; R | 1 | 345 | 222 | 1334 | 1528 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_345-L16704TB-S_SRT-A | 106.71 | 105.61 | No | To be adressed through supplemental process. |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N11-ST217 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L10112AR-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 106.66 | 101.19 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST218 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L10801_B-S_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 106.66 | 105.04 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L18502AB-N_SRT-A | COMED_P1-2_345-L15616__-R_SRT-A | 106.58 | 101.88 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L15616__-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 106.57 | 103.35 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST219 | 270725 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 106.52 | 102.54 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L18502AB-N_SRT-A | COMED_P1-2_345-L97104__-R_SRT-A | 106.48 | 101.81 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Informational-Only | N/A | 270883 | SILVER LK; R | 270917 | WAYNE ; R | 1 | 345 | 222 | 1202 | 1202 | COMED_P1-2_345-L97104__-R_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 106.47 | 103.28 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST220 | 272487 | S ELGIN ;RT | 272741 | WAYNE ; R | 1 | 138 | 222 | 504 | 553 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_138-L7910__B-N_SRT-A | 106.05 | 100.01 | Yes |  |  | 533.7384 | 690.5375 | 734.7567 | 833.7123 | 641.0597 | 768.22 | 820.327 | 930.0385 | 618.8306 | 751.7274 | 802.1612 | 909.2435
Active | 2026W1-N11-ST221 | 272457 | ELK GROVE; R | 998470 | ELK GROVE 81 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_138-L12015_R-N_SRT-A | COMED_P1-2_345-L18417_R-N_SRT-A | 105.96 | 100.39 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270900 | TOLLWAY ; B | 270916 | WAYNE ; B | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L13821_R-R_SRT-A | Base Case | 105.73 | 102.35 | No | To be adressed through supplemental process. |  | 1201.6882 | 1201.6882 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST222 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_138-L10301_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 105.2 | 101.63 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST223 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_138-L10301_B-S_SRT-A | 105.2 | 102.87 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST224 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 105.01 | 102.62 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST225 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 105.01 | 102.84 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST226 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_138-L10301_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 104.91 | 101.17 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST227 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_138-L10301_B-S_SRT-A | 104.91 | 102.7 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST228 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 104.6 | 102.14 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST229 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 104.6 | 102.17 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST230 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12002_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 104.52 | 102.18 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST231 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L12002_R-N_SRT-A | 104.52 | 102.35 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 275228 | WAYNE ;1M | 272740 | WAYNE ; B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_138-L7915__R-N_SRT-A | 104.51 | 104.62 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270916 | WAYNE ; B | 275228 | WAYNE ;1M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_345-L14402AB-N_SRT-A | COMED_P1-2_138-L7915__R-N_SRT-A | 104.51 | 104.62 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 275228 | WAYNE ;1M | 272740 | WAYNE ; B | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_138-L7915__R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 104.51 | 100.25 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270916 | WAYNE ; B | 275228 | WAYNE ;1M | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_138-L7915__R-N_SRT-A | COMED_P1-2_345-L14402AB-N_SRT-A | 104.51 | 100.25 | No | To be adressed through supplemental process. |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST232 | 270781 | ITASCA ; R | 998462 | ITASCA 84 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-2_138-L12015_R-N_SRT-A | COMED_P1-3_TR82_ITASC_R-N_SRT-A | 104.35 | 101.63 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST233 | 270781 | ITASCA ; R | 998462 | ITASCA 84 | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR82_ITASC_R-N_SRT-A | COMED_P1-2_138-L12015_R-N_SRT-A | 104.35 | 101.54 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 270773 | GRAYSLAKE; B | 270900 | TOLLWAY ; B | 1 | 345 | 222 | 1202 | 1387 | COMED_P1-2_345-L11124_B-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 104.14 | 103.41 | No | To be adressed through supplemental process. |  | 1201.0906 | 1201.0906 | 1251.883 | 1367.2116 | 1498.0767 | 1498.0767 | 1572.1739 | 1729.929 | 1437.7234 | 1437.7234 | 1505.845 | 1654.6368
Active | 2026W1-N11-ST234 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L10808_B-S_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 104.12 | 101.74 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST235 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L10808_B-S_SRT-A | 104.12 | 101.67 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST236 | 271739 | ITASCA ;4R | 998462 | ITASCA 84 | 1 | 138 | 222 | 420 | 480 | COMED_P1-2_138-L12015_R-N_SRT-A | COMED_P1-3_TR82_ITASC_R-N_SRT-A | 104.07 | 101.36 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST237 | 271739 | ITASCA ;4R | 998462 | ITASCA 84 | 1 | 138 | 222 | 420 | 480 | COMED_P1-3_TR82_ITASC_R-N_SRT-A | COMED_P1-2_138-L12015_R-N_SRT-A | 104.07 | 101.29 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST238 | 271668 | VETERANS ;BT | 272782 | WILL CNTY; B | 1 | 138 | 222 | 292 | 321 | COMED_P1-2_138-L5104__R-S_SRT-A | COMED_P1-2_138-L5103__B-S_SRT-A | 103.75 | 101.07 | Yes |  |  | 310.0129 | 396.7782 | 403.9489 | 433.5877 | 371.9198 | 440.9975 | 450.0803 | 484.7387 | 359.2516 | 431.6756 | 440.2804 | 473.7436
Active | 2026W1-N11-ST239 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-3_TR83_ELMHU_B-C_SRT-A | 103.41 | 101.96 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST240 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | 1334 | 1726 | COMED_P1-2_345-L13821_R-R_SRT-A | COMED_P1-2_345-L2310___-S_SRT-A | 103.27 | 100.01 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-N11-ST241 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-3_TR83_ELMHU_B-C_SRT-A | 102.93 | 101.49 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST242 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 173 | 223 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 102.39 | 101.6 | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-N11-ST243 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L12005_B-N_SRT-A | 101.84 | 100.33 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST244 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | 392 | 465 | COMED_P1-2_345-L12005_B-N_SRT-A | COMED_P1-2_345-L11120_R-N_SRT-A | 101.84 | 100.24 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST245 | 272465 | SILVER LK; R | 272791 | WILSON RD; R | 1 | 138 | 222 | 297 | 297 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L13821_R-R_SRT-A | 101.59 | 100.69 | Yes |  |  | 297 | 297 | 297 | 305.7104 | 322.9201 | 322.9201 | 323 | 332.9591 | 317 | 317 | 317 | 326.9835
Informational-Only | N/A | 270774 | GRAYSLAKE; R | 270883 | SILVER LK; R | 1 | 345 | 222 | 1449 | 1864 | COMED_P1-2_345-L11120_R-N_SRT-A | COMED_P1-2_345-L18502AB-N_SRT-A | 101.45 | 100.97 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-N11-ST246 | 270781 | ITASCA ; R | 271735 | ITASCA ;3R | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR84_ITASC_B-N_SRT-A | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | 101.36 | 100.91 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST247 | 270781 | ITASCA ; R | 271735 | ITASCA ;3R | 1 | 345/138 | 222 | 420 | 480 | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | COMED_P1-3_TR84_ITASC_B-N_SRT-A | 101.36 | 100.97 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-N11-ST248 | 271081 | BELLWOOD ; R | 271875 | LAGRANGE ; R | 1 | 138 | 222 | 292 | 321 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L10807_R-S_SRT-A | 101.25 | 101.55 | Yes |  |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N11-ST249 | 271668 | VETERANS ;BT | 272782 | WILL CNTY; B | 1 | 138 | 222 | 292 | 321 | COMED_P1-2_345-L10802_R-S_SRT-A | COMED_P1-2_345-L11617_B-S_SRT-A | 100.36 | 100.49 | Yes |  |  | 310.0129 | 396.7782 | 403.9489 | 433.5877 | 371.9198 | 440.9975 | 450.0803 | 484.7387 | 359.2516 | 431.6756 | 440.2804 | 473.7436
Active | 2026W1-N11-ST250 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 126.51 | 109.47 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST251 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#18125_SRT-A | 126.51 | 108.75 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST252 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#17431_SRT-A | AEP_P1-2_#6227_574_SRT-A | 113.54 | 104.8 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST253 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | 329 | 350 | AEP_P1-2_#713_569_SRT-A | AEP_P1-2_#18036_SRT-A | 105.9 | 104.53 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Active | 2026W1-N11-ST254 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | 329 | 350 | AEP_P1-2_#18036_SRT-A | AEP_P1-2_#713_569_SRT-A | 105.9 | 104.38 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Active | 2026W1-N11-ST255 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | 329 | 350 | AEP_P1-3_#18039_05CYPRUS 345_1_SRT-A | AEP_P1-3_#18040_05CYPRUS 345_2_SRT-A | 103.92 | 103.92 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Active | 2026W1-N11-ST256 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | 329 | 350 | AEP_P1-3_#18040_05CYPRUS 345_2_SRT-A | AEP_P1-3_#18039_05CYPRUS 345_1_SRT-A | 103.92 | 103.92 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Active | 2026W1-N11-ST257 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 121.6 | 102.66 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST258 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#727_573_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 117.37 | 102.31 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST259 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#6227_574_SRT-A | AEP_P1-2_#17431_SRT-A | 113.54 | 102.19 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST260 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#18125_SRT-A | 121.6 | 101.67 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST261 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 223 | AEP_P1-2_#17432_SRT-A | AEP_P1-2_#6227_574_SRT-A | 110.57 | 101.61 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-ST262 | 243472 | 05BEXLEY | 243592 | 05YEARLG | 1 | 138 | 205 | 196 | 247 | AEP_P1-2_#6793_13398_SRT-A | AEP_P1-2_#13640_27882_SRT-A | 101.17 | 101.17 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 277 | 277 | N/A | N/A | 350 | 350 | N/A | N/A | 213 | 260 | N/A | N/A
Active | 2026W1-N11-ST263 | 243472 | 05BEXLEY | 243592 | 05YEARLG | 1 | 138 | 205 | 196 | 247 | AEP_P1-2_#13640_27882_SRT-A | AEP_P1-2_#6793_13398_SRT-A | 101.17 | 101.17 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 277 | 277 | N/A | N/A | 350 | 350 | N/A | N/A | 213 | 260 | N/A | N/A
Active | 2026W1-N11-ST264 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_CEI-345-714_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 127.33 | 109.45 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026W1-N11-ST265 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OEC-345-813_SRT-A | ATSI_P1-2_CEI-345-714_SRT-A | 127.31 | 106.35 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026W1-N11-ST266 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-1_CEI-345-711_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 106.59 | 102.9 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026W1-N11-ST267 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | 239035 02PERRG1 22.0 1 _SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 106.59 | 102.9 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026W1-N11-ST268 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OEC-345-820_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 104.27 | 102.78 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026W1-N11-ST269 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OEC-138-023_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 109.29 | 102.45 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026W1-N11-ST270 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | AEP_P1-2_#775_563_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 108.65 | 102.23 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Active | 2026W1-N11-ST271 | 238678 | 02EAKRON | 238787 | 02HAYES+ | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OEC-138-036_SRT-A | ATSI_P1-2_OEC-345-813_SRT-A | 107.32 | 101.12 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 233 | 282 | N/A | 317 | 263 | 333 | N/A | 359 | 233 | 282 | N/A | 317
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 546 | 666 | DPL_P1_2_CKT 5025_SRT-A | Base Case | 104.83 | 100.59 | No | To be adressed through Interregional process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Volt Mag
PJM N-1-1 Voltage Magnitude Result (Summer 2031 Case)
FG # Status | FG # | Bus # | Name | KV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026W1-N11-SVM1 | 213505 | COCHRNVL | 230 | 230 | 0.95 | 1.05 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 0.9958 | 0.93612 | Yes
Active | 2026W1-N11-SVM2 | 213505 | COCHRNVL | 230 | 230 | 0.95 | 1.05 | DPL_P1_2_CKT 5025_SRT-A | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | 0.98726 | 0.93559 | Yes
Active | 2026W1-N11-SVM3 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0112__B-S_SRT-A | Base Case | 0.82488 | - | Yes
Active | 2026W1-N11-SVM4 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0112__B-S_SRT-A | Base Case | 0.85706 | - | Yes
Active | 2026W1-N11-SVM5 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0112__B-S_SRT-A | Base Case | 0.90587 | - | Yes
Active | 2026W1-N11-SVM6 | 271723 | ESS J370 ; R | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.95912 | 0.88786 | Yes
Active | 2026W1-N11-SVM7 | 271722 | ESS J370 ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.95913 | 0.88786 | Yes
Active | 2026W1-N11-SVM8 | 271723 | ESS J370 ; R | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.95912 | 0.89092 | Yes
Active | 2026W1-N11-SVM9 | 271722 | ESS J370 ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.95913 | 0.89092 | Yes
Active | 2026W1-N11-SVM10 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99942 | 0.91192 | Yes
Active | 2026W1-N11-SVM11 | 271418 | ESS J390 ;BT | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.98604 | 0.91447 | Yes
Active | 2026W1-N11-SVM12 | 271418 | ESS J390 ;BT | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.98604 | 0.91761 | Yes
Active | 2026W1-N11-SVM13 | 271020 | ESS J402 ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.98445 | 0.91779 | Yes
Active | 2026W1-N11-SVM14 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L0903__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0064 | 0.91813 | Yes
Active | 2026W1-N11-SVM15 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L11602SR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99774 | 0.91633 | Yes
Active | 2026W1-N11-SVM16 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1205__B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0005 | 0.82475 | Yes
Active | 2026W1-N11-SVM17 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1205__B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0084 | 0.85689 | Yes
Active | 2026W1-N11-SVM18 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1205__B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0106 | 0.90562 | Yes
Active | 2026W1-N11-SVM19 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1206__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0001 | 0.9151 | Yes
Active | 2026W1-N11-SVM20 | 271723 | ESS J370 ; R | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.97952 | 0.88758 | Yes
Active | 2026W1-N11-SVM21 | 271722 | ESS J370 ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.96141 | 0.88758 | Yes
Active | 2026W1-N11-SVM22 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99303 | 0.88827 | Yes
Active | 2026W1-N11-SVM23 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99993 | 0.89429 | Yes
Active | 2026W1-N11-SVM24 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0054 | 0.89696 | Yes
Active | 2026W1-N11-SVM25 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0005 | 0.89853 | Yes
Active | 2026W1-N11-SVM26 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99894 | 0.90387 | Yes
Active | 2026W1-N11-SVM27 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99884 | 0.90402 | Yes
Active | 2026W1-N11-SVM28 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0023 | 0.90957 | Yes
Active | 2026W1-N11-SVM29 | 271418 | ESS J390 ;BT | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.97003 | 0.91418 | Yes
Active | 2026W1-N11-SVM30 | 970832 | AG2-524 TAP | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99245 | 0.91538 | Yes
Active | 2026W1-N11-SVM31 | 271020 | ESS J402 ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.96992 | 0.91749 | Yes
Active | 2026W1-N11-SVM32 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L7719__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0002 | 0.91111 | Yes
Active | 2026W1-N11-SVM33 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L7719__R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0072 | 0.91732 | Yes
Active | 2026W1-N11-SVM34 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_DRESD_B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99985 | 0.91358 | Yes
Active | 2026W1-N11-SVM35 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_DRESD_B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0068 | 0.91981 | Yes
Active | 2026W1-N11-SVM36 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L1205__B-S_SRT-A | 0.91892 | 0.82408 | Yes
Active | 2026W1-N11-SVM37 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.91892 | 0.88796 | Yes
Active | 2026W1-N11-SVM38 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.91892 | 0.88974 | Yes
Active | 2026W1-N11-SVM39 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.9252 | 0.89397 | Yes
Active | 2026W1-N11-SVM40 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.9252 | 0.89577 | Yes
Active | 2026W1-N11-SVM41 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.92854 | 0.89666 | Yes
Active | 2026W1-N11-SVM42 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.92848 | 0.89818 | Yes
Active | 2026W1-N11-SVM43 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.92854 | 0.89851 | Yes
Active | 2026W1-N11-SVM44 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.92848 | 0.89991 | Yes
Active | 2026W1-N11-SVM45 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93761 | 0.90362 | Yes
Active | 2026W1-N11-SVM46 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.9378 | 0.90378 | Yes
Active | 2026W1-N11-SVM47 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L1205__B-S_SRT-A | 0.96196 | 0.90515 | Yes
Active | 2026W1-N11-SVM48 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93761 | 0.90561 | Yes
Active | 2026W1-N11-SVM49 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.9378 | 0.90576 | Yes
Active | 2026W1-N11-SVM50 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93721 | 0.90913 | Yes
Active | 2026W1-N11-SVM51 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93721 | 0.91071 | Yes
Active | 2026W1-N11-SVM52 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.91892 | 0.91191 | Yes
Active | 2026W1-N11-SVM53 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR81_DRESD_B-S_SRT-A | 0.91892 | 0.9135 | Yes
Active | 2026W1-N11-SVM54 | 970832 | AG2-524 TAP | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.95181 | 0.91522 | Yes
Active | 2026W1-N11-SVM55 | 970832 | AG2-524 TAP | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.95181 | 0.91739 | Yes
Active | 2026W1-N11-SVM56 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.9252 | 0.91813 | Yes
Active | 2026W1-N11-SVM57 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | Base Case | 0.91892 | - | Yes
Active | 2026W1-N11-SVM58 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR81_DRESD_B-S_SRT-A | 0.9252 | 0.91973 | Yes
Active | 2026W1-N11-SVM59 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99521 | 0.89021 | Yes
Active | 2026W1-N11-SVM60 | 271723 | ESS J370 ; R | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.9831 | 0.89092 | Yes
Active | 2026W1-N11-SVM61 | 271722 | ESS J370 ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.96484 | 0.89093 | Yes
Active | 2026W1-N11-SVM62 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0021 | 0.89624 | Yes
Active | 2026W1-N11-SVM63 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0077 | 0.89896 | Yes
Active | 2026W1-N11-SVM64 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0025 | 0.90041 | Yes
Active | 2026W1-N11-SVM65 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0013 | 0.90602 | Yes
Active | 2026W1-N11-SVM66 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0012 | 0.90618 | Yes
Active | 2026W1-N11-SVM67 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0041 | 0.91128 | Yes
Active | 2026W1-N11-SVM68 | 271418 | ESS J390 ;BT | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-2_138-L0903__R-S_SRT-A | 0.97344 | 0.91761 | Yes
Active | 2026W1-N11-SVM69 | 970832 | AG2-524 TAP | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99496 | 0.91774 | Yes
Active | 2026W1-N11-SVM70 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-1_DR-2U_______-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99987 | 0.91652 | Yes
Active | 2026W1-N11-SVM71 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-1_DR-3U_______-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99966 | 0.91545 | Yes
Active | 2026W1-N11-SVM72 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | 274658 DRESDEN ;2U 18.0 2 _SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99987 | 0.91652 | Yes
Active | 2026W1-N11-SVM73 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | 274659 DRESDEN ;3U 18.0 3 _SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99966 | 0.91545 | Yes
Active | 2026W1-N11-SVM74 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99849 | 0.90898 | Yes
Active | 2026W1-N11-SVM75 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0059 | 0.91573 | Yes
Active | 2026W1-N11-SVM76 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0062 | 0.91933 | Yes
Active | 2026W1-N11-SVM77 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0121 | 0.9194 | Yes
Active | 2026W1-N11-SVM78 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L6102___-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99723 | 0.86926 | Yes
Active | 2026W1-N11-SVM79 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0008 | 0.89704 | Yes
Active | 2026W1-N11-SVM80 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0078 | 0.90313 | Yes
Active | 2026W1-N11-SVM81 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0081 | 0.90477 | Yes
Active | 2026W1-N11-SVM82 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0134 | 0.90725 | Yes
Active | 2026W1-N11-SVM83 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0094 | 0.90938 | Yes
Active | 2026W1-N11-SVM84 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0117 | 0.91866 | Yes
Active | 2026W1-N11-SVM85 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0117 | 0.91889 | Yes
Active | 2026W1-N11-SVM86 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L98105_R-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.0006 | 0.82284 | Yes
Active | 2026W1-N11-SVM87 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L98105_R-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.0084 | 0.85491 | Yes
Active | 2026W1-N11-SVM88 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L98105_R-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.0102 | 0.90351 | Yes

## Volt Drop
PJM N-1-1 Voltage Drop Result (Summer 2031 Case)
FG # Status | FG # | Bus # | Name | KV | Area | % Vdrop | Contingency 1 | Contingency 2 | BaseVolt | ContVolt | % Vdrop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2026W1-N11-SVD1 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.99826 | 0.91585 | 8.241 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-SVD2 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.99826 | 0.91585 | 8.241 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-SVD3 | 213505 | COCHRNVL | 230 | 230 | 7 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | DPL_P1_2_CKT 5025_SRT-A | 0.9958 | 0.92156 | 7.424 | Yes
Active | 2026W1-N11-SVD4 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0056 | 0.88743 | 11.821 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-SVD5 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0054 | 0.88779 | 11.758 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-SVD6 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0092 | 0.89055 | 11.868 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-SVD7 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0075 | 0.88747 | 12.006 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-SVD8 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0105 | 0.88783 | 12.269 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-SVD9 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0078 | 0.89059 | 11.722 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## Non-Convergence
PJM N-1-1 Non-Convergence Result (Summer 2031 Case)
FG # Status | FG # | Contingency 1 | Contingency 2 | Status | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2026W1-N11-SNCV1 | COMED_P1-2_138-L13701GR-C_SRT-A | COMED_P1-2_138-L17404GB-C_SRT-A | NotCnv | Yes

## Load Drop
PJM N-1-1 Load Drop Result (Summer 2031 Case)
FG # Status | FG# | Contingency 1 | Contingency 2 | MW Drop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2026W1-N11-SLD1 | DVP_P1-2: LN 201_SRT-A | DVP_P1-2: LN 2311_SRT-A | 405.84 | No | Will be addressed through the supplemental process
Active | 2026W1-N11-SLD2 | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 201_SRT-A | 405.84 | No | Will be addressed through the supplemental process
Active | 2026W1-N11-SLD3 | COMED_P1-2_138-L18505_R-N_SRT-A | COMED_P1-2_138-L18506_B-N_SRT-A | 355.34 | Yes
Active | 2026W1-N11-SLD4 | COMED_P1-2_138-L18506_B-N_SRT-A | COMED_P1-2_138-L18505_R-N_SRT-A | 355.34 | Yes