## Summer GenDeliv
2034 RTEP PJM Generator Deliverability Result (Summer) | [19 empty] | Conductor/Transformer Limit
FG # Status | FG # | FG Index # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Cont Name | ContType | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | N/A | 749 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P2-3_PE-500-014_SRT-SL | Breaker | 3792 | 5005.1 | 5167.7 | 131.99 | 136.28 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 20 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P1-2_PE-500-004B_SRT-A | Single | 3792 | 5003.3 | 5141.9 | 131.94 | 135.6 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 756 | 237812 | 01BUTCHERRUN | 235103 | 01BLACKO | 1 | 500 | 201 | AP_P2-3_PE-500-235103-SB4_SRT-SL | Breaker | 3260 | 4220.8 | 4365.8 | 129.47 | 133.92 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 25 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P1-2_PE-500-004A_SRT-A | Single | 3792 | 4914 | 4989.1 | 129.59 | 131.57 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 770 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P2-3_WP-500-DRT19_SRT-SL | Breaker | 3792 | 4907.8 | 4982.9 | 129.43 | 131.41 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 805 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P2-3_PE-500-015_SRT-A | Breaker | 3792 | 4781 | 4781 | 126.08 | 126.08 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 135 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P1-2_MP-500-511AT_SRT-SL | Single | 3792 | 4080.5 | 4185.9 | 107.61 | 110.39 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 136 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | DVP_P1-2: LN 554_SRT-A | Single | 3792 | 4078.3 | 4184.9 | 107.55 | 110.36 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 972 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | DVP_P4-2: MTS_554TB3_SRT-A | Breaker | 3792 | 4067.1 | 4177.7 | 107.26 | 110.17 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 974 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | DVP_P4-2: AH1_283_554X2_SRT-A | Breaker | 3792 | 4066.9 | 4176.3 | 107.25 | 110.13 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 2365 | 235103 | 01BLACKO | 235101 | 01BEDNGT | 1 | 500 | 201 | AP_P7-1_PE-500-235098-001_SRT-A | Tower | 3792 | 3827 | 4123.8 | 100.92 | 108.75 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 1034 | 235103 | 01BLACKO | 235101 | 01BEDNGT | 1 | 500 | 201 | AP_P2-3_PE-500-235103-SB6_SRT-SL | Breaker | 3792 | 3816.5 | 4098 | 100.65 | 108.07 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 168 | 235108 | 01HATFLD | 237812 | 01BUTCHERRUN | 1 | 500 | 201 | AP_P1-3_WP-500-DRT14_SRT-SL | Single | 2771 | 2997.6 | 2978.3 | 108.18 | 107.48 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 1069 | 235103 | 01BLACKO | 235101 | 01BEDNGT | 1 | 500 | 201 | NEET_P2-3_500-CB-A1_SRT-A | Breaker | 3792 | 3751.5 | 4035.9 | 98.93 | 106.43 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 1082 | 235103 | 01BLACKO | 235101 | 01BEDNGT | 1 | 500 | 201 | NEET_P2-3_500-CB-A_SRT-A | Breaker | 3792 | 3751.5 | 4018.3 | 98.93 | 105.97 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 217 | 235103 | 01BLACKO | 235101 | 01BEDNGT | 1 | 500 | 201 | AP_P1-2_PE-500-3838B_SRT-A | Single | 3792 | 3736.8 | 4003.6 | 98.54 | 105.58 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 246 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P1-2_WP-500-DRT19_SRT-SL | Single | 3792 | 3992.5 | 3967.3 | 105.29 | 104.62 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 1118 | 235098 | WOODSIDE | 235105 | 01DOUBS | 2 | 500 | 201 | NEET_P2-3_500-CB-D_SRT-A | Breaker | 4357 | 4458.9 | 4555.7 | 102.34 | 104.56 | No | Informational Only |  | 4490 | 5023 | N/A | 5435 | 5291 | 5723 | N/A | 6098 | 5144 | 5594 | N/A | 5973
Active | N/A | 1990 | 235851 | 01NTHLNV | 235111 | 01 502 J | 1 | 500 | 201 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus | 3792 | 3983.6 | 3958.4 | 105.05 | 104.39 | No | Informational Only |  | 3573 | 4378 | N/A | N/A | 4050 | 5194 | N/A | N/A | 3573 | 4378 | N/A | N/A
Active | N/A | 1123 | 235098 | WOODSIDE | 235105 | 01DOUBS | 2 | 500 | 201 | NEET_P2-3_500-CB-D1_SRT-A | Breaker | 4357 | 4446.2 | 4548 | 102.05 | 104.38 | No | Informational Only |  | 4490 | 5023 | N/A | 5435 | 5291 | 5723 | N/A | 6098 | 5144 | 5594 | N/A | 5973
Active | N/A | 2411 | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | AP_P7-1_PE-500-235098-003_SRT-SL | Tower | 4453 | 4530.4 | 4635.6 | 101.74 | 104.1 | No | Informational Only |  | 4330 | 4453 | #N/A | 5120 | 5066 | 5229 | #N/A | 6013 | 4936 | 5102 | #N/A | 5867
Active | N/A | 1155 | 235098 | WOODSIDE | 235105 | 01DOUBS | 2 | 500 | 201 | AP_P2-3_PE-500-019A_SRT-A | Breaker | 4357 | 4423.4 | 4515.4 | 101.52 | 103.64 | No | Informational Only |  | 4490 | 5023 | N/A | 5435 | 5291 | 5723 | N/A | 6098 | 5144 | 5594 | N/A | 5973
Active | N/A | 2415 | 235098 | WOODSIDE | 235105 | 01DOUBS | 2 | 500 | 201 | NEET_P7-1_WOODSIDE-DOUBS_SRT-A | Tower | 4357 | 4422.9 | 4514.9 | 101.51 | 103.62 | No | Informational Only |  | 4490 | 5023 | N/A | 5435 | 5291 | 5723 | N/A | 6098 | 5144 | 5594 | N/A | 5973
Active | N/A | 2420 | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | AP_P7-1_PE-500-235098-002B_SRT-SL | Tower | 4453 | 4498.9 | 4605.6 | 101.03 | 103.43 | No | Informational Only |  | 4330 | 4453 | #N/A | 5120 | 5066 | 5229 | #N/A | 6013 | 4936 | 5102 | #N/A | 5867
Active | N/A | 2422 | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | AP_P7-1_PE-500-235098-002A_SRT-SL | Tower | 4453 | 4498.6 | 4603.1 | 101.02 | 103.37 | No | Informational Only |  | 4330 | 4453 | #N/A | 5120 | 5066 | 5229 | #N/A | 6013 | 4936 | 5102 | #N/A | 5867
Active | N/A | 1171 | 235098 | WOODSIDE | 235105 | 01DOUBS | 2 | 500 | 201 | AP_P2-3_PE-500-019D_SRT-SL | Breaker | 4357 | 4410.9 | 4498.9 | 101.24 | 103.26 | No | Informational Only |  | 4490 | 5023 | N/A | 5435 | 5291 | 5723 | N/A | 6098 | 5144 | 5594 | N/A | 5973
Active | N/A | 283 | 235098 | WOODSIDE | 235105 | 01DOUBS | 2 | 500 | 201 | AP_P1-2_PE-500-3837_SRT-A | Single | 4357 | 4393.2 | 4484.3 | 100.83 | 102.92 | No | Informational Only |  | 4490 | 5023 | N/A | 5435 | 5291 | 5723 | N/A | 6098 | 5144 | 5594 | N/A | 5973
Active | N/A | 1207 | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | NEET_P2-3_500-CB-C_SRT-A | Breaker | 4453 | 4450.6 | 4555.7 | 99.95 | 102.31 | No | Informational Only |  | 4330 | 4453 | #N/A | 5120 | 5066 | 5229 | #N/A | 6013 | 4936 | 5102 | #N/A | 5867
Active | N/A | 1214 | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | NEET_P2-3_500-CB-C1_SRT-A | Breaker | 4453 | 4437.8 | 4548 | 99.66 | 102.13 | No | Informational Only |  | 4330 | 4453 | #N/A | 5120 | 5066 | 5229 | #N/A | 6013 | 4936 | 5102 | #N/A | 5867
Active | N/A | 330 | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | AP_P1-2_PE-500-3839_SRT-A | Single | 4453 | 4384.8 | 4484.3 | 98.47 | 100.7 | No | Informational Only |  | 4330 | 4453 | #N/A | 5120 | 5066 | 5229 | #N/A | 6013 | 4936 | 5102 | #N/A | 5867
Active | 2026W1-2034GD-S21 | 21 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | Base Case | Single | 1334 | 1771.5 | 1791.3 | 132.79 | 134.28 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S24 | 24 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | Base Case | Single | 1334 | 1745.9 | 1757.4 | 130.87 | 131.74 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S44 | 44 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | COMED_P1-2_345-L11602SR-S_SRT-A | Single | 1726 | 2146.1 | 2186.1 | 124.34 | 126.66 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S61 | 61 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | COMED_P1-2_345-L10805_B-S_SRT-A | Single | 1528 | 1868.4 | 1889.8 | 122.28 | 123.68 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-2034GD-S66 | 66 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | COMED_P1-2_345-L11601_B-S_SRT-A | Single | 1726 | 2082.7 | 2112.7 | 120.67 | 122.41 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S68 | 68 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | COMED_P1-2_345-L2001__B-S_SRT-A | Single | 1726 | 2075.8 | 2102.7 | 120.27 | 121.83 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S84 | 84 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | AEP_P1-2_#695_1681_SRT-A | Single | 1726 | 1976.6 | 2008.6 | 114.52 | 116.37 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S86 | 86 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | 765-L11215__-S_SRT-A | Single | 1726 | 1978.2 | 2005.9 | 114.61 | 116.22 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S95 | 95 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | COMED_P1-2_345-L6608__R-S_SRT-A | Single | 1726 | 1950 | 1975.7 | 112.98 | 114.47 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S110 | 110 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | COMED_P1-2_345-L90013_B-S_SRT-A | Single | 1726 | 1922.4 | 1951.8 | 111.38 | 113.08 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S116 | 116 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | AEP_P1-2_#695_1681_SRT-A | Single | 1726 | 1916.7 | 1937.1 | 111.05 | 112.23 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S117 | 117 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | 765-L11215__-S_SRT-A | Single | 1726 | 1918.2 | 1936.8 | 111.14 | 112.21 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S120 | 120 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | COMED_P1-2_345-L2004__R-S_SRT-A | Single | 1726 | 1917 | 1928.2 | 111.06 | 111.71 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S1949 | 1949 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | COMED_P2-2_023_CO-345R__1_SRT-A | Bus | 1726 | 1862.2 | 1885.5 | 107.89 | 109.24 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-2034GD-S1003 | 1003 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | COMED_P4_023-45-L2310___SRT-A | Breaker | 1726 | 1862.2 | 1885.5 | 107.89 | 109.24 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-2034GD-S1004 | 1004 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | COMED_P4_023-45-TR92____SRT-A | Breaker | 1726 | 1862.2 | 1885.5 | 107.89 | 109.24 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-2034GD-S1955 | 1955 | 270728 | E FRANKFO; B | 270770 | GOODINGS ; B | 1 | 345 | 222 | COMED_P2-2_111_EJ-345R__3_SRT-A | Bus | 1726 | 1840.8 | 1872.7 | 106.65 | 108.5 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S1959 | 1959 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | COMED_P2-2_023_CO-345R__1_SRT-A | Bus | 1726 | 1840.9 | 1864 | 106.65 | 107.99 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S164 | 164 | 270770 | GOODINGS ; B | 270810 | LOCKPORT ; B | 1 | 345 | 222 | Base Case | Single | 1334 | 1424.8 | 1437.6 | 106.81 | 107.77 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-2034GD-S165 | 165 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | Base Case | Single | 1201 | 1282.7 | 1293.4 | 106.81 | 107.69 | YES |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-S166 | 166 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | Base Case | Single | 1201 | 1282.7 | 1293.3 | 106.81 | 107.69 | YES |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-S177 | 177 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | COMED_P1-2_345-L2310___-S_SRT-A | Single | 1726 | 1826.6 | 1848.8 | 105.83 | 107.12 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-2034GD-S1966 | 1966 | 270729 | E FRANKFO; R | 270769 | GOODINGS ; R | 1 | 345 | 222 | COMED_P2-2_111_EJ-345R__3_SRT-A | Bus | 1726 | 1823.4 | 1846.9 | 105.64 | 107 | YES |  |  | 2391.4252 | 2391.4252 | 2435.6445 | 2587.4241 | 2591.0094 | 2591.0094 | 2648.375 | 2832.4227 | 2547.9853 | 2547.9853 | 2601.7655 | 2778.6425
Active | 2026W1-2034GD-S210 | 210 | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | Base Case | Single | 1201 | 1259.9 | 1272.5 | 104.9 | 105.96 | YES |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-2034GD-S281 | 281 | 270769 | GOODINGS ; R | 270811 | LOCKPORT ; R | 1 | 345 | 222 | Base Case | Single | 1334 | 1366.3 | 1375.2 | 102.42 | 103.09 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1856 | 1856 | 2325.0963 | 1547.0764 | 1879.3184 | 1856 | 2273.1088
Active | 2026W1-2034GD-S282 | 282 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | Base Case | Single | 1201 | 1230 | 1237.7 | 102.41 | 103.06 | YES |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | N/A | 229 | 200013 | PCHBTM2N | 200024 | LIMERICK | 1 | 500 | 230 | DPL_P1_2_CKT 5025_SRT-A | Single | 2983 | 3108.8 | 3141.8 | 104.22 | 105.32 | No | Informational Only |  | 2347 | 3145 | N/A | N/A | 3145 | 3972 | N/A | N/A | 2986 | 3807 | N/A | N/A
Active | N/A | 1103 | 200013 | PCHBTM2N | 200024 | LIMERICK | 1 | 500 | 230 | DPL_P4_2_KEENEY-ROCK AT50_SRT-A | Breaker | 2983 | 3108.3 | 3141.8 | 104.2 | 105.32 | No | Informational Only |  | 2347 | 3145 | N/A | N/A | 3145 | 3972 | N/A | N/A | 2986 | 3807 | N/A | N/A
Active | N/A | 1102 | 200013 | PCHBTM2N | 200024 | LIMERICK | 1 | 500 | 230 | DPL_P4_2_KEENEY-ROCK AT51_SRT-A | Breaker | 2983 | 3108.3 | 3141.8 | 104.2 | 105.32 | No | Informational Only |  | 2347 | 3145 | N/A | N/A | 3145 | 3972 | N/A | N/A | 2986 | 3807 | N/A | N/A
Active | N/A | 1088 | 200051 | ROCKSPGS | 200010 | KEENEY | 1 | 500 | 235 | PECO_P4_LIMER225_SRT-A/* $ MONTCO $ PECO_P4_LIMER225 $ STBK | Breaker | 3302 | 3521 | 3490.8 | 106.63 | 105.72 | No | Informational Only |  | 2648 | 3440 | N/A | N/A | 3376 | 4195 | N/A | N/A | 3229 | 4041 | N/A | N/A
Active | N/A | 1104 | 200051 | ROCKSPGS | 200010 | KEENEY | 1 | 500 | 235 | PECO_P4_LIMER325_SRT-A/* $ MONTCO $ PECO_P4_LIMER325 $ STBK | Breaker | 3302 | 3504 | 3470 | 106.12 | 105.09 | No | Informational Only |  | 2648 | 3440 | N/A | N/A | 3376 | 4195 | N/A | N/A | 3229 | 4041 | N/A | N/A
Active | N/A | 238 | 200051 | ROCKSPGS | 200010 | KEENEY | 1 | 500 | 235 | PECO_P1-2_5010_SRT-A/* $ MONTCO $ PECO_P1-2_5010 $ L | Single | 3302 | 3504 | 3470 | 106.12 | 105.09 | No | Informational Only |  | 2648 | 3440 | N/A | N/A | 3376 | 4195 | N/A | N/A | 3229 | 4041 | N/A | N/A
Active | N/A | 1105 | 200051 | ROCKSPGS | 200010 | KEENEY | 1 | 500 | 235 | PECO_P4_PEACH055_SRT-A/* $ CHESCO $ PECO_P4_PEACH055 $ STBK | Breaker | 3302 | 3502.8 | 3469.1 | 106.08 | 105.06 | No | Informational Only |  | 2648 | 3440 | N/A | N/A | 3376 | 4195 | N/A | N/A | 3229 | 4041 | N/A | N/A
Active | N/A | 286 | 200051 | ROCKSPGS | 200010 | KEENEY | 1 | 500 | 235 | Base Case | Single | 2647 | 2812.1 | 2719.2 | 106.24 | 102.73 | No | Informational Only |  | 2648 | 3440 | N/A | N/A | 3376 | 4195 | N/A | N/A | 3229 | 4041 | N/A | N/A
Active | N/A | 1280 | 200051 | ROCKSPGS | 200010 | KEENEY | 1 | 500 | 235 | PECO_P4_PEACH065_SRT-A/* $ CHESCO $ PECO_P4_PEACH065 $ STBK | Breaker | 3302 | 3335.7 | 3312.7 | 101.02 | 100.32 | No | Informational Only |  | 2648 | 3440 | N/A | N/A | 3376 | 4195 | N/A | N/A | 3229 | 4041 | N/A | N/A
Active | N/A | 206 | 314929 | 8FRONT ROYAL | 314916 | 8MORRSVL | 1 | 500 | 345 | DVP_P1-2: LN 535_SRT-A | Single | 3219.5 | 3426.6 | 3414.8 | 106.43 | 106.07 | No | Informational Only |  | 3322 | 3425 | N/A | N/A | 4244 | 4376 | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 214 | 314910 | 8CUNINGHAM | 313378 | 8VONTAY | 1 | 500 | 345 | AEP_P1-3_#1372_05JOSHUA 765_1_SRT-A | Single | 4090.9 | 4298.4 | 4326 | 105.07 | 105.75 | No | Informational Only |  | 4356 | 4356 | N/A | N/A | 5154 | 5154 | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 221 | 314910 | 8CUNINGHAM | 313378 | 8VONTAY | 1 | 500 | 345 | AEP_P4_#18462_05JOSHUA 765_CB1_SRT-A | Single | 4090.9 | 4298.4 | 4317.1 | 105.07 | 105.53 | No | Informational Only |  | 4356 | 4356 | N/A | N/A | 5154 | 5154 | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 222 | 314910 | 8CUNINGHAM | 313378 | 8VONTAY | 1 | 500 | 345 | AEP_P4_#15068_05JOSHUA 138_H_SRT-A | Single | 4090.9 | 4298.4 | 4317.1 | 105.07 | 105.53 | No | Informational Only |  | 4356 | 4356 | N/A | N/A | 5154 | 5154 | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 223 | 314910 | 8CUNINGHAM | 313378 | 8VONTAY | 1 | 500 | 345 | AEP_P4_#6332_05JOSHUA 765_A1_SRT-A | Single | 4090.9 | 4299.8 | 4316.9 | 105.11 | 105.52 | No | Informational Only |  | 4356 | 4356 | N/A | N/A | 5154 | 5154 | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 232 | 314910 | 8CUNINGHAM | 313378 | 8VONTAY | 1 | 500 | 345 | DVP_P1-2: LN 289576_315986_1_SRT-A | Single | 4090.9 | 4279.7 | 4306.6 | 104.62 | 105.27 | No | Informational Only |  | 4356 | 4356 | N/A | N/A | 5154 | 5154 | N/A | N/A | N/A | N/A | N/A | N/A
Active | N/A | 878 | 235118 | 01SOBEND | 200011 | KEYSTONE | 1 | 500 | 226/201 | PN_P2-3_PN-500-DRT32_SRT-A | Breaker | 2078 | 2460.4 | 2421.3 | 118.4 | 116.52 | No | Informational Only |  | 3573 (PN and APS) | 4378 (PN and APS) | N/A | N/A | 4050 (PN and APS) | 5194 (PN and APS) | N/A | N/A | 3573 (PN and APS) | 4378 (PN and APS) | N/A | N/A
Active | N/A | 1228 | 200005 | CONEM-GH | 200009 | JUNI | 1 | 500 | 226/229 | NEET_P4_2_SRT-A | Breaker | 2844 | 2706.2 | 2896.5 | 95.15 | 101.84 | No | Informational Only | The conductor limits for PPL & PENELEC were not available at the time of window opening - please contact PJM if specific ratings are needed.
Active | N/A | 2288 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PL_18_P71_103518_SRT-A | Tower | 2844 | 3359.3 | 3470.7 | 118.12 | 122.04 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 864 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PL_30_P42_103492_SRT-A | Breaker | 2844 | 3270.3 | 3380.3 | 114.99 | 118.86 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 865 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PL_30_P42_000134_SRT-A | Breaker | 2844 | 3270.2 | 3380.2 | 114.98 | 118.85 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 890 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PL_30_P42_000145_SRT-A | Breaker | 2844 | 3156.9 | 3282 | 111 | 115.4 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 1029 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PL_18_P42_000129_SRT-A | Breaker | 2844 | 2917.5 | 3080.1 | 102.58 | 108.3 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 1079 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PL_18_P42_000130_SRT-A | Breaker | 2844 | 2867.2 | 3023 | 100.82 | 106.3 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 245 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PL_18_P12_000083_SRT-A | Single | 2844 | 2828 | 2979.2 | 99.44 | 104.75 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 297 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PN_P1-2_PN-500-007_SRT-A | Single | 2844 | 2787.1 | 2903 | 98 | 102.07 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 318 | 200076 | BERN500 | 200016 | 3 MILE I | 1 | 500 | 227/229 | PN_P1-2_PN-500-010T_SRT-A | Single | 2844 | 2742 | 2878.6 | 96.41 | 101.22 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (ME) | 4541 (ME) | N/A | N/A | 4262 (ME) | 5503 (ME) | N/A | N/A | 3678 (ME) | 4541 (ME) | N/A | N/A
Active | N/A | 943 | 200001 | ALBU | 200002 | BRANCHBG | 1 | 500 | 229/231 | PECO_P4_ELROY145_SRT-A/* $ MONTCO $ PECO_P4_ELROY145 $ STBK | Breaker | 3112 | 3506 | 3474.9 | 112.66 | 111.66 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (PSEG) | 4541 (PSEG) | N/A | N/A | 4262 (PSEG) | 5503 (PSEG) | N/A | N/A | 3678 (PSEG) | 4541 (PSEG) | N/A | N/A
Active | N/A | 968 | 200001 | ALBU | 200002 | BRANCHBG | 1 | 500 | 229/231 | PECO_P4_ELROY475_SRT-A/* $ MONTCO $ PECO_P4_ELROY475 $ STBK | Breaker | 3112 | 3464.4 | 3433 | 111.32 | 110.31 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (PSEG) | 4541 (PSEG) | N/A | N/A | 4262 (PSEG) | 5503 (PSEG) | N/A | N/A | 3678 (PSEG) | 4541 (PSEG) | N/A | N/A
Active | N/A | 202 | 200001 | ALBU | 200002 | BRANCHBG | 1 | 500 | 229/231 | PECO_P1-2_5028_SRT-A/* $ MONTCO $ PECO_P1-2_5028 $ L | Single | 3112 | 3330.4 | 3302.2 | 107.02 | 106.11 | No | Informational Only | The conductor limits for PPL were not available at the time of window opening - please contact PJM if specific ratings are needed | 3678 (PSEG) | 4541 (PSEG) | N/A | N/A | 4262 (PSEG) | 5503 (PSEG) | N/A | N/A | 3678 (PSEG) | 4541 (PSEG) | N/A | N/A