## N-1 Thermal
PJM N-1 Thermal Result (Winter 2031 Case) | [16 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-N1-WT1 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138/138 | 205/205 | 345 | 102.3188 | 103.99 | Tower | 'AEP_P7-1_#17439___SRT-A' | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A

## N-1 Volt Mag
Will be addressed through the interregional process
PJM N-1 Voltage Magnitude Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026W1-N1-WVM1 | 211962 | WHHA 1 | 69 | 229 | 0.8879 | 0.90168 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM2 | 211962 | WHHA 1 | 69 | 229 | 0.88774 | 0.90168 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM3 | 211962 | WHHA 1 | 69 | 229 | 0.88676 | 0.90168 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM4 | 211960 | WHHA 2 | 69 | 229 | 0.8879 | 0.90169 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM5 | 211960 | WHHA 2 | 69 | 229 | 0.88774 | 0.90169 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM6 | 211960 | WHHA 2 | 69 | 229 | 0.88676 | 0.90169 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM7 | 211946 | FLND DC | 69 | 229 | 0.89073 | 0.90443 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM8 | 211946 | FLND DC | 69 | 229 | 0.89057 | 0.90443 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM9 | 211946 | FLND DC | 69 | 229 | 0.88959 | 0.90443 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM10 | 211533 | FLND | 69 | 229 | 0.8896 | 0.90333 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM11 | 211533 | FLND | 69 | 229 | 0.88944 | 0.90333 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM12 | 211533 | FLND | 69 | 229 | 0.88846 | 0.90333 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM13 | 211532 | FLND TP2 | 69 | 229 | 0.89073 | 0.90444 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM14 | 211532 | FLND TP2 | 69 | 229 | 0.89057 | 0.90444 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM15 | 211532 | FLND TP2 | 69 | 229 | 0.8896 | 0.90444 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM16 | 210918 | WHHA DC | 69 | 229 | 0.8879 | 0.90169 | 0.893 | Line_FB | PL_40_P42_101979_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM17 | 210918 | WHHA DC | 69 | 229 | 0.88774 | 0.90169 | 0.893 | Line_FB | PL_40_P42_101982_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N1-WVM18 | 210918 | WHHA DC | 69 | 229 | 0.88676 | 0.90169 | 0.893 | Line_FB | PL_40_P43_102414_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment

## N-1 Load Drop
PJM N-1 Load Drop Result (Winter 2031 Case)
FG # Status | FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational Only | N/A | DVP_P1-2: LN 9812_SRT-W | Single | 345 | 0.0 | 327.7 | 327.7 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P1-2: LN 2375_SRT-A | Single | 345 | 0.0 | 327.7 | 327.7 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P4-2: AE1157_256T9812_SRT-W | Line_FB | 345 | 0.0 | 327.7 | 327.7 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P4-2: FOU_2061T9812_SRT-W | Line_FB | 345 | 0.0 | 327.7 | 327.7 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P4-2: FOU_2125T9812_SRT-W | Line_FB | 345 | 0.0 | 327.7 | 327.7 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P4-3: WSH_L142_SRT-A | Line_FB | 345 | 0.0 | 495.2 | 495.2 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P4-2: 2375T9500_SRT-A | Line_FB | 345 | 0.0 | 327.7 | 327.7 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P2-1: LN 9812_SRT-A | P2_1 | 345 | 0.0 | 327.7 | 327.7 | No | To be adressed through supplemental process.
Informational Only | N/A | DVP_P7-1: LN 2165-2170_SRT-A | Tower | 345 | 0.0 | 345.0 | 345 | No | To be adressed through supplemental process.