## Winter GenDeliv
2031 RTEP PJM Generator Deliverability Result (Winter) | [19 empty] | Conductor/Transformer Limit
FG # Status | FG # | FG Index | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-GD-W198 | 198 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 345 | 355.7 | 361.5 | 103.1 | 104.78 | AEP_P7-1_#17439___SRT-A | Tower | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026W1-GD-W115 | 115 | 239154 | 02W.FREM | 243009 | 05FRMNT | 1 | 138 | 202/205 | 450 | 454.5 | 453.6 | 101 | 100.8 | AEP_P4_#17249_05FOSTOR 345_A1_SRT-A | Breaker | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 296/312 | 398/380 | #N/A | 429 | 375/353 | 452/450 | #N/A | 487 | 296/312 | 398/380 | #N/A | 429
Active | 2026W1-GD-W200 | 200 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 345 | 341.1 | 346.8 | 98.87 | 100.53 | AEP_P7-1_#17440___SRT-A | Tower | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A

## Winter IPD
2031 RTEP PJM Individual Plant Deliverability Result (Winter) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)