## Thermal
PJM N-1-1 Thermal Result (Winter 2031 Case) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-N11-WT1 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069B_SRT-A | 137.87 | 137.66 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-WT2 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23069B_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 137.87 | 135.29 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-WT3 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23034_SRT-A | DPL_P1_2_CKT 23069A_SRT-A | 137.57 | 135 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-WT4 | 232117 | VIENNA 8 | 232119 | NELSON | 1 | 138 | 235 | 192 | 211 | DPL_P1_2_CKT 23069A_SRT-A | DPL_P1_2_CKT 23034_SRT-A | 137.57 | 132.42 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap DPL EOL candidate | 392 | 485 | N/A | 540 | 452 | 546 | N/A | 610 | 439 | 534 | N/A | 595
Active | 2026W1-N11-WT5 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 118.71 | 115.23 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT6 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#8668_659_SRT-A | 118.71 | 114.46 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT7 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#8668_659_SRT-A | 115.87 | 112.15 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT8 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 115.87 | 112.4 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT9 | 243579 | 05STROUD | 243835 | 05STRDREQ2 | 1 | 138/1.0 | 205 | 105 | 118 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 111.53 | 111.53 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 93 | 107 | N/A | N/A | 105 | 118 | N/A | N/A | 96 | 110 | N/A | N/A
Active | 2026W1-N11-WT10 | 243579 | 05STROUD | 243835 | 05STRDREQ2 | 1 | 138/1.0 | 205 | 105 | 118 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 111.53 | 111.53 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 93 | 107 | N/A | N/A | 105 | 118 | N/A | N/A | 96 | 110 | N/A | N/A
Active | 2026W1-N11-WT11 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#5858_13837_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 110.25 | 109.68 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT12 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#18473_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 107.89 | 107.32 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT13 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5858_13837_SRT-A | 110.25 | 107 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT14 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 110.58 | 107.11 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT15 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 107.17 | 106.23 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT16 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | DAY_P1_MILLCREEK_MEADOW_138KV_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 107.26 | 105.88 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT17 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#8668_659_SRT-A | 110.58 | 106.33 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT18 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#18473_SRT-A | 107.89 | 104.64 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT19 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#5858_13837_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 105.13 | 104.56 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT20 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | ATSI_P1-2_OES-138-035B_SRT-A | 107.17 | 104.3 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT21 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#5784_654_SRT-A | Base Case | 109.32 | 104.25 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT22 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#8668_659_SRT-A | 107.73 | 104 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT23 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | DAY_P1_DARBY_MEADOW_138KV_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 104.4 | 103.9 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT24 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | DAY_P1_MILLCREEK_MEADOW_138KV_SRT-A | 107.26 | 103.68 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT25 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#17431_SRT-A | AEP_P1-2_#6227_574_SRT-A | 104.71 | 104.59 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026W1-N11-WT26 | 238574 | 02BELPT+ | 238964 | 02MLCRK+ | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 107.73 | 104.25 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT27 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#6227_574_SRT-A | AEP_P1-2_#17431_SRT-A | 104.71 | 104.16 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026W1-N11-WT28 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#727_573_SRT-A | 103.79 | 103.88 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026W1-N11-WT29 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#727_573_SRT-A | AEP_P1-2_#13648_26782_SRT-A | 103.79 | 103.64 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026W1-N11-WT30 | 243499 | 05DUBLIN CS | 247873 | 05BRITTON | 1 | 138 | 205 | 269 | 345 | AEP_P1-2_#17432_SRT-A | AEP_P1-2_#6227_574_SRT-A | 100.42 | 100.3 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A | 269 | 345 | N/A | N/A
Active | 2026W1-N11-WT31 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | Base Case | 106.48 | 102.96 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT32 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | Base Case | 104.05 | 102.99 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT33 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#18473_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 102.76 | 102.18 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT34 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5858_13837_SRT-A | 105.13 | 102.11 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT35 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | DAY_P1_DARBY_MEADOW_138KV_SRT-A | 104.4 | 101.81 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT36 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5784_654_SRT-A | 102.97 | 102.16 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT37 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 102.07 | 101.13 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT38 | 238964 | 02MLCRK+ | 291044 | 09MEADOW | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#8668_659_SRT-A | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | 105.22 | 101.73 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT39 | 243526 | 05HYATT | 245952 | 05DLAWAR1 | 2 | 138 | 205 | 248 | 286 | DAY_P1_MILLCREEK_MEADOW_138KV_SRT-A | AEP_P1-2_#7211_300000_SRT-A | 102.29 | 100.92 | No | Substation Equipment Exclusion |  | 492 | 492 | N/A | N/A | 519 | 519 | N/A | N/A | 500 | 500 | N/A | N/A
Active | 2026W1-N11-WT40 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | Base Case | 103.39 | 101.29 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT41 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | Base Case | 103.39 | 101.29 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT42 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 281 | 281 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#18125_SRT-A | 100.89 | 100.64 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N11-WT43 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#18125_SRT-A | Base Case | 102.14 | 101.34 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT44 | 238964 | 02MLCRK+ | 291044 | 09MEADOW | 1 | 138 | 202 | 180 | 228 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#8668_659_SRT-A | 105.22 | 100.95 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT45 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | AEP_P1-2_#5784_654_SRT-A | 103.09 | 101 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT46 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | AEP_P1-2_#5784_654_SRT-A | 103.09 | 101 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT47 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | 101.49 | 100.84 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217
Active | 2026W1-N11-WT48 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | Base Case | 100.85 | 100.2 | No | Substation Equipment Exclusion; Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 160 | 192 | N/A | 217 | 180 | 228 | N/A | 246 | 160 | 192 | N/A | 217

## Volt Mag
To be addressed by Interregional process
PJM N-1-1 Voltage Magnitude Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2026W1-N11-WVM1 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.89789 | 0.88906 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM2 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.8979 | 0.88906 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM3 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.8979 | 0.88906 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM4 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.89789 | 0.89038 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM5 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.8979 | 0.89038 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM6 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.8979 | 0.89039 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM7 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.89789 | 0.8904 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM8 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.8979 | 0.89041 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM9 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.8979 | 0.89041 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM10 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.89789 | 0.89046 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM11 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.8979 | 0.89046 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM12 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.8979 | 0.89047 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM13 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.89789 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM14 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.8979 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM15 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.8979 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM16 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.89955 | 0.89075 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM17 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.90067 | 0.89188 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM18 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P14_102839_SRT-A | 0.90067 | 0.89189 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM19 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P12_000189_SRT-A | 0.89955 | 0.89207 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM20 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_48_P11_000840_SRT-A | 0.89955 | 0.89209 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM21 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001449_SRT-A | 0.89955 | 0.89215 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM22 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_000002_SRT-A | PL_40_P11_001448_SRT-A | 0.89955 | 0.89216 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM23 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.89962 | 0.89098 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM24 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.89962 | 0.89098 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM25 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.89962 | 0.89098 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM26 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P12_000189_SRT-A | 0.89962 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM27 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P12_000189_SRT-A | 0.89962 | 0.89133 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM28 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P12_000189_SRT-A | 0.89962 | 0.89133 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM29 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_08_P12_000081A_SRT-A | 0.90127 | 0.89267 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM30 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89376 | 0.88914 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM31 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89376 | 0.88914 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM32 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89376 | 0.88914 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM33 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89376 | 0.88919 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM34 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89376 | 0.88919 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM35 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89376 | 0.88919 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM36 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89376 | 0.88945 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM37 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89376 | 0.88945 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM38 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89376 | 0.88945 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM39 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89376 | 0.88994 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM40 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89376 | 0.88994 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM41 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89376 | 0.88994 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM42 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89376 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM43 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89376 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM44 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89376 | 0.89011 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM45 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89544 | 0.89084 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM46 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89544 | 0.89088 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM47 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89544 | 0.89114 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM48 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_100842_SRT-A | 0.89376 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM49 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_100842_SRT-A | 0.89376 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM50 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_100842_SRT-A | 0.89376 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM51 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89376 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM52 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89376 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM53 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89376 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM54 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081_SRT-A | 0.89376 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM55 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081_SRT-A | 0.89376 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM56 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081_SRT-A | 0.89376 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM57 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_103307_SRT-A | 0.89376 | 0.89154 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM58 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_103307_SRT-A | 0.89376 | 0.89154 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM59 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_103307_SRT-A | 0.89376 | 0.89154 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM60 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446A_SRT-A | 0.89376 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM61 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446A_SRT-A | 0.89376 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM62 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446A_SRT-A | 0.89376 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM63 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89544 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM64 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89544 | 0.8918 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM65 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89656 | 0.89197 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM66 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P14_103484_SRT-A | 0.89656 | 0.89197 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM67 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89656 | 0.89201 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM68 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100410_SRT-A | 0.89656 | 0.89202 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM69 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89656 | 0.89227 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM70 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_40_P12_100411_SRT-A | 0.89656 | 0.89228 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM71 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89656 | 0.89276 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM72 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P14_001171_SRT-A | 0.89656 | 0.89276 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM73 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_000793_SRT-A | 0.89544 | 0.89291 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM74 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_100446_SRT-A | 0.89544 | 0.89292 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM75 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89656 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM76 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P12_000081A_SRT-A | 0.89656 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM77 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_001557_SRT-A | 0.89656 | 0.89296 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM78 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P13_001557_SRT-A | 0.89656 | 0.89296 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM79 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001447_SRT-A | 0.89544 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM80 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_48_P12_100842_SRT-A | 0.89544 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM81 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | PL_08_P11_001446_SRT-A | 0.89544 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM82 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P11_000840_SRT-A | 0.90058 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM83 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P11_000840_SRT-A | 0.90059 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM84 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P11_000840_SRT-A | 0.90059 | 0.89159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM85 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P12_000189_SRT-A | 0.90058 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM86 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P12_000189_SRT-A | 0.90059 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM87 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_48_P12_000189_SRT-A | 0.90059 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM88 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001449_SRT-A | 0.90058 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM89 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001449_SRT-A | 0.90059 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM90 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001449_SRT-A | 0.90059 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM91 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001448_SRT-A | 0.90058 | 0.89167 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM92 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001448_SRT-A | 0.90059 | 0.89167 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM93 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | PL_40_P11_001448_SRT-A | 0.90059 | 0.89167 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM94 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90058 | 0.89174 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM95 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90059 | 0.89174 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM96 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446A_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90059 | 0.89174 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM97 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.89989 | 0.891 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM98 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.89989 | 0.891 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM99 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.89989 | 0.89101 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM100 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.89989 | 0.89102 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM101 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.89989 | 0.89102 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM102 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.89989 | 0.89102 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM103 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.89989 | 0.89108 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM104 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.89989 | 0.89108 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM105 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.89989 | 0.89108 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM106 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.89989 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM107 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.89989 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM108 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.89989 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM109 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89989 | 0.89124 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM110 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89989 | 0.89124 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM111 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89989 | 0.89124 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM112 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001448_SRT-A | 0.90154 | 0.89269 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM113 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_40_P11_001449_SRT-A | 0.90154 | 0.8927 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM114 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P12_000189_SRT-A | 0.90154 | 0.89276 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM115 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | PL_48_P11_000840_SRT-A | 0.90154 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM116 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_000793_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90154 | 0.89292 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM117 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89378 | 0.88996 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM118 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89378 | 0.88996 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM119 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89379 | 0.88996 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM120 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89378 | 0.89016 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM121 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89378 | 0.89016 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM122 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89379 | 0.89016 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM123 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89378 | 0.89037 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM124 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89378 | 0.89037 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM125 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89379 | 0.89037 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM126 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89378 | 0.89124 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM127 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89378 | 0.89125 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM128 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89379 | 0.89125 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM129 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89378 | 0.89125 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM130 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89378 | 0.89125 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM131 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89379 | 0.89126 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM132 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001447_SRT-A | 0.89378 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM133 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001447_SRT-A | 0.89378 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM134 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001447_SRT-A | 0.89379 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM135 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_100842_SRT-A | 0.89378 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM136 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89378 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM137 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_100842_SRT-A | 0.89378 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM138 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89378 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM139 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_100842_SRT-A | 0.89379 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM140 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89379 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM141 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_103307_SRT-A | 0.89378 | 0.89156 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM142 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_103307_SRT-A | 0.89378 | 0.89156 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM143 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P12_103307_SRT-A | 0.89379 | 0.89156 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM144 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446A_SRT-A | 0.89378 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM145 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446A_SRT-A | 0.89378 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM146 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446A_SRT-A | 0.89379 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM147 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89546 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM148 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89546 | 0.89185 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM149 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_40_P14_000002_SRT-A | 0.89546 | 0.89206 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM150 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89658 | 0.89278 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM151 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P14_001171_SRT-A | 0.89658 | 0.89278 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM152 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_000793_SRT-A | 0.89546 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM153 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_100446_SRT-A | 0.89546 | 0.89294 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM154 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89546 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM155 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89658 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM156 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_48_P13_001557_SRT-A | 0.89658 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM157 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001447_SRT-A | 0.89546 | 0.893 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM158 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88794 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM159 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88794 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM160 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88794 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM161 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.89982 | 0.88964 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM162 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.90093 | 0.89077 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM163 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_40_P14_102839_SRT-A | 0.90093 | 0.89077 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM164 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_48_P13_001557_SRT-A | 0.89816 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM165 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_48_P13_001557_SRT-A | 0.89816 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM166 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_000870_SRT-A | PL_48_P13_001557_SRT-A | 0.89816 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM167 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89772 | 0.88889 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM168 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89772 | 0.88889 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM169 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89772 | 0.88889 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM170 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89772 | 0.88997 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM171 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89772 | 0.88997 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM172 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89772 | 0.88998 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM173 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89772 | 0.88999 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM174 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89772 | 0.88999 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM175 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89772 | 0.89 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM176 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89772 | 0.89005 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM177 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89772 | 0.89005 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM178 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89772 | 0.89006 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM179 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89772 | 0.89006 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM180 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89772 | 0.89007 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM181 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89772 | 0.89007 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM182 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89772 | 0.89013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM183 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89772 | 0.89013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM184 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89772 | 0.89013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM185 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.89938 | 0.89058 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM186 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.89938 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM187 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.89938 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM188 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.9005 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM189 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P14_102839_SRT-A | 0.9005 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM190 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.89938 | 0.89174 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM191 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.89938 | 0.89176 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM192 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89938 | 0.89182 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM193 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.9005 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM194 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P12_000189_SRT-A | 0.9005 | 0.89279 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM195 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.9005 | 0.89281 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM196 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_48_P11_000840_SRT-A | 0.9005 | 0.89282 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM197 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.9005 | 0.89287 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM198 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001449_SRT-A | 0.9005 | 0.89287 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM199 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.9005 | 0.89288 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM200 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | PL_40_P11_001448_SRT-A | 0.9005 | 0.89289 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM201 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9005 | 0.89294 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM202 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P14_001171_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.9005 | 0.89295 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM203 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.89995 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM204 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.89995 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM205 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.89996 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM206 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.89995 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM207 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.89995 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM208 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.89996 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM209 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.89995 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM210 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.89995 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM211 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.89995 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM212 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.89996 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM213 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.89995 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM214 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.89996 | 0.89118 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM215 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89995 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM216 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89995 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM217 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89996 | 0.89139 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM218 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001449_SRT-A | 0.9016 | 0.89278 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM219 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P12_000189_SRT-A | 0.9016 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM220 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_40_P11_001448_SRT-A | 0.9016 | 0.89286 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM221 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001446_SRT-A | PL_48_P11_000840_SRT-A | 0.9016 | 0.89286 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM222 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.89993 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM223 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.89993 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM224 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.89993 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM225 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.89993 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM226 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.89993 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM227 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.89993 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM228 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM229 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM230 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.89993 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM231 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM232 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.89993 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM233 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.89993 | 0.89117 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM234 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89993 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM235 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89993 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM236 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89993 | 0.89131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM237 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001448_SRT-A | 0.90158 | 0.89278 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM238 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P12_000189_SRT-A | 0.90158 | 0.89283 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM239 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_40_P11_001449_SRT-A | 0.90158 | 0.89285 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM240 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | PL_48_P11_000840_SRT-A | 0.90158 | 0.89285 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM241 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P11_001447_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90158 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM242 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89385 | 0.89003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM243 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89385 | 0.89003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM244 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89386 | 0.89003 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM245 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.89385 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM246 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.89385 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM247 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.89386 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM248 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.89385 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM249 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.89385 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM250 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.89386 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM251 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.89385 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM252 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.89385 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM253 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.89386 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM254 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_000793_SRT-A | 0.89385 | 0.89108 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM255 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_000793_SRT-A | 0.89385 | 0.89108 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM256 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_000793_SRT-A | 0.89386 | 0.89108 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM257 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446_SRT-A | 0.89385 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM258 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446_SRT-A | 0.89385 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM259 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446_SRT-A | 0.89386 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM260 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89385 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM261 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89385 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM262 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89386 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM263 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_100842_SRT-A | 0.89385 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM264 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_100842_SRT-A | 0.89385 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM265 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_100842_SRT-A | 0.89386 | 0.89141 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM266 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_103307_SRT-A | 0.89385 | 0.89162 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM267 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_103307_SRT-A | 0.89385 | 0.89162 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM268 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P12_103307_SRT-A | 0.89386 | 0.89163 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM269 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446A_SRT-A | 0.89385 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM270 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446A_SRT-A | 0.89385 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM271 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_100446A_SRT-A | 0.89386 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM272 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89553 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM273 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_000081A_SRT-A | 0.89553 | 0.89191 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM274 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P13_001557_SRT-A | 0.89553 | 0.89191 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM275 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_40_P14_000002_SRT-A | 0.89553 | 0.89213 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM276 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_000793_SRT-A | 0.89553 | 0.89277 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM277 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89665 | 0.89285 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM278 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_48_P14_001171_SRT-A | 0.89665 | 0.89285 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM279 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_001447_SRT-A | 0.89553 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM280 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89384 | 0.89002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM281 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89384 | 0.89002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM282 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89384 | 0.89002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM283 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89384 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM284 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89384 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM285 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89384 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM286 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89384 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM287 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89384 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM288 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89384 | 0.89021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM289 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89384 | 0.89043 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM290 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89384 | 0.89043 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM291 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89384 | 0.89043 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM292 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_000793_SRT-A | 0.89384 | 0.89109 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM293 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_000793_SRT-A | 0.89384 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM294 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_000793_SRT-A | 0.89384 | 0.8911 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM295 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_100842_SRT-A | 0.89384 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM296 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_100842_SRT-A | 0.89384 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM297 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_100842_SRT-A | 0.89384 | 0.89132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM298 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446_SRT-A | 0.89384 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM299 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446_SRT-A | 0.89384 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM300 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446_SRT-A | 0.89384 | 0.89134 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM301 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89384 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM302 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89384 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM303 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89384 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM304 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_103307_SRT-A | 0.89384 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM305 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_103307_SRT-A | 0.89384 | 0.89161 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM306 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P12_103307_SRT-A | 0.89384 | 0.89162 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM307 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446A_SRT-A | 0.89384 | 0.8917 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM308 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446A_SRT-A | 0.89384 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM309 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_100446A_SRT-A | 0.89384 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM310 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89552 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM311 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_000081A_SRT-A | 0.89552 | 0.8919 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM312 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P13_001557_SRT-A | 0.89552 | 0.8919 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM313 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_40_P14_000002_SRT-A | 0.89552 | 0.89212 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM314 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_000793_SRT-A | 0.89552 | 0.89278 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM315 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89664 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM316 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_48_P14_001171_SRT-A | 0.89664 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM317 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_001446_SRT-A | 0.89552 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM318 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P11_001447_SRT-A | 0.89552 | 0.893 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM319 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89688 | 0.89017 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM320 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89688 | 0.89017 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM321 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89688 | 0.89017 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM322 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89688 | 0.89019 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM323 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89688 | 0.89019 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM324 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89688 | 0.89019 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM325 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89688 | 0.89024 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM326 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89688 | 0.89024 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM327 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89688 | 0.89024 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM328 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89688 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM329 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89688 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM330 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89688 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM331 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89688 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM332 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89688 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM333 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89688 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM334 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_000870_SRT-A | 0.89688 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM335 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89688 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM336 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_000870_SRT-A | 0.89688 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM337 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89688 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM338 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100411_SRT-A | 0.89688 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM339 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100411_SRT-A | 0.89688 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM340 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_000870_SRT-A | 0.89688 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM341 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89688 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM342 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100411_SRT-A | 0.89688 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM343 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89854 | 0.89186 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM344 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89854 | 0.89188 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM345 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89854 | 0.89193 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM346 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001448_SRT-A | 0.89854 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM347 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P13_100388_SRT-A | 0.89688 | 0.89272 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM348 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P13_100388_SRT-A | 0.89688 | 0.89272 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM349 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P13_100388_SRT-A | 0.89688 | 0.89272 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM350 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P12_100410_SRT-A | 0.89854 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM351 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89966 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM352 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P12_000189_SRT-A | 0.89966 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM353 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_60_P13_001558_SRT-A | 0.89688 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM354 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_60_P13_001558_SRT-A | 0.89688 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM355 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_60_P13_001558_SRT-A | 0.89688 | 0.893 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM356 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.8997 | 0.88829 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM357 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.89971 | 0.8883 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM358 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.89971 | 0.8883 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM359 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.90136 | 0.88999 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM360 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.90247 | 0.89112 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM361 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_40_P14_102839_SRT-A | 0.90247 | 0.89113 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM362 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_48_P13_001557_SRT-A | 0.8997 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM363 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_48_P13_001557_SRT-A | 0.89971 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM364 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_60_P13_001558_SRT-A | PL_48_P13_001557_SRT-A | 0.89971 | 0.893 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM365 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.89956 | 0.88839 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM366 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.89956 | 0.88839 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM367 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.89956 | 0.88839 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM368 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.90121 | 0.89009 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM369 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.90232 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM370 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_40_P14_102839_SRT-A | 0.90232 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM371 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_48_P13_001557_SRT-A | 0.89956 | 0.89272 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM372 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_48_P13_001557_SRT-A | 0.89956 | 0.89272 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM373 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100388_SRT-A | PL_48_P13_001557_SRT-A | 0.89956 | 0.89272 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM374 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM375 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM376 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM377 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89816 | 0.89076 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM378 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89816 | 0.89076 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM379 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89816 | 0.89076 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM380 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.89982 | 0.89092 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM381 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.90093 | 0.89205 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM382 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_40_P14_102839_SRT-A | 0.90094 | 0.89206 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM383 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100404_SRT-A | PL_48_P12_000189_SRT-A | 0.89982 | 0.89245 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM384 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.89795 | 0.8876 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM385 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.89795 | 0.88761 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM386 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.89795 | 0.88761 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM387 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.89795 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM388 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.89795 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM389 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.89795 | 0.88923 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM390 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.89961 | 0.88931 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM391 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.90072 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM392 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_102839_SRT-A | 0.90072 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM393 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.89961 | 0.89092 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM394 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.89795 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM395 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.89795 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM396 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.89795 | 0.89115 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM397 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.90072 | 0.89205 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM398 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P12_000189_SRT-A | 0.90072 | 0.89205 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM399 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_48_P13_001557_SRT-A | 0.89961 | 0.89284 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM400 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_103484_SRT-A | 0.89795 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM401 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_103484_SRT-A | 0.89795 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM402 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100410_SRT-A | PL_40_P14_103484_SRT-A | 0.89795 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM403 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.89867 | 0.88781 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM404 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.89867 | 0.88781 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM405 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.89867 | 0.88781 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM406 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.89867 | 0.88949 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM407 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.89867 | 0.88949 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM408 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.89867 | 0.88949 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM409 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.90033 | 0.88951 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM410 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.90144 | 0.89064 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM411 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_40_P14_102839_SRT-A | 0.90144 | 0.89064 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM412 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.90033 | 0.89119 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM413 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P13_001557_SRT-A | 0.89867 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM414 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P13_001557_SRT-A | 0.89867 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM415 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P13_001557_SRT-A | 0.89867 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM416 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.90144 | 0.89231 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM417 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P12_100411_SRT-A | PL_48_P12_000189_SRT-A | 0.90144 | 0.89232 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM418 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P12_000189_SRT-A | 0.90084 | 0.89127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM419 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P12_000189_SRT-A | 0.90085 | 0.89127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM420 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P12_000189_SRT-A | 0.90085 | 0.89127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM421 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P11_000840_SRT-A | 0.90084 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM422 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P11_000840_SRT-A | 0.90085 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM423 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P11_000840_SRT-A | 0.90085 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM424 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001449_SRT-A | 0.90084 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM425 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001448_SRT-A | 0.90084 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM426 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001449_SRT-A | 0.90085 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM427 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001448_SRT-A | 0.90085 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM428 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001449_SRT-A | 0.90085 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM429 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_40_P11_001448_SRT-A | 0.90085 | 0.89138 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM430 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90084 | 0.89145 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM431 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90085 | 0.89145 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM432 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90085 | 0.89145 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM433 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P12_000189_SRT-A | 0.90249 | 0.89295 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM434 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P13_100446_SRT-A | PL_48_P11_000840_SRT-A | 0.90249 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM435 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P12_000189_SRT-A | 0.90087 | 0.89133 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM436 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P12_000189_SRT-A | 0.90087 | 0.89133 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM437 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P12_000189_SRT-A | 0.90087 | 0.89133 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM438 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001449_SRT-A | 0.90087 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM439 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001449_SRT-A | 0.90087 | 0.89135 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM440 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P11_000840_SRT-A | 0.90087 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM441 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001449_SRT-A | 0.90087 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM442 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P11_000840_SRT-A | 0.90087 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM443 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_48_P11_000840_SRT-A | 0.90087 | 0.89136 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM444 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001448_SRT-A | 0.90087 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM445 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001448_SRT-A | 0.90087 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM446 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | PL_40_P11_001448_SRT-A | 0.90087 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM447 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90087 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM448 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90087 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM449 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_100842_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.90087 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM450 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100410_SRT-A | 0.89392 | 0.88931 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM451 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100411_SRT-A | 0.89392 | 0.88951 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM452 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P11_000870_SRT-A | 0.89392 | 0.88964 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM453 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89392 | 0.88964 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM454 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_103484_SRT-A | 0.89392 | 0.88971 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM455 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P13_100388_SRT-A | 0.89392 | 0.89009 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM456 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100410_SRT-A | 0.89504 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM457 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100410_SRT-A | 0.89504 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM458 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P14_001171_SRT-A | 0.89392 | 0.89058 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM459 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100411_SRT-A | 0.89504 | 0.89064 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM460 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100411_SRT-A | 0.89504 | 0.89064 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM461 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_000002_SRT-A | 0.89392 | 0.89075 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM462 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P11_000870_SRT-A | 0.89504 | 0.89077 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM463 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89504 | 0.89077 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM464 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P11_000870_SRT-A | 0.89504 | 0.89078 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM465 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | 209023 WIENIPP1 13.8 1 _SRT-A | 0.89504 | 0.89078 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM466 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_103484_SRT-A | 0.89504 | 0.89084 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM467 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_103484_SRT-A | 0.89504 | 0.89085 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM468 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100404_SRT-A | 0.89392 | 0.89092 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM469 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P12_103307_SRT-A | 0.89392 | 0.89103 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM470 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P13_100388_SRT-A | 0.89504 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM471 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P13_100388_SRT-A | 0.89504 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM472 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P14_001171_SRT-A | 0.89504 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM473 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P14_001171_SRT-A | 0.89504 | 0.89171 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM474 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_000002_SRT-A | 0.89504 | 0.89188 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM475 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P14_000002_SRT-A | 0.89504 | 0.89189 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM476 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100404_SRT-A | 0.89504 | 0.89205 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM477 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_40_P12_100404_SRT-A | 0.89504 | 0.89206 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM478 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P12_103307_SRT-A | 0.89504 | 0.89216 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM479 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | PL_48_P12_103307_SRT-A | 0.89504 | 0.89216 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM480 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | Base Case | 0.89224 | - | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM481 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | Base Case | 0.89224 | - | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM482 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_102839_SRT-A | Base Case | 0.89224 | - | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM483 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89825 | 0.88933 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM484 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89825 | 0.88933 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM485 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89826 | 0.88934 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM486 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.89991 | 0.89103 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM487 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P12_000189_SRT-A | 0.89825 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM488 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P12_000189_SRT-A | 0.89825 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM489 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P12_000189_SRT-A | 0.89826 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM490 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P11_000840_SRT-A | 0.89825 | 0.89159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM491 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P11_000840_SRT-A | 0.89825 | 0.89159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM492 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_48_P11_000840_SRT-A | 0.89826 | 0.89159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM493 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89825 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM494 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89825 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM495 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001449_SRT-A | 0.89825 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM496 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001449_SRT-A | 0.89825 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM497 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89826 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM498 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001449_SRT-A | 0.89826 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM499 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001448_SRT-A | 0.89825 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM500 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001448_SRT-A | 0.89825 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM501 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P11_001448_SRT-A | 0.89826 | 0.89166 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM502 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.90102 | 0.89216 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM503 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P12_103307_SRT-A | PL_40_P14_102839_SRT-A | 0.90103 | 0.89216 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM504 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89686 | 0.88801 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM505 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89686 | 0.88801 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM506 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89686 | 0.88801 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM507 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89686 | 0.88903 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM508 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89686 | 0.88904 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM509 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89686 | 0.88904 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM510 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89852 | 0.88971 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM511 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89852 | 0.89073 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM512 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89964 | 0.89084 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM513 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P14_102839_SRT-A | 0.89964 | 0.89085 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM514 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89964 | 0.89186 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM515 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_48_P12_000189_SRT-A | 0.89964 | 0.89186 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM516 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P12_100410_SRT-A | 0.89686 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM517 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P12_100410_SRT-A | 0.89686 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM518 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P14_103484_SRT-A | PL_40_P12_100410_SRT-A | 0.89686 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM519 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.89996 | 0.8912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM520 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.89996 | 0.8912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM521 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.89997 | 0.8912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM522 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.89996 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM523 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.89996 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM524 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.89997 | 0.89122 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM525 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001448_SRT-A | 0.89996 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM526 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001448_SRT-A | 0.89996 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM527 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001448_SRT-A | 0.89997 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM528 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89996 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM529 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89996 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM530 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89997 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM531 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P12_000189_SRT-A | 0.90161 | 0.89288 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM532 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_48_P11_000840_SRT-A | 0.90161 | 0.8929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM533 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001448_SRT-A | 0.90161 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM534 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.89405 | 0.89022 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM535 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.89405 | 0.89023 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM536 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.89405 | 0.89023 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM537 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_100842_SRT-A | 0.89405 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM538 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_100842_SRT-A | 0.89405 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM539 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_100842_SRT-A | 0.89405 | 0.89157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM540 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446_SRT-A | 0.89405 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM541 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446_SRT-A | 0.89405 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM542 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446_SRT-A | 0.89405 | 0.89158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM543 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_000793_SRT-A | 0.89405 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM544 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_000793_SRT-A | 0.89405 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM545 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_000793_SRT-A | 0.89405 | 0.89165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM546 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89405 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM547 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89405 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM548 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89405 | 0.89169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM549 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001446_SRT-A | 0.89405 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM550 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001446_SRT-A | 0.89405 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM551 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001446_SRT-A | 0.89405 | 0.89172 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM552 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_103307_SRT-A | 0.89405 | 0.89173 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM553 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_103307_SRT-A | 0.89405 | 0.89173 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM554 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P12_103307_SRT-A | 0.89405 | 0.89174 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM555 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P14_001171_SRT-A | 0.89572 | 0.89191 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM556 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446A_SRT-A | 0.89405 | 0.89202 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM557 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446A_SRT-A | 0.89405 | 0.89202 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM558 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_48_P13_100446A_SRT-A | 0.89405 | 0.89202 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM559 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88794 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM560 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88794 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM561 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89816 | 0.88794 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM562 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.89982 | 0.88964 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM563 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.90093 | 0.89077 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM564 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_40_P14_102839_SRT-A | 0.90093 | 0.89077 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM565 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_48_P13_001557_SRT-A | 0.89816 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM566 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_48_P13_001557_SRT-A | 0.89816 | 0.89152 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM567 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 209023 WIENIPP1 13.8 1 _SRT-A | PL_48_P13_001557_SRT-A | 0.89816 | 0.89153 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM568 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.89979 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM569 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.89979 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM570 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.89979 | 0.89015 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM571 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.89979 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM572 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.89979 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM573 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.89979 | 0.89025 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM574 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.89979 | 0.89026 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM575 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.89979 | 0.89026 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM576 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.89979 | 0.89026 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM577 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.89979 | 0.89099 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM578 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.89979 | 0.89099 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM579 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.89979 | 0.89099 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM580 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.90144 | 0.89184 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM581 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.90144 | 0.89194 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM582 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001448_SRT-A | 0.90144 | 0.89195 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM583 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_08_P12_000081_SRT-A | 0.90144 | 0.89267 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM584 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.90255 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM585 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_48_P12_000189_SRT-A | 0.90255 | 0.89297 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM586 | 235212 | 01LOYALH1 | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-138-052_SRT-A | AP_P1-3_WP-138-023_SRT-A | 0.9796 | 0.89884 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM587 | 235212 | 01LOYALH1 | 138 | 201 | 0.92 | 1.05 | AP_P1-3_WP-138-023_SRT-A | AP_P1-2_WP-138-052_SRT-A | 0.969 | 0.89884 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM588 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1205__B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.001 | 0.84163 | Yes
Active | 2026W1-N11-WVM589 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1205__B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0058 | 0.86787 | Yes
Active | 2026W1-N11-WVM590 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L1205__B-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0048 | 0.91052 | Yes
Active | 2026W1-N11-WVM591 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99821 | 0.904 | Yes
Active | 2026W1-N11-WVM592 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0043 | 0.90927 | Yes
Active | 2026W1-N11-WVM593 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0097 | 0.91197 | Yes
Active | 2026W1-N11-WVM594 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0041 | 0.91226 | Yes
Active | 2026W1-N11-WVM595 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.005 | 0.91872 | Yes
Active | 2026W1-N11-WVM596 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_345-L1223_TR-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0049 | 0.91888 | Yes
Active | 2026W1-N11-WVM597 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_DRESD_B-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.006 | 0.86651 | Yes
Active | 2026W1-N11-WVM598 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_DRESD_B-S_SRT-A | COMED_P1-2_138-L0112__B-S_SRT-A | 1.0044 | 0.90911 | Yes
Active | 2026W1-N11-WVM599 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L1205__B-S_SRT-A | 0.92622 | 0.841 | Yes
Active | 2026W1-N11-WVM600 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L1205__B-S_SRT-A | 0.93974 | 0.86721 | Yes
Active | 2026W1-N11-WVM601 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.92622 | 0.90367 | Yes
Active | 2026W1-N11-WVM602 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.92622 | 0.90467 | Yes
Active | 2026W1-N11-WVM603 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93169 | 0.90894 | Yes
Active | 2026W1-N11-WVM604 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93169 | 0.90995 | Yes
Active | 2026W1-N11-WVM605 | 272521 | STREATOR ; | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_138-L1205__B-S_SRT-A | 0.95956 | 0.91006 | Yes
Active | 2026W1-N11-WVM606 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93495 | 0.91166 | Yes
Active | 2026W1-N11-WVM607 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93391 | 0.91191 | Yes
Active | 2026W1-N11-WVM608 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93495 | 0.9127 | Yes
Active | 2026W1-N11-WVM609 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.93391 | 0.91288 | Yes
Active | 2026W1-N11-WVM610 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.94339 | 0.91843 | Yes
Active | 2026W1-N11-WVM611 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.94357 | 0.91859 | Yes
Active | 2026W1-N11-WVM612 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.94339 | 0.91956 | Yes
Active | 2026W1-N11-WVM613 | 271977 | MARSEILLE; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-2_345-L1223_TR-S_SRT-A | 0.93974 | 0.91962 | Yes
Active | 2026W1-N11-WVM614 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR81_LASCO_B-S_SRT-A | COMED_P1-3_TR83_DRESD_R-S_SRT-A | 0.94357 | 0.91972 | Yes
Active | 2026W1-N11-WVM615 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.9984 | 0.90496 | Yes
Active | 2026W1-N11-WVM616 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0045 | 0.91024 | Yes
Active | 2026W1-N11-WVM617 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0099 | 0.91297 | Yes
Active | 2026W1-N11-WVM618 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0042 | 0.91319 | Yes
Active | 2026W1-N11-WVM619 | 271910 | LASCOPMP ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0052 | 0.9198 | Yes
Active | 2026W1-N11-WVM620 | 271932 | LAS 0108 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-3_TR83_DRESD_R-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0052 | 0.91996 | Yes
Active | 2026W1-N11-WVM621 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0024 | 0.91311 | Yes
Active | 2026W1-N11-WVM622 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0085 | 0.91846 | Yes
Active | 2026W1-N11-WVM623 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | COMED_P1-2_138-L91907_-S_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0081 | 0.91962 | Yes
Active | 2026W1-N11-WVM624 | 271588 | GR 138 | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 0.99749 | 0.90734 | Yes
Active | 2026W1-N11-WVM625 | 271844 | KICKAPOO ; B | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0047 | 0.91383 | Yes
Active | 2026W1-N11-WVM626 | 271933 | LAS 6102 ; T | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0045 | 0.91667 | Yes
Active | 2026W1-N11-WVM627 | 271908 | LASCO STA; B | 138 | 222 | 0.92 | 1.05 | 274847 GRI_WTG 0.57 W1_SRT-A | COMED_P1-3_TR81_LASCO_B-S_SRT-A | 1.0112 | 0.91786 | Yes
Active | 2026W1-N11-WVM628 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P11_000840_SRT-A | 0.89961 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM629 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P11_000840_SRT-A | 0.89961 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM630 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_48_P11_000840_SRT-A | 0.89962 | 0.89137 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM631 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001449_SRT-A | 0.89961 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM632 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001449_SRT-A | 0.89961 | 0.89143 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM633 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001449_SRT-A | 0.89962 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM634 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001448_SRT-A | 0.89961 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM635 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001448_SRT-A | 0.89961 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM636 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | PL_40_P11_001448_SRT-A | 0.89962 | 0.89144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM637 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89961 | 0.89151 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM638 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89961 | 0.89151 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM639 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081_SRT-A | 208918 SUSQ 1 24.0 1 _SRT-A | 0.89962 | 0.89151 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM640 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P12_000189_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89543 | 0.89289 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM641 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89378 | 0.89041 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM642 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89378 | 0.89041 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM643 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89378 | 0.89041 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM644 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P12_101622A_SRT-A | 0.89545 | 0.8921 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM645 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_48_P11_000840_SRT-A | PL_08_P11_001446_SRT-A | 0.89545 | 0.89295 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM646 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.89385 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM647 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.89385 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM648 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.89385 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM649 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P12_101622A_SRT-A | 0.89552 | 0.89217 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM650 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | PL_08_P11_001446_SRT-A | 0.89552 | 0.89295 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM651 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001448_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89552 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM652 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89384 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM653 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89384 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM654 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89384 | 0.89048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM655 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | PL_08_P12_101622A_SRT-A | 0.89551 | 0.89217 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM656 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_40_P11_001449_SRT-A | 200038 SUSQ 2 24.0 2 _SRT-A | 0.89551 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM657 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89964 | 0.89288 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM658 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_48_P11_000840_SRT-A | 0.89964 | 0.89288 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM659 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89964 | 0.89293 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM660 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_48_P13_001557_SRT-A | PL_40_P11_001449_SRT-A | 0.89964 | 0.89294 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM661 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.89129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM662 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM663 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001449_SRT-A | 0.89993 | 0.8913 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM664 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | 200038 SUSQ 2 24.0 2 _SRT-A | PL_40_P11_001449_SRT-A | 0.90158 | 0.89298 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM665 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001447_SRT-A | 0.89404 | 0.89173 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM666 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001447_SRT-A | 0.89404 | 0.89173 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM667 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | 208918 SUSQ 1 24.0 1 _SRT-A | PL_08_P11_001447_SRT-A | 0.89404 | 0.89173 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM668 | 211946 | FLND DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.90251 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM669 | 211532 | FLND TP2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_000081A_SRT-A | PL_40_P11_001449_SRT-A | 0.90251 | 0.89299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM670 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.89837 | 0.89042 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM671 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.89837 | 0.89042 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM672 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.89837 | 0.89042 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM673 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.89837 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM674 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.89837 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM675 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.89837 | 0.89044 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM676 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.89837 | 0.8905 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM677 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.89837 | 0.8905 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM678 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.89837 | 0.8905 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM679 | 211962 | WHHA 1 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.89837 | 0.8905 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM680 | 211960 | WHHA 2 | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.89837 | 0.89051 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM681 | 210918 | WHHA DC | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.89837 | 0.89051 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM682 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P12_000189_SRT-A | 0.90003 | 0.89211 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM683 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_48_P11_000840_SRT-A | 0.90003 | 0.89213 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM684 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001448_SRT-A | 0.90003 | 0.89218 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM685 | 211533 | FLND | 69 | 229 | 0.893 | 1.019 | PL_08_P12_101622A_SRT-A | PL_40_P11_001449_SRT-A | 0.90003 | 0.89219 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Informational Only | N/A | 200680 | 26LAUREL L | 115 | 226 | 0.92 | 1.05 | PN_P1-2_PN-115-102T_B_SRT-A | Base Case | 1.0505 | - | No | To be addressed by Interregional process
Active | 2026W1-N11-WVM686 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5915_4306_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97619 | 0.87299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM687 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.96963 | 0.8096 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM688 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 0.96449 | 0.80952 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM689 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#16352_SRT-A | 0.96449 | 0.86222 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM690 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5915_4306_SRT-A | 0.96449 | 0.87299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM691 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16352_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97401 | 0.86156 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM692 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5915_4306_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97619 | 0.87299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM693 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#5919_6281_SRT-A | AEP_P1-2_#16351_SRT-A | 0.96963 | 0.8096 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM694 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5919_6281_SRT-A | 0.96448 | 0.80951 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM695 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#16352_SRT-A | 0.96448 | 0.86222 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM696 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5915_4306_SRT-A | 0.96448 | 0.87299 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVM697 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#16352_SRT-A | AEP_P1-2_#16351_SRT-A | 0.97401 | 0.86156 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## Volt Drop
PJM N-1-1 Voltage Drop Result (Winter 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | % Vdrop | Contingency 1 | Contingency 2 | BaseVolt | ContVolt | % Vdrop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2026W1-N11-WVD13 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0058 | 0.88245 | 12.34 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVD14 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0055 | 0.88266 | 12.288 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVD15 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | 1.0093 | 0.88558 | 12.373 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVD16 | 314621 | 3WEYRHAEUSER | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0078 | 0.88243 | 12.535 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVD17 | 314613 | 3TRWBRDG | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.0106 | 0.88264 | 12.794 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVD18 | 314614 | 3TRWBRDG2 | 115 | 345 | 10 | DVP_P1-3: 2-WDG 1 3TRWBRDG2_SRT-A | DVP_P1-3: 2-WDG 1 3TRWBRDG_SRT-A | 1.008 | 0.88555 | 12.25 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2026W1-N11-WVD19 | 314677 | 6BUCKING | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0009 | 0.8492 | 15.17 | Yes
Active | 2026W1-N11-WVD20 | 316322 | AB2-045 | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0009 | 0.84921 | 15.17 | Yes
Active | 2026W1-N11-WVD21 | 971844 | AH1-439_POI | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0006 | 0.8493 | 15.132 | Yes
Active | 2026W1-N11-WVD22 | 82745 | AH1-439_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0006 | 0.8493 | 15.132 | Yes
Active | 2026W1-N11-WVD23 | 314692 | 6FARMVIL | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99937 | 0.8497 | 14.967 | Yes
Active | 2026W1-N11-WVD24 | 972002 | AH1-546_POI | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.84974 | 15.734 | Yes
Active | 2026W1-N11-WVD25 | 82920 | AH1-546_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.84976 | 15.734 | Yes
Active | 2026W1-N11-WVD26 | 314691 | 3FARMVIL | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0012 | 0.85568 | 14.557 | Yes
Active | 2026W1-N11-WVD27 | 314719 | 3S CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.98537 | 0.85662 | 12.875 | Yes
Active | 2026W1-N11-WVD28 | 313127 | 3CURDSVILLE | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99897 | 0.85783 | 14.113 | Yes
Active | 2026W1-N11-WVD29 | 314726 | 3WILLIS | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99991 | 0.85897 | 14.094 | Yes
Active | 2026W1-N11-WVD30 | 315822 | AE2-259_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99992 | 0.85898 | 14.094 | Yes
Active | 2026W1-N11-WVD31 | 314664 | 3REDH DP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.9921 | 0.86447 | 12.763 | Yes
Active | 2026W1-N11-WVD32 | 314663 | 3REDH TP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99226 | 0.86465 | 12.761 | Yes
Active | 2026W1-N11-WVD33 | 314707 | 3MORAN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0018 | 0.86659 | 13.525 | Yes
Active | 2026W1-N11-WVD34 | 314521 | 3PAMPL_1 | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99532 | 0.86828 | 12.704 | Yes
Active | 2026W1-N11-WVD35 | 314713 | 3PAMPLIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99532 | 0.86828 | 12.704 | Yes
Active | 2026W1-N11-WVD36 | 314426 | 3FT PKET | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99956 | 0.87028 | 12.929 | Yes
Active | 2026W1-N11-WVD37 | 313156 | 3FT PIC DT T | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99957 | 0.87029 | 12.928 | Yes
Active | 2026W1-N11-WVD38 | 313755 | 3FLAT CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0048 | 0.87373 | 13.111 | Yes
Active | 2026W1-N11-WVD39 | 314429 | 3JTRSVLE | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0073 | 0.87891 | 12.837 | Yes
Active | 2026W1-N11-WVD40 | 314428 | 3HOOPERS | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.87893 | 12.814 | Yes
Active | 2026W1-N11-WVD41 | 314701 | 3LONEPN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0071 | 0.87902 | 12.804 | Yes
Active | 2026W1-N11-WVD42 | 314687 | 3CREWE | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.007 | 0.87917 | 12.786 | Yes
Active | 2026W1-N11-WVD43 | 314519 | 3LONEPINE_1 | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0076 | 0.87946 | 12.81 | Yes
Active | 2026W1-N11-WVD44 | 314715 | 3MADSONV | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 0.99895 | 0.87953 | 11.941 | Yes
Active | 2026W1-N11-WVD45 | 313853 | 3PONTONDP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0084 | 0.87999 | 12.839 | Yes
Active | 2026W1-N11-WVD46 | 313462 | 3AF1-294 | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0084 | 0.88002 | 12.838 | Yes
Active | 2026W1-N11-WVD47 | 319063 | AF1-294_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0085 | 0.88011 | 12.838 | Yes
Active | 2026W1-N11-WVD48 | 314432 | 3MARTIN DP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0073 | 0.88783 | 11.944 | Yes
Active | 2026W1-N11-WVD49 | 314706 | 3MARTIN TAP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0073 | 0.88788 | 11.944 | Yes
Active | 2026W1-N11-WVD50 | 970681 | AG2-440_POI | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0044 | 0.89693 | 10.749 | Yes
Active | 2026W1-N11-WVD51 | 81065 | AG2-440_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0045 | 0.89697 | 10.749 | Yes
Active | 2026W1-N11-WVD52 | 81080 | AG2-442_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0047 | 0.89715 | 10.751 | Yes
Active | 2026W1-N11-WVD53 | 313281 | 3VICTORIA DP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0076 | 0.89994 | 10.771 | Yes
Active | 2026W1-N11-WVD54 | 314725 | 3VICTORIA TP | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0077 | 0.90001 | 10.771 | Yes
Active | 2026W1-N11-WVD55 | 314723 | 3VICTRIA | 115 | 345 | 10 | DVP_P1-2: LN 9632_SRT-W | DVP_P1-2: LN 9646_SRT-W | 1.0079 | 0.90469 | 10.322 | Yes
Active | 2026W1-N11-WVD56 | 314677 | 6BUCKING | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0196 | 0.85015 | 16.946 | Yes
Active | 2026W1-N11-WVD57 | 316322 | AB2-045 | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0196 | 0.85015 | 16.946 | Yes
Active | 2026W1-N11-WVD58 | 971844 | AH1-439_POI | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0197 | 0.85025 | 16.943 | Yes
Active | 2026W1-N11-WVD59 | 82745 | AH1-439_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0197 | 0.85025 | 16.943 | Yes
Active | 2026W1-N11-WVD60 | 314692 | 6FARMVIL | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0199 | 0.85064 | 16.928 | Yes
Active | 2026W1-N11-WVD61 | 972002 | AH1-546_POI | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0203 | 0.85069 | 16.957 | Yes
Active | 2026W1-N11-WVD62 | 82920 | AH1-546_MAIN | 230 | 345 | 8 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0203 | 0.8507 | 16.957 | Yes
Active | 2026W1-N11-WVD63 | 314691 | 3FARMVIL | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0181 | 0.85654 | 16.154 | Yes
Active | 2026W1-N11-WVD64 | 314719 | 3S CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 0.99756 | 0.85742 | 14.013 | Yes
Active | 2026W1-N11-WVD65 | 313127 | 3CURDSVILLE | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.014 | 0.85868 | 15.532 | Yes
Active | 2026W1-N11-WVD66 | 314726 | 3WILLIS | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0149 | 0.8598 | 15.511 | Yes
Active | 2026W1-N11-WVD67 | 315822 | AE2-259_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0149 | 0.85981 | 15.511 | Yes
Active | 2026W1-N11-WVD68 | 314664 | 3REDH DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0042 | 0.86523 | 13.897 | Yes
Active | 2026W1-N11-WVD69 | 314663 | 3REDH TP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0044 | 0.8654 | 13.895 | Yes
Active | 2026W1-N11-WVD70 | 314707 | 3MORAN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0162 | 0.86737 | 14.881 | Yes
Active | 2026W1-N11-WVD71 | 314521 | 3PAMPL_1 | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0074 | 0.86901 | 13.835 | Yes
Active | 2026W1-N11-WVD72 | 314713 | 3PAMPLIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0074 | 0.86901 | 13.835 | Yes
Active | 2026W1-N11-WVD73 | 314426 | 3FT PKET | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0114 | 0.87098 | 14.046 | Yes
Active | 2026W1-N11-WVD74 | 313156 | 3FT PIC DT T | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0114 | 0.87099 | 14.046 | Yes
Active | 2026W1-N11-WVD75 | 313755 | 3FLAT CREEK | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0175 | 0.87444 | 14.31 | Yes
Active | 2026W1-N11-WVD76 | 314429 | 3JTRSVLE | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0191 | 0.87959 | 13.95 | Yes
Active | 2026W1-N11-WVD77 | 314428 | 3HOOPERS | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0189 | 0.87961 | 13.926 | Yes
Active | 2026W1-N11-WVD78 | 314701 | 3LONEPN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0188 | 0.87969 | 13.914 | Yes
Active | 2026W1-N11-WVD79 | 314687 | 3CREWE | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0188 | 0.87984 | 13.893 | Yes
Active | 2026W1-N11-WVD80 | 314519 | 3LONEPINE_1 | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0193 | 0.88013 | 13.921 | Yes
Active | 2026W1-N11-WVD81 | 314715 | 3MADSONV | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0098 | 0.88019 | 12.958 | Yes
Active | 2026W1-N11-WVD82 | 313853 | 3PONTONDP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0202 | 0.88067 | 13.952 | Yes
Active | 2026W1-N11-WVD83 | 313462 | 3AF1-294 | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0202 | 0.8807 | 13.951 | Yes
Active | 2026W1-N11-WVD84 | 319063 | AF1-294_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0203 | 0.88079 | 13.951 | Yes
Active | 2026W1-N11-WVD85 | 314432 | 3MARTIN DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0178 | 0.88842 | 12.943 | Yes
Active | 2026W1-N11-WVD86 | 314706 | 3MARTIN TAP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0179 | 0.88846 | 12.942 | Yes
Active | 2026W1-N11-WVD87 | 970681 | AG2-440_POI | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0135 | 0.89745 | 11.609 | Yes
Active | 2026W1-N11-WVD88 | 81065 | AG2-440_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0136 | 0.89749 | 11.609 | Yes
Active | 2026W1-N11-WVD89 | 81080 | AG2-442_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0138 | 0.89768 | 11.611 | Yes
Active | 2026W1-N11-WVD90 | 313281 | 3VICTORIA DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0168 | 0.90041 | 11.634 | Yes
Active | 2026W1-N11-WVD91 | 314725 | 3VICTORIA TP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0168 | 0.90048 | 11.633 | Yes
Active | 2026W1-N11-WVD92 | 314723 | 3VICTRIA | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0165 | 0.90512 | 11.135 | Yes
Active | 2026W1-N11-WVD93 | 313460 | 3BIRDSBRANCH | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0152 | 0.90848 | 10.674 | Yes
Active | 2026W1-N11-WVD94 | 319088 | AF2-222_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0152 | 0.90848 | 10.674 | Yes
Active | 2026W1-N11-WVD95 | 314710 | 3NUTBUSH | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0156 | 0.90943 | 10.618 | Yes
Active | 2026W1-N11-WVD96 | 314695 | 3GARY DP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0159 | 0.90961 | 10.628 | Yes
Active | 2026W1-N11-WVD97 | 971775 | AH1-396 GEN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0159 | 0.90961 | 10.628 | Yes
Active | 2026W1-N11-WVD98 | 314430 | 3KENBRDG | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.016 | 0.90974 | 10.627 | Yes
Active | 2026W1-N11-WVD99 | 970322 | AG2-213_POI | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0161 | 0.90982 | 10.626 | Yes
Active | 2026W1-N11-WVD100 | 314431 | 3KENB TP | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0161 | 0.90984 | 10.625 | Yes
Active | 2026W1-N11-WVD101 | 970256 | AG2-171_POI | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.016 | 0.90987 | 10.613 | Yes
Active | 2026W1-N11-WVD102 | 80369 | AG2-171_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.016 | 0.90987 | 10.613 | Yes
Active | 2026W1-N11-WVD103 | 80472 | AG2-213_MAIN | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0161 | 0.90987 | 10.627 | Yes
Active | 2026W1-N11-WVD104 | 314427 | 3LUNENBURG | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0161 | 0.91003 | 10.611 | Yes
Active | 2026W1-N11-WVD105 | 314722 | 3TWITTYS | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0153 | 0.91296 | 10.234 | Yes
Active | 2026W1-N11-WVD106 | 316034 | AC1-036 C | 115 | 345 | 10 | DVP_P1-2: LN 9646_SRT-W | DVP_P1-2: LN 9632_SRT-W | 1.0153 | 0.91296 | 10.234 | Yes

## Non-Convergence
PJM N-1-1 Non-Convergence Result (Winter Case)
FG # Status | FG # | Contingency 1 | Contingency 2 | Status | PJM Accepting Proposals | Reasons for Exclusions | Comment

## Load Drop
PJM N-1-1 Load Drop Result (Winter 2031 Case)
FG # Status | FG# | Contingency 1 | Contingency 2 | MW Drop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational-Only | N/A | DVP_P1-2: LN 201_SRT-A | DVP_P1-2: LN 2311_SRT-A | 442.24 | No | To be resolved through the supplemental M3 process
Informational-Only | N/A | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 201_SRT-A | 442.24 | No | To be resolved through the supplemental M3 process