## Tracking By Flowgate
2014 RTEP Proposal Window 1
Original Posting Date: 8/29/2014
Revised Posting Date:
Version: 1
Revision History:
V1: Tracking by Flowgate Spreadsheet Posted
Test | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency 1 | Contingency 2 (only applicable for N-1-1 test methodology) | STATUS | Project ID | Upgrade/Greenfield | Proposing Entity | Cost ($M) | Target Zone | Comment | Gen Retirements
N-1 Thermal | 99 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 103.52 | 111.13 | Tower | 'C5-TWL-NR054A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
N-1 Thermal | 100 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 103.52 | 111.13 | Line_FB | 'C2-BRK-NR125A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
N-1 Thermal | 101 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 100.85 | 106.57 | Line_FB | 'C2-BRK-NR127A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
N-1 Thermal | 124 | 250057 | 08M.FORT | 250131 | 08WILEY2 | 1 | 138/138 | 212/212 | 198 | 106.11 | 108.86 | Line_FB | 'C2 925_MIAMIFORT' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-1A | Upgrade | Duke Energy | 2 | DEO&K | ****
[16 empty] | P2014_1-1B | Greenfield | Duke Energy | 20 | DEO&K
[16 empty] | P2014_1-3H | Greenfield | Transource | 34.1 | DEO&K/AEP
[16 empty] | P2014_1-7A | Greenfield | PPL | 61.8 | AE
[16 empty] | P2014_1-7B | Greenfield | PPL | 73.2 | AE
[16 empty] | P2014_1-7C | Greenfield | PPL | 69.1 | AE
[16 empty] | P2014_1-7D | Greenfield | PPL | 128.6 | AE
[16 empty] | P2014_1-14F | Greenfield | Northeast Transmission Development | 32 | DEOK/Dayton
N-1 Thermal | 133 | 235428 | 01WINDSR | 243131 | 05TILTON | 1 | 138/138 | 201/205 | 205 | 105.22 | 107.53 | Single | 'BASE CASE' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | ****
[16 empty] | P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS
N-1 Thermal | 175 | 272378 | ROSCOE BE;BT | 271638 | HARLEM ; B | 1 | 138/138 | 222/222 | 175 | 104.29 | 102.59 | Single | '156-L15624__' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-6A | Upgrade | Comed | 4.6 | Comed | ****
[16 empty] | P2014_1-6B | Upgrade | Comed | 4.7 | Comed
N-1 Thermal | 195 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | 96.09 | 101.41 | Line_FB | 'BKR_73B' |  |  | P2014_1-3J | Greenfield | Transource | 30.8 | DLCO | ***
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-10A | Upgrade | Duquesne | 7.285 | Duquesne
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14A | Greenfield | Northeast Transmission Development | 50.1 | DLCO/APS/ATSI
N-1 Thermal | 196 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | 96.09 | 101.37 | Bus | 'BUS_11' |  |  | P2014_1-3J | Greenfield | Transource | 30.8 | DLCO | ***
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-10A | Upgrade | Duquesne | 7.285 | Duquesne
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14A | Greenfield | Northeast Transmission Development | 50.1 | DLCO/APS/ATSI
N-1 Thermal | 197 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | 96.09 | 101.37 | Line_FB | 'BKR_73C' |  |  | P2014_1-3J | Greenfield | Transource | 30.8 | DLCO | ***
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-10A | Upgrade | Duquesne | 7.285 | Duquesne
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14A | Greenfield | Northeast Transmission Development | 50.1 | DLCO/APS/ATSI
N-1 Thermal | 204 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | 99.47 | 101.11 | Tower | '4743' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | ****
[16 empty] | P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS
[16 empty] | P2014_1-7F | Greenfield | PPL | 98.1 | AEP/APS
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS
[16 empty] | P2014_1-14D | Greenfield | Northeast Transmission Development | 20.8 | AEP
[16 empty] | P2014_1-14G | Greenfield | Northeast Transmission Development | 12.8 | AEP/APS
N-1 Thermal | 205 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | 99.47 | 101.11 | Line_FB | '4743_C2_05TIDD 345-CC' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | ****
[16 empty] | P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS
[16 empty] | P2014_1-7F | Greenfield | PPL | 98.1 | AEP/APS
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS
[16 empty] | P2014_1-14D | Greenfield | Northeast Transmission Development | 20.8 | AEP
[16 empty] | P2014_1-14G | Greenfield | Northeast Transmission Development | 12.8 | AEP/APS
N-1 Thermal | 222 | 221231 | RIV982-2 | 221147 | RIVERSDE | 1 | 115/115 | 232/232 | 437 | 98.76 | 100.46 | Line_FB | 'BRDNSHR_5T' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-8A | Upgrade | BGE | 1.14 | BGE | *
[16 empty] | P2014_1-8B | Upgrade | BGE | 2.6 | BGE
[16 empty] | P2014_1-8C | Upgrade | BGE | 3.74 | BGE
N-1 Thermal | 366 | 314211 | 3ACCA | 313832 | 3HERM159 | 1 | 115/115 | 345/345 | 180 | 94.5 | 97.49 | Single | 'LN 20' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-4A | Upgrade | Dominion Virginia Power | 1.82 | Dominion Virginia Power | ****
N-1 Thermal | 429 | 314234 | 3NRTHEST | 314213 | 3CARVER | 1 | 115/115 | 345/345 | 159 | 95.22 | 96.4 | Single | 'LN 20' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-4B | Upgrade | Dominion Virginia Power | 0.04 | Dominion Virginia Power | ****
Gen Deliv/Common Mode Outage | 81 | 227905 | SCULL#1 | 227903 | MILL #1 | 1 | 138/138 | 234/234 | 262 | 121.7 | 123.69 | single | 'BLE-SC-ML2' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 83 | 227905 | SCULL#1 | 227903 | MILL #1 | 1 | 138/138 | 234/234 | 262 | 119.38 | 121.31 | single | 'BLE-ML-LEW2' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 87 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | 126.99 | 121.43 | single | 'BLE-SC-ML1' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 88 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | 125.85 | 120.24 | single | 'BLE-ML-LEW1' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 91 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 219 | 110.28 | 108.86 | single | Base Case |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 105 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 112.44 | 113.88 | single | '5296_B2_TOR97B_MOAB' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 106 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 111.72 | 113.3 | single | '5294_B2_TOR97_WOMOAB' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 108 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 108.35 | 110.25 | single | '1375_B3' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 110 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 108.06 | 109.71 | single | '5295_B2_TOR97A_MOAB' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 116 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | 111.88 | 115.45 | single | 'BLE-SC-ML1' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 117 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | 110.74 | 114.25 | single | 'BLE-ML-LEW1' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 120 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 219 | 101.29 | 100.53 | single | Base Case |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 132 | 228110 | BLE | 227905 | SCULL#1 | 1 | 138/138 | 234/234 | 307 | 118.91 | 114.22 | single | 'BLE-SC-ML2' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 134 | 228110 | BLE | 227905 | SCULL#1 | 1 | 138/138 | 234/234 | 307 | 116.93 | 112.18 | single | 'BLE-ML-LEW2' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 164 | 248005 | 06KYGER | 242528 | 05SPORN | 2 | 345/345 | 206/205 | 971 | 101.98 | 102.01 | single | '349_B2_TOR21' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of Tanner Creek Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 165 | 248005 | 06KYGER | 242528 | 05SPORN | 2 | 345/345 | 206/205 | 971 | 101.09 | 101.28 | single | '6190_B3_05SPORN 345-4_WOMOAB' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of Tanner Creek Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 170 | 213489 | CHICHST1 | 213588 | EDDYSTN4 | 1 | 230/230 | 230/230 | 863 | 107.53 | 107.09 | single | '220-04/* $ DELCO $ 220-04 $ L' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-5A | Upgrade | PECO | 0.4 | PECO | *
[16 empty] | P2014_1-5B | Upgrade | PECO | 2.2 | PECO
[16 empty] | P2014_1-14B | Greenfield | Northeast Transmission Development | 22.7 | PECO
Gen Deliv/Common Mode Outage | 171 | 213489 | CHICHST1 | 213588 | EDDYSTN4 | 1 | 230/230 | 230/230 | 863 | 104.79 | 104.42 | single | '220-67/* $ DELCO $ 220-67 $ L' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-5A | Upgrade | PECO | 0.4 | PECO | *
[16 empty] | P2014_1-5B | Upgrade | PECO | 2.2 | PECO
[16 empty] | P2014_1-14B | Greenfield | Northeast Transmission Development | 22.7 | PECO
Gen Deliv/Common Mode Outage | 190 | 272378 | ROSCOE BE;BT | 271638 | HARLEM ; B | 1 | 138/138 | 222/222 | 175 | 105.11 | 103.41 | single | '156-L15624__' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-6A | Upgrade | Comed | 4.6 | Comed | ****
[16 empty] | P2014_1-6B | Upgrade | Comed | 4.7 | Comed
Gen Deliv/Common Mode Outage | 192 | 242605 | 05CLNCHR | 242606 | 05CLNLFD | 1 | 138/138 | 205/205 | 223 | 108.29 | 108.39 | single | Base Case |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 209 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 296 | 107.1 | 106.65 | single | Base Case |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 211 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | 101.41 | 101.21 | single | '5296_B2_TOR97B_MOAB' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 212 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | 100.81 | 100.73 | single | '5294_B2_TOR97_WOMOAB' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 219 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | 106.75 | 106.61 | single | '6174_B2_TOR98A_MOAB' |  | Defer action Pending Retirement | [5 empty] | *** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 220 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | 106.57 | 106.46 | single | '6173_B2_TOR98_WOMOAB' |  | Defer action Pending Retirement | [5 empty] | *** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 221 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | 105.85 | 105.83 | single | '6175_B2_TOR98B_MOAB' |  | Defer action Pending Retirement | [5 empty] | *** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 222 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | 104.78 | 105.01 | single | '6176_B2_TOR98C_MOAB' |  | Defer action Pending Retirement | [5 empty] | *** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 232 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 205 | 103.66 | 105.9 | single | Base Case |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | ****
[16 empty] | P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS
[16 empty] | P2014_1-7F | Greenfield | PPL | 98.1 | AEP/APS
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS
[16 empty] | P2014_1-14D | Greenfield | Northeast Transmission Development | 20.8 | AEP
[16 empty] | P2014_1-14G | Greenfield | Northeast Transmission Development | 12.8 | AEP/APS
Gen Deliv/Common Mode Outage | 234 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | 100.67 | 101.85 | single | '8319_B2_TOR587B' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | ****
[16 empty] | P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS
[16 empty] | P2014_1-7F | Greenfield | PPL | 98.1 | AEP/APS
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS
[16 empty] | P2014_1-14D | Greenfield | Northeast Transmission Development | 20.8 | AEP
[16 empty] | P2014_1-14G | Greenfield | Northeast Transmission Development | 12.8 | AEP/APS
Gen Deliv/Common Mode Outage | 273 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | 103.57 | 104.41 | single | '6174_B2_TOR98A_MOAB' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 274 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | 103.39 | 104.26 | single | '6173_B2_TOR98_WOMOAB' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 275 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | 102.67 | 103.63 | single | '6175_B2_TOR98B_MOAB' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 276 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | 101.59 | 102.81 | single | '6176_B2_TOR98C_MOAB' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 289 | 314211 | 3ACCA | 313832 | 3HERM159 | 1 | 115/115 | 345/345 | 169.2 | 100.59 | 103.72 | single | 'LN 20' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-4A | Upgrade | Dominion Virginia Power | 1.82 | Dominion Virginia Power | ****
Gen Deliv/Common Mode Outage | 301 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 296 | 103.18 | 103.27 | single | Base Case |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 315 | 213844 | NOTTNGHM | 213553 | DALEVLLE | 1 | 230/230 | 230/230 | 519 | 103.67 | 102.7 | single | 'CKT 22088' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-5C | Upgrade | PECO | 0.1 | PECO | *
[16 empty] | P2014_1-5D | Upgrade | PECO | 26.5 | PECO
[16 empty] | P2014_1-11D | Greenfield | ITC | 27.1 | PECO/DPL
Gen Deliv/Common Mode Outage | 320 | 314234 | 3NRTHEST | 314213 | 3CARVER | 1 | 115/115 | 345/345 | 149.46 | 101.04 | 102.31 | single | 'LN 20' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-4B | Upgrade | Dominion Virginia Power | 0.04 | Dominion Virginia Power | ****
Gen Deliv/Common Mode Outage | 358 | 243026 | 05KAMMR1 | 243143 | 05WBELLA | 1 | 138/138 | 205/205 | 296 | 100.7 | 100.1 | single | '53_B2_TOR587A' |  | Defer action Pending Retirement | [5 empty] | *** | Overload as a result of Kammer Reitred generators
Gen Deliv/Common Mode Outage | 719 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | 95.9 | 101.16 | bus | 'BUS_11' |  |  | P2014_1-3J | Greenfield | Transource | 30.8 | DLCO | **
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-10A | Upgrade | Duquesne | 7.285 | Duquesne
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14A | Greenfield | Northeast Transmission Development | 50.1 | DLCO/APS/ATSI
Gen Deliv/Common Mode Outage | 720 | 239070 | 02RICHLD | 238521 | 02NAOMI | 1 | 138/138 | 202/202 | 194 | 100.79 | 101.15 | bus | 'C1-BUS-WR002B' |  |  | P2014_1-3D | Greenfield | Transource | 19 | AEP/ATSI | ****
[16 empty] | P2014_1-3E | Greenfield | Transource | 10.2 | AEP/ATSI
[16 empty] | P2014_1-7H | Greenfield | PPL | 66.1 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9H | Upgrade | First Energy | 0.02 | ATSI
Gen Deliv/Common Mode Outage | 754 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 164.06 | 171.62 | tower | 'C5-TWL-NR054A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
Gen Deliv/Common Mode Outage | 763 | 228110 | BLE | 228111 | MDLE TP | 1 | 138/138 | 234/234 | 286 | 105.3803 | 102.4323 | tower | 'AE7TOWER' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 773 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 117.1 | 118.58 | tower | '8345' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 774 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 116.02 | 117.4 | tower | '8634' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 775 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 109.9 | 111.25 | tower | '8344' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 790 | 239030 | 02OTTAWA | 238874 | 02LAKVEW | 1 | 138/138 | 202/202 | 375 | 110.21 | 112.36 | tower | 'C5-TWL-CR040A' |  |  | P2014_1-3F | Greenfield | Transource | 64.9 | AEP/ATSI | ****
[16 empty] | P2014_1-3G | Greenfield | Transource | 67.3 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9G | Upgrade | First Energy | 7.4 | ATSI
[16 empty] | P2014_1-11B | Greenfield | ITC | 107 | ATSI/AEP
[16 empty] | P2014_1-11C | Greenfield | ITC | 97.4 | ATSI/AEP
Gen Deliv/Common Mode Outage | 794 | 242605 | 05CLNCHR | 242606 | 05CLNLFD | 1 | 138/138 | 205/205 | 310 | 110.91 | 111.8 | tower | '8634' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2D | Upgrade | AEP | 1.1 | AEP | ****
[16 empty] | P2014_1-2E | Upgrade | AEP | 2 | AEP
[16 empty] | P2014_1-2F | Upgrade | AEP | 8 | AEP
[16 empty] | P2014_1-7E | Greenfield | PPL | 82.5 | AEP
[16 empty] | P2014_1-11A | Greenfield | ITC | 207.9 | AEP
[16 empty] | P2014_1-14H | Greenfield | Northeast Transmission Development | 46 | AEP
[16 empty] | P2014_1-14H | Greenfield | Northeast Transmission Development | 53.8 | AEP
Gen Deliv/Common Mode Outage | 795 | 242605 | 05CLNCHR | 242606 | 05CLNLFD | 1 | 138/138 | 205/205 | 310 | 107.13 | 107.84 | tower | '8345' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 797 | 208040 | MONT | 208034 | MILT | 1 | 230/230 | 229/229 | 802 | 111.21 | 108.98 | tower | 'PL100484' |  | Analysis Still Underway | P2014_1-3I | Greenfield | Transource | 146.4 | PPL | ****
[16 empty] | P2014_1-4C | Greenfield | Dominion Virginia Power | 31.8 | PPL
[16 empty] | P2014_1-7I | Upgrade | PPL | 139.2 | PPL
[16 empty] | P2014_1-7J | Upgrade | PPL | 29.2 | PPL
[16 empty] | P2014_1-7K | Greenfield | PPL | 114.1 | PPL
[16 empty] | P2014_1-7L | Greenfield | PPL | 87.1 | PPL
[16 empty] | P2014_1-7M | Greenfield | PPL | 102.9 | PPL
[16 empty] | P2014_1-7N | Greenfield | PPL | 112.5 | PPL
[16 empty] | P2014_1-7O | Greenfield | PPL | 164.2 | PPL
[16 empty] | P2014_1-7P | Greenfield | PPL | 1367 | PPL/Penelec
[16 empty] | P2014_1-13B | Greenfield | NextEra Energy Transmission LLC | 55.36 | PPL
[16 empty] | P2014_1-14E | Greenfield | Northeast Transmission Development | 49.8 | PPL
[16 empty] | P2014_1-14E1 | Greenfield | Northeast Transmission Development | 80.9 | PPL
Gen Deliv/Common Mode Outage | 799 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | 107.08 | 108.67 | tower | '4743' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | ****
[16 empty] | P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS
[16 empty] | P2014_1-7F | Greenfield | PPL | 98.1 | AEP/APS
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS
[16 empty] | P2014_1-14D | Greenfield | Northeast Transmission Development | 20.8 | AEP
[16 empty] | P2014_1-14G | Greenfield | Northeast Transmission Development | 12.8 | AEP/APS
Gen Deliv/Common Mode Outage | 801 | 208034 | MILT | 208109 | SUNB | 1 | 230/230 | 229/229 | 730.61 | 108.74 | 107.6 | tower | 'PL100484' |  | Analysis Still Underway | P2014_1-3I | Greenfield | Transource | 146.4 | PPL | ****
[16 empty] | P2014_1-4C | Greenfield | Dominion Virginia Power | 31.8 | PPL
[16 empty] | P2014_1-7I | Upgrade | PPL | 139.2 | PPL
[16 empty] | P2014_1-7J | Upgrade | PPL | 29.2 | PPL
[16 empty] | P2014_1-7K | Greenfield | PPL | 114.1 | PPL
[16 empty] | P2014_1-7L | Greenfield | PPL | 87.1 | PPL
[16 empty] | P2014_1-7M | Greenfield | PPL | 102.9 | PPL
[16 empty] | P2014_1-7N | Greenfield | PPL | 112.5 | PPL
[16 empty] | P2014_1-7O | Greenfield | PPL | 164.2 | PPL
[16 empty] | P2014_1-7P | Greenfield | PPL | 1367 | PPL/Penelec
[16 empty] | P2014_1-13B | Greenfield | NextEra Energy Transmission LLC | 55.36 | PPL
[16 empty] | P2014_1-14E | Greenfield | Northeast Transmission Development | 49.8 | PPL
[16 empty] | P2014_1-14E1 | Greenfield | Northeast Transmission Development | 80.9 | PPL
Gen Deliv/Common Mode Outage | 802 | 238874 | 02LAKVEW | 238768 | 02GRNFLD | 1 | 138/138 | 202/202 | 316 | 105.75 | 106.95 | tower | 'C5-TWL-CR040A' |  |  | P2014_1-3F | Greenfield | Transource | 64.9 | AEP/ATSI | *
[16 empty] | P2014_1-3G | Greenfield | Transource | 67.3 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9G | Upgrade | First Energy | 7.4 | ATSI
[16 empty] | P2014_1-11B | Greenfield | ITC | 107 | ATSI/AEP
[16 empty] | P2014_1-11C | Greenfield | ITC | 97.4 | ATSI/AEP
Gen Deliv/Common Mode Outage | 804 | 231215 | SILVERSD | 231205 | DARLEY | 1 | 69/69 | 235/235 | 123 | 127.65 | 123.78 | tower | 'DBL_5NC' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-12K | Upgrade | PHI | 0.04 | DP&L | ****
Gen Deliv/Common Mode Outage | 807 | 228401 | MCKLTON | 228402 | MONROE | 2 | 230/230 | 234/234 | 478 | 105.37 | 105.37 | tower | 'V2274+P2242_LT' |  | Defer action Pending ISA | [5 empty] | **** | Overload as a result of queued FSA generator
Gen Deliv/Common Mode Outage | 812 | 228401 | MCKLTON | 228402 | MONROE | 1 | 230/230 | 234/234 | 478 | 105.37 | 105.37 | tower | 'V2274+P2242_LT' |  | Defer action Pending ISA | [5 empty] | **** | Overload as a result of queued FSA generator
Gen Deliv/Common Mode Outage | 822 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | 105.31 | 105.13 | tower | '8345' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 823 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | 104.4 | 104.14 | tower | '8634' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 828 | 243026 | 05KAMMR1 | 243143 | 05WBELLA | 1 | 138/138 | 205/205 | 296 | 104.35 | 103.33 | tower | '476' |  | Defer action Pending Retirement | [5 empty] | *** | Overload as a result of Kammer Reitred generators
Gen Deliv/Common Mode Outage | 831 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 384 | 102.29 | 102.52 | tower | '8345' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 832 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 384 | 101.36 | 101.52 | tower | '8634' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 843 | 206322 | 28PARLIN | 206298 | 28WILLIAMS | 1 | 230/230 | 228/228 | 813 | 101.83 | 101.1 | tower | '1LINE+2LINE' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9D | Upgrade | First Energy | 0.6 | JCPL | *
Gen Deliv/Common Mode Outage | 844 | 206322 | 28PARLIN | 206298 | 28WILLIAMS | 1 | 230/230 | 228/228 | 813 | 101.83 | 101.1 | tower | '37PS_B' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9D | Upgrade | First Energy | 0.6 | JCPL | *
Gen Deliv/Common Mode Outage | 846 | 206298 | 28WILLIAMS | 206292 | 28FRENEAU | 1 | 230/230 | 228/228 | 813 | 101.21 | 100.49 | tower | '1LINE+2LINE' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9D | Upgrade | First Energy | 0.6 | JCPL | *
Gen Deliv/Common Mode Outage | 847 | 206298 | 28WILLIAMS | 206292 | 28FRENEAU | 1 | 230/230 | 228/228 | 813 | 101.2 | 100.49 | tower | '37PS_B' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9D | Upgrade | First Energy | 0.6 | JCPL | *
Gen Deliv/Common Mode Outage | 918 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 164.06 | 171.62 | breaker | 'C2-BRK-NR125A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
Gen Deliv/Common Mode Outage | 919 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 116.16 | 121.31 | breaker | 'C2-BRK-NR04A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
Gen Deliv/Common Mode Outage | 920 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 111.95 | 117.69 | breaker | 'C2-BRK-NR127A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
Gen Deliv/Common Mode Outage | 921 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | 97.05 | 103.23 | breaker | 'C2-BRK-NR126A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | ****
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
Gen Deliv/Common Mode Outage | 943 | 227905 | SCULL#1 | 227903 | MILL #1 | 1 | 138/138 | 234/234 | 262 | 134.54 | 131.85 | breaker | 'AE24' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 951 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | 129.3 | 127.05 | breaker | 'AE23' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 952 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | 112.52 | 112.49 | breaker | 'AE28' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 964 | 227903 | MILL #1 | 227902 | LEWIS #1 | 1 | 138/138 | 234/234 | 262 | 107.8738 | 105.7504 | breaker | 'AE24' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 965 | 200706 | 26N.MESHPN | 200708 | 26OXBOW | 1 | 230/230 | 226/226 | 617 | 123.36 | 123.36 | breaker | 'PL100926' |  |  | P2014_1-7P | Greenfield | PPL | 1367 | PPL/Penelec | ****
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9A | Upgrade | First Energy | 26.5 | PPL/Penelec
[16 empty] | P2014_1-9B | Upgrade | First Energy | 73.4 | PPL/Penelec
[16 empty] | P2014_1-13A | Greenfield | NextEra Energy Transmission LLC | 68.81 | PPL/Penelec
Gen Deliv/Common Mode Outage | 971 | 200708 | 26OXBOW | 208009 | LACK | 1 | 230/230 | 226/229 | 624 | 121.64 | 121.64 | breaker | 'PL100926' |  |  | P2014_1-7P | Greenfield | PPL | 1367 | PPL/Penelec | ****
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9A | Upgrade | First Energy | 26.5 | PPL/Penelec
[16 empty] | P2014_1-9B | Upgrade | First Energy | 73.4 | PPL/Penelec
[16 empty] | P2014_1-13A | Greenfield | NextEra Energy Transmission LLC | 68.81 | PPL/Penelec
Gen Deliv/Common Mode Outage | 976 | 228110 | BLE | 227905 | SCULL#1 | 1 | 138/138 | 234/234 | 307 | 123.71 | 121.19 | breaker | 'AE24' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 977 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | 122.88 | 121.07 | breaker | 'AE23' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 978 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | 106.07 | 106.54 | breaker | 'AE28' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 988 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | 114.08 | 115.8 | breaker | '1528_C2' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 993 | 270717 | DRESDEN ; R | 275180 | DRESDEN ;3M | 1 | 345/138 | 222/222 | 530 | 112.76 | 115.29 | breaker | '900-45-BT4-5__' |  |  | P2014_1-3K | Greenfield | Transource | 71 | Comed | **
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-6C | Upgrade | Comed | 2.6 | Comed
Gen Deliv/Common Mode Outage | 1037 | 250057 | 08M.FORT | 250131 | 08WILEY2 | 1 | 138/138 | 212/212 | 198 | 106.54 | 109.22 | breaker | 'C2 925_MIAMIFORT' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-1A | Upgrade | Duke Energy | 2 | DEO&K | ****
[16 empty] | P2014_1-1B | Greenfield | Duke Energy | 20 | DEO&K
[16 empty] | P2014_1-3H | Greenfield | Transource | 34.1 | DEO&K/AEP
[16 empty] | P2014_1-14F | Greenfield | Northeast Transmission Development | 32 | DEOK/Dayton
Gen Deliv/Common Mode Outage | 1042 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | 107.08 | 108.67 | breaker | '4743_C2_05TIDD 345-CC' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | ****
[16 empty] | P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS
[16 empty] | P2014_1-7F | Greenfield | PPL | 98.1 | AEP/APS
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS
[16 empty] | P2014_1-14D | Greenfield | Northeast Transmission Development | 20.8 | AEP
[16 empty] | P2014_1-14G | Greenfield | Northeast Transmission Development | 12.8 | AEP/APS
Gen Deliv/Common Mode Outage | 1057 | 238551 | 02AVON | 238552 | 02AVON | 92 | 345/138 | 202/202 | 602 | 105.84 | 106.51 | breaker | 'C2-BRK-NR127A' |  |  | P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | **
[16 empty] | P2014_1-3C | Greenfield | Transource | 52.4 | ATSI
[16 empty] | P2014_1-7G | Greenfield | PPL | 279.5 | ATSI
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9E | Upgrade | First Energy | 5.4 | ATSI
[16 empty] | P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI
Gen Deliv/Common Mode Outage | 1085 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | 102.78 | 102.82 | breaker | '1528_C2' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | 1099 | 221231 | RIV982-2 | 221147 | RIVERSDE | 1 | 115/115 | 232/232 | 437 | 99.67 | 101.43 | breaker | 'BRDNSHR_5T' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-8A | Upgrade | BGE | 1.14 | BGE | *
[16 empty] | P2014_1-8B | Upgrade | BGE | 2.6 | BGE
[16 empty] | P2014_1-8C | Upgrade | BGE | 3.74 | BGE
Gen Deliv/Common Mode Outage | 1102 | 219110 | GLOUCSTR_2 | 219755 | CUTHBERT_4 | 2 | 230/230 | 231/231 | 711 | 102.19 | 101.41 | breaker | 'BF_GLOU_1-8_LT' |  | Defer action Pending Retirement | [5 empty] | **** | Overload as a result of BL England Generators
Gen Deliv/Common Mode Outage | 1108 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | 95.9 | 101.21 | breaker | 'BKR_73B' |  |  | P2014_1-3J | Greenfield | Transource | 30.8 | DLCO | **
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-10A | Upgrade | Duquesne | 7.285 | Duquesne
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14A | Greenfield | Northeast Transmission Development | 50.1 | DLCO/APS/ATSI
Gen Deliv/Common Mode Outage | 1109 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | 95.9 | 101.16 | breaker | 'BKR_73C' |  |  | P2014_1-3J | Greenfield | Transource | 30.8 | DLCO | **
[15 empty] | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-10A | Upgrade | Duquesne | 7.285 | Duquesne
[16 empty] | P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS
[16 empty] | P2014_1-14A | Greenfield | Northeast Transmission Development | 50.1 | DLCO/APS/ATSI
Gen Deliv/Common Mode Outage | 1128 | 206322 | 28PARLIN | 206298 | 28WILLIAMS | 1 | 230/230 | 228/228 | 813 | 100.64 | 100.53 | breaker | 'C2_CNJ2-SB-#36A' |  | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9D | Upgrade | First Energy | 0.6 | JCPL | *
Gen Deliv/Common Mode Outage | 1132 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 384 | 99.74 | 100.2 | breaker | '1528_C2' |  | Defer action Pending Retirement | [5 empty] | * | Overload as a result of the Clinch River Retired generator (6/1/2015)
Gen Deliv/Common Mode Outage | new1 | 228113 | MIDDLE#1 | 228122 | MIDDLE#1 | 1 | 138/69 | 234/234 | 193 | 247.82 | 128.41 | breaker | 'AE12' |  | Analysis Still Underway | P2014_1-12J | Upgrade | PHI | 7.98 | AE | ** | On July 21th, 2014, FG#new1 was added to the violation list as a result of updated contingency definition for AE12. (Updated as part of V4)
N-1-1 Thermal | 1.1 | 204540 | 27JACKSON | 204548 | 27N.HANOVR | 1 | 115/115 | 227/227 | 131 | 101.37 | 104.38 | N-1-1 | 'B_ME115-SX-#24' | 'B_ME115-SX-#21' | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9C | Upgrade | First Energy | 0.1 | Meted | *
N-1-1 Thermal | 1.2 | 204540 | 27JACKSON | 204548 | 27N.HANOVR | 1 | 115/115 | 227/227 | 131 | 102.44 | 104.38 | N-1-1 | 'B_ME115-SX-#21' | 'B_ME115-SX-#24' | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-9C | Upgrade | First Energy | 0.1 | Meted | *
N-1-1 Thermal | 2.3 | 213571 | EDDYREA1 | 213759 | LLAN13 | 1 | 138/138 | 230/230 | 311 | 99.16 | 104.34 | N-1-1 | '130-35/* $ DELCO $ 130-35 $ L' | '130-42/* $ DELCO $ 130-42 $ L' | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-5E | Upgrade | PECO | 0.1 | PECO | *
[16 empty] | P2014_1-5F | Upgrade | PECO | 38.4 | PECO
[16 empty] | P2014_1-14B | Greenfield | Northeast Transmission Development | 22.7 | PECO
N-1-1 Thermal | 1.4 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | 116.84 | 121.57 | N-1-1 | 138-L15623_R-R | 138-L15624_B-R | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-6A | Upgrade | Comed | 4.6 | Comed | ****
[16 empty] | P2014_1-6B | Upgrade | Comed | 4.7 | Comed
N-1-1 Thermal | 1.5 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | 113.64 | 114.37 | N-1-1 | 138-L15624_B-R | 138-L15625_B-R | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-6A | Upgrade | Comed | 4.6 | Comed | ****
[16 empty] | P2014_1-6B | Upgrade | Comed | 4.7 | Comed
N-1-1 Thermal | 2.6 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | 114.24 | 108.5 | N-1-1 | 138-L15624_B-R | 138-L15623_R-R | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-6A | Upgrade | Comed | 4.6 | Comed | ****
[16 empty] | P2014_1-6B | Upgrade | Comed | 4.7 | Comed
N-1-1 Thermal | 1.7 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | 121.18 | 119.5 | N-1-1 | 138-L15625_B-R | 138-L15624_B-R | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-6A | Upgrade | Comed | 4.6 | Comed | ****
[16 empty] | P2014_1-6B | Upgrade | Comed | 4.7 | Comed
N-1-1 Thermal | 1.8 | 221011 | NWEST2 | 221061 | N.WEST | Z | 115/115 | 232/232 | 350 | 107.3 | 107.9 | N-1-1 | 'NWEST_230-2' | NWEST_230-3' | Preliminary Recomendation of this project at 9/2/2014 TEAC | P2014_1-8D | Upgrade | BGE | 1.2 | BGE | *
[16 empty] | P2014_1-8E | Upgrade | BGE | 2.5 | BGE
Note on V34: Author: