## Tracking
PJM 2014 RTEP Proposal Window #1 Tracking Spreadsheet
Proposal Window: | 2014 RTEP Proposal Window 1
Window Opening Date: | 2014-06-27
Window Closing Date: | 2014-07-28
Current Spreadsheet Version | V3 - 8/29/2014 |  |  |  |  | * Flowgate #'s correspond to detail in Flowgates from Results sheet
Project ID | Upgrade/Greenfield | Proposing Entity | Proposed Cost ($M) | Target Zone | Reliability Criteria Violation Test Procedure Type | Reliability Criteria Violation* Test Procedure Flowgate # | Major Components
P2014_1-1A | Upgrade | Duke Energy | 2 | DEO&K | Baseline Thermal; Gen Deliv | 124; 1037 | Add two breakers at Miami Fort 138 kV
P2014_1-1B | Greenfield | Duke Energy | 20 | DEO&K | Baseline Thermal; Gen Deliv | 124; 1037 | New 138 kV line from Miami Fort to Wiley
P2014_1-2A | Upgrade | AEP | 2 | AEP/APS | Baseline Thermal; Gen Deliv | 133; 204, 205, 232, 234, 799, 1042 | Reconductor .5 miles of Tiltonsville-Windsor 138 kVand string the vacant side of the 4.5 mile section using 556 ACSR in a six wire configuration
P2014_1-2C | Upgrade | AEP | 0.6 | AEP | Gen Deliv | 358, 828 | Perform remediation work to improve the rating of Kammer to West Bellaire
P2014_1-2D | Upgrade | AEP | 1.1 | AEP | Gen Deliv | 794 | Install two 138 kV prop structures to increase the Maximum Operating Temperature of the Clinch River – Clinchfield 138 kV line.
P2014_1-2E | Upgrade | AEP | 2 | AEP | Gen Deliv | 105, 106, 108, 110, 192, 209, 211, 212, 219, 220, 221, 222, 273, 274, 275, 276, 301, 773, 774, 775, 794, 795, 822, 823, 831, 832, 988, 1085, 1132 | Install two 138 kV prop structures to increase the Maximum Operating Temperature of the Clinch River – Clinchfield 138 kV line. Additionally upgrade ACSR Entrance/Exit spans, MOAB's, and MCMs at Clinch River, Lebanon, Elk Garden, Saltville, and Fletchers Ridge.
P2014_1-2F | Upgrade | AEP | 8 | AEP | Gen Deliv | 105, 106, 108, 110, 192, 209, 211, 212, 219, 220, 221, 222, 273, 274, 275, 276, 301, 773, 774, 775, 794, 795, 822, 823, 831, 832, 988, 1085, 1132 | Rebuild 5.09 miles of Clinch River – Clinchfield 138 kV line. Additionally upgrade ACSR Entrance/Exit spans, MOAB's, and MCMs at Clinch River, Lebanon, Elk Garden, Saltville, and Fletchers Ridge.
P2014_1-2G | Greenfield | AEP | 38.5 | AEP | Gen Deliv | 105, 106, 108, 110, 192, 209, 211, 212, 219, 220, 221, 222, 273, 274, 275, 276, 301, 773, 774, 775, 822, 823, 831, 832, 988, 1085, 1132 | Construct a ~22 mile of new 138 kV line between Clinch River and Keen Mountain
P2014_1-2H | Greenfield | AEP | 95 | AEP | Gen Deliv | 105, 106, 108, 110, 192, 209, 211, 212, 219, 220, 221, 222, 273, 274, 275, 276, 301, 773, 774, 775, 822, 823, 831, 832, 988, 1085, 1132 | Construct a ~43 mile of new 138 kV line between Clinch River and new Beaver Creek station.
P2014_1-2I | Upgrade | AEP | 15.5 | AEP/OVEC | Gen Deliv | 164, 165 | Reconductor Kyger Creek-Sporn 345 kV CKT 2
P2014_1-2J | Upgrade | AEP | 21.3 | AEP/OVEC | Gen Deliv | 164, 165 | Reconductor both Kyger Creek-Sporn 345 kV CKTS 1 and 2
P2014_1-2K | Upgrade | AEP | 0.3 | AEP/OVEC | Gen Deliv | 164, 165 | Configure both Kyger Creek-Sporn 345 kV CKTS 1 and 2 in a six wired arrangement
P2014_1-2L | Greenfield | AEP | 17.7 | AEP/OVEC | Gen Deliv | 164, 165 | Construct a ~3.2 mile of new 345 kV line between OVEC's Kyger Creek and AEP's Gavin stations, and install a 345/138kV transformer at Gavin.
P2014_1-3A | Greenfield | Transource | 14.6 | AEP/APS | Baseline Thermal; Gen Deliv | 133; 204, 205 232, 234, 799, 1042, 358, 828 | Construct a new 138 kV switchyard at the intersection of the AEP Tidd-Fort Henry 138 kV line and the Allegheny Power Windsor-Dutch Fork 138 kV line.
P2014_1-3B | Greenfield | Transource | 38.3 | ATSI | Baseline Thermal; Gen Deliv | 99, 100, 101; 754, 918, 919, 920, 921, 1057 | Construct approximately 6 miles of new, double circuit 345 kV line to connect the FirstEnergy proposed Lake Avenue station to a new substation south of the existing Lorain station. This new substation will tie into the existing Avon Lake – Crestwood – Fowles 138 kV circuit and the Avon Lake – Lorain – Slater – Crystal – Fowles 138 kV circuit, both owned by FirstEnergy.
P2014_1-3C | Greenfield | Transource | 52.4 | ATSI | Baseline Thermal; Gen Deliv | 99, 100, 101; 754, 918, 919, 920, 921, 1057 | Construct approximately 5 miles of new, double circuit 345 kV line to connect the FirstEnergy proposed Lake Avenue station to a new substation west of the existing Lorain station. This new substation will tie into the existing Avon - Juniper 345 kV circuit, the Avon Lake – Crestwood – Fowles 138 kV circuit, and the Carlisle - Lorain 138 kV circuit.
P2014_1-3D | Greenfield | Transource | 19 | AEP/ATSI | Gen Deliv | 720 | Construct approximately 17 miles of new single circuit 138 kV line between AEP’s existing Lockwood Road station and FirstEnergy’s existing Stryker station.
P2014_1-3E | Greenfield | Transource | 10.2 | AEP/ATSI | Gen Deliv | 720 | Construct approximately 7 miles of new single circuit 138 kV line the existing customer owned City of Bryan station and the FirstEnergy's existing Stryker station.
P2014_1-3F | Greenfield | Transource | 64.9 | AEP/ATSI | Gen Deliv | 790, 802 | Construct approximately 24 miles of new single circuit 345 kV line between the existing AEP Fremont 138 kV station and the under development FirstEnergy Hayes 345 kV station. Expand the existing Fremont 138 kV station to accomodate the new 345 kV line termination and a new 345/138 kV transformer. Construct a new 138 kV line between the Fremont 138 kV station and existing FirstEnergy West Fremont 138 kV station. The project will include a new 345/69 kV station where the new 345 kV lines intersect the FirstEnergy Castalia-Bellevue 69 kV line.
P2014_1-3G | Greenfield | Transource | 67.3 | ATSI | Gen Deliv | 790, 802 | Construct 24 miles of new double circuit 345 kV line between a new proposed 345/138 kV station adjacent to FirstEnergy's West Freemont station and the First Energy under development Hayes station. The project will include a new 345/69 kV station where the new 345 kV lines intersect the FirstEnergy Castalia-Bellevue 69 kV line.
P2014_1-3H | Greenfield | Transource | 34.1 | DEO&K/AEP | Baseline Thermal; Gen Deliv | 124; 1037 | Construct a new 138 kV path between Duke Ohio & Kentucky’s Willey Station to a new 345/138 kV station to be established on the AEP Tanner’s Creek to Desoto 345 kV in Indiana
P2014_1-3I | Greenfield | Transource | 146.4 | PPL | Gen Deliv | 797, 801 | Establish a new 500 kV path between the existing Montour 230 kV station and the Sunbury - Susquehanna 500kV line.
P2014_1-3J | Greenfield | Transource | 30.8 | DLCO | Baseline Thermal; Gen Deliv | 195, 196, 197; 719, 1108, 1109 | Tie Beaver Valley - Clinton and Beaver Valley - Crescent 345 kV lines into a new 345 kV switching station configured in a breaker and a half. Build a new 345 kV line from this new station to Clilnton Station.
P2014_1-3K | Greenfield | Transource | 71 | Comed | Gen Deliv | 993 | Establish a new 765/345 kV station near the existing ComEd Dresden station. Loop the Collins-Wilton Center 765 kV line and the Dresden Red - Pontiac Midpoint Red 345 kV line into this station, and install a 765/345 kV transformer
P2014_1-3L | Greenfield | Transource | 49 | PECO/AE | Gen Deliv | 807, 812, 1102 | Construct new 230 kV line between Mickleton station in New Jersey and Eddystone station in Pennsylvania
P2014_1-4A | Upgrade | Dominion Virginia Power | 1.82 | Dominion Virginia Power | Baseline Thermal; Gen Deliv | 366; 289 | Reconductor 1.41 miles of existing line between Acca and Hermitage and upgrade associated terminal equipment.
P2014_1-4B | Upgrade | Dominion Virginia Power | 0.04 | Dominion Virginia Power | Baseline Thermal; Gen Deliv | 429; 320 | Replace Wave Trap at Carver Substation with a 2000a Wave Trap
P2014_1-4C | Greenfield | Dominion High Voltage MidAtlantic | 31.8 | PPL | Gen Deliv | 797, 801 | A new 500/230kV transformaton station at the intersection of the 500kV Sunbury-Susquehanna line and 230kV Montour-Columbia-Frackville line, and Line upgrades to the Montour-Columbia-Frackville line.
P2014_1-5A | Upgrade | PECO | 0.4 | PECO | Gen Deliv | 170, 171 | Replace terminal equipment inside Chichester substation on 220-36 Chichester-Eddystone 230 kV line
P2014_1-5B | Upgrade | PECO | 2.2 | PECO | Gen Deliv | 170, 171 | Replace terminal equipment inside Chichester and Eddystone substations on 220-36 Chichester-Eddystone 230 kV line
P2014_1-5C | Upgrade | PECO | 0.1 | PECO | Gen Deliv | 315 | Replace terminal equipment inside Nottingham substation on 220-05 Nottingham-Daleville-Bradford 230 kV line
P2014_1-5D | Upgrade | PECO | 26.5 | PECO | Gen Deliv | 315 | Re-conductor the 220-05 Nottingham-Daleville-Bradford 230 kV line
P2014_1-5E | Upgrade | PECO | 0.1 | PECO | N-1-1 Thermal | 2.3 | Replace terminal equipment inside Llanerch substation on 130-45 Eddystone-Llanerch 138 kV line
P2014_1-5F | Upgrade | PECO | 38.4 | PECO | N-1-1 Thermal | 2.3 | Rebuild 130-45 Eddystone-Llanerch 138 kV line
P2014_1-6A | Upgrade | Comed | 4.6 | Comed | Baseline Thermal; Gen Deliv; N-1-1 Thermal | 175; 190; 1.4, 1.5, 2.6, 1.7 | Remove 2.0 miles of wood poles on 138 kV line 17105, erect new steel structures, and install new 1113 kcmil ACSR conductor from Roscoe Bert to Harlem
P2014_1-6B | Upgrade | Comed | 4.7 | Comed | Baseline Thermal; Gen Deliv; N-1-1 Thermal | 175; 190; 1.4, 1.5, 2.6, 1.7 | Remove 2.0 miles of wood poles on 138 kV line 17105, erect new steel structures, and install new 1113 kcmil ACSR conductor from Roscoe Bert to Harlem; replace existing 138kV line 17105 circuit-switcher #0564
P2014_1-6C | Upgrade | Comed | 2.6 | Comed | Gen Deliv | 993 | Install new 345 kV circuit breaker 5-7 at Elwood substation
P2014_1-7A | Greenfield | PPL | 61.8 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 122, 124, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978, 1092 | Build new 138 Kv line from BL England-Cardiff
P2014_1-7B | Greenfield | PPL | 73.2 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 122, 124, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978, 1092 | Build 2 new 138 kV lines double ckt from BL England-Cardiff
P2014_1-7C | Greenfield | PPL | 69.1 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 122, 124, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978, 1092 | Build one new 230 kV line, single ckt, from BL England-Cardiff
P2014_1-7D | Greenfield | PPL | 128.6 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 122, 124, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978, 1092 | Build one new 230 kV line, single ckt, Dennis-BL England and BL England-Cardiff
P2014_1-7E | Greenfield | PPL | 82.5 | AEP | Gen Deliv | 105, 106, 108, 110, 192, 209, 211, 212, 219, 220, 221, 222, 273, 274, 275, 276, 301, 773, 774, 775, 794, 795, 822, 823, 831, 832, 988, 1085, 1132 | Build one new 139 kV line, single ckt, from Clinch River-Saltville
P2014_1-7F | Greenfield | PPL | 98.1 | AEP/APS | Baseline Thermal; Gen Deliv | 113, 204, 205; 232, 234, 358, 799, 828, 1042 | Build one new double ckt 138 kV line Kammer-Windsor
P2014_1-7G | Greenfield | PPL | 279.5 | ATSI | Baseline Thermal; Gen Deliv | 99, 100, 101; 754, 790, 802, 918, 919, 920, 921, 1036, 1057 | Build one new 345kV line, built singlecircuit, from Davis-Besse to Carlisle to Avon, and Build one new double circuit 138kV line, built double-circuit, from Avon to Black River
P2014_1-7H | Greenfield | PPL | 66.1 | ATSI | Gen Deliv | 720 | Build one new single ckt 138 kV line, Midway-Richland
P2014_1-7I | Upgrade | PPL | 139.2 | PPL | Gen Deliv | 797, 801 | Rebuild Existing Montour-Milton-Sunbury 230 kV ckt to higher capacity
P2014_1-7J | Upgrade | PPL | 29.2 | PPL | Gen Deliv | 797, 801 | Add second 230 kV circuit to existing Montour - Sunbury 230 kV circuit from Montour to Milton Substation. Energize existing 69 kV circuit from Milton to Sunbury at 230 kV.
P2014_1-7K | Greenfield | PPL | 114.1 | PPL | Gen Deliv | 797, 801 | Build new 230 kV line from Montour-Sunbury
P2014_1-7L | Greenfield | PPL | 87.1 | PPL | Gen Deliv | 797, 801 | Build new 230 kV line from Montour-Susquhanna T-10
P2014_1-7M | Greenfield | PPL | 102.9 | PPL | Gen Deliv | 797, 801 | Build a new 500-230 kV Substation near Catawissa with 1-750 MVA transformer and increase capacity on the existing 230 kV line from Montour to Catawissa Sub
P2014_1-7N | Greenfield | PPL | 112.5 | PPL | Gen Deliv | 797, 801 | Build a new 500-230 kV Substation near Catawissa with 2-750 MVA transformers and increase capacity on the existing 230 kV line from Montour to Catawissa Sub
P2014_1-7O | Greenfield | PPL | 164.2 | PPL | Gen Deliv | 797, 801 | Build a new 230 kV line Montour-Harwood
P2014_1-7P | Greenfield | PPL | 1367 | PPL/Penelec | Gen Deliv | 965, 971, 797, 801 | Build a new double circuit 500 kV line and corresponding 500 kV substations. The line begins at PPL EU's Lackawanna 500 kV substation and terminates at PPL EU's Sunbury 500 kV substation. Between start and end points, the line connects to FE's existing North Meshoppen 230 kV and PLL EU's Montour 230 kV substation.
P2014_1-8A | Upgrade | BGE | 1.14 | BGE | Baseline Thermal; Gen Deliv | 222; 1099 | Upgrade the Riverside 115kV substation strain bus conductors on circuits 115012 and 115011 with double bundled 1272 ACSR to achieve ratings of 491/577 MVA SN/SE on both transformer leads.
P2014_1-8B | Upgrade | BGE | 2.6 | BGE | Baseline Thermal; Gen Deliv | 222; 1099 | Reconfigure Riverside 230kV substation by installing a 230kV breaker on line 2344 and install circuit switchers on the high side of transformers 230-1 and 230-2
P2014_1-8C | Upgrade | BGE | 3.74 | BGE | Baseline Thermal; Gen Deliv | 222; 1099 | Upgrade the Riverside 115kV substation strain bus conductors on circuits 115012 and 115011 with double bundled 1272 ACSR to achieve ratings of 491/577 MVA SN/SE on both transformer leads. Reconfigure Riverside 230kV substation by installing a 230kV breaker on line 2344 and installing circuit switchers on the high side of transformers 230-1 and 230-2
P2014_1-8D | Upgrade | BGE | 1.2 | BGE | N-1-1 Thermal | 1.8 | Reconductor Northwest – Northwest #2 115kV 110574 substation tie circuit with 2167 ACSR to achieve ratings of 400/462 MVA SN/SE
P2014_1-8E | Upgrade | BGE | 2.5 | BGE | N-1-1 Thermal | 1.8 | Reconductor Northwest – Northwest #2 115kV 110574 substation tie circuit with 2-bundle 1272 ACSR and replace the Northwest 115kV 110574 tie circuit breaker to achieve ratings of 519/600 MVA SN/SE.
P2014_1-9A | Upgrade | First Energy | 26.5 | PPL/Penelec | Gen Deliv | 965, 971 | Reconductor Lackawanna - North Meshoppen Line and upgrade terminals.
P2014_1-9B | Upgrade | First Energy | 73.4 | PPL/Penelec | Gen Deliv | 965, 971 | Rebuild Lackawanna - North Meshoppen Line and upgrade terminals.
P2014_1-9C | Upgrade | First Energy | 0.1 | Meted | N-1-1 Thermal | 1.1, 1.2 | Upgrade the limiting terminal facilities at both Jackson and North Hanover.
P2014_1-9D | Upgrade | First Energy | 0.6 | JCPL | Gen Deliv | 843, 844, 846, 847, 1128 | Upgrade limiting terminal facilities at Freneau, Parlin, and Williams substatons.
P2014_1-9E | Upgrade | First Energy | 5.4 | ATSI | Gen Deliv | 1057 | At Avon substation, replace the existing 345/138kV 448MVA #92 transformer with a 560MVA unit.
P2014_1-9F | Upgrade | First Energy | 9.6 | ATSI | Baseline Thermal; Gen Deliv | 99, 100, 101; 754, 918, 919, 920, 921 | Reconductor the Black River-Lorain 138kV line and upgrade Black River and Lorain substation terminal end equipment.
P2014_1-9G | Upgrade | First Energy | 7.4 | ATSI | Gen Deliv | 802, 790 | Construct second 138kV line between West Fremont and Hayes substation on open tower position of the West Fremont - Groton - Hayes 138kV line
P2014_1-9H | Upgrade | First Energy | 0.02 | ATSI | Gen Deliv | 720 | Close normally open switch A13404 to create a Richland J Bus - Richalnd K Bus 138kV line.
P2014_1-10A | Upgrade | Duquesne | 7.285 | Duquesne | Baseline Thermal; Gen Deliv | 195, 196, 197; 719, 1108, 1109 | Operate with the Crescent No. 3 345/138kV autotransformer in-service by replacing eight (8) overdutied 138kV breakers at Crescent and three (3) 138kV breakers at Beaver Valley and install a No. 1 section 345kV breaker for the 331 circuit at Crescent.
P2014_1-11A | Greenfield | ITC | 207.9 | AEP | Gen Deliv | 192, 209, 211, 212, 794, 795, 822, 823, 1085, 219, 220, 221, 222, 273, 274, 275, 276, 301, 831, 832, 1132, 105, 106, 108, 110, 773, 774, 775, 988 | Build a new 765/138 kV substation (Clinch River 765 kV) that taps the Virginia City-Clinch River 138 kV ckt #1, add 765/138 kV xfmr at new substation, run two 765 kV single structure single ckt from new substation to Broadford-Baker 765 kV cutting into the existing 765 kV line. Upgrade the limiting equiptment on the Elk Garden-Saltville line.
P2014_1-11B | Greenfield | ITC | 107 | ATSI/AEP | Gen Deliv | 790, 802 | Build Fremont - Avery 138 kV double ckt line and reconductor Freemont-West Freemont 138 kV line
P2014_1-11C | Greenfield | ITC | 97.4 | ATSI/AEP | Gen Deliv | 790, 802 | Build Freemont-Avery 138 kV line with series compensation
P2014_1-11D | Greenfield | ITC | 27.1 | PECO/DPL | Gen Deliv | 315 | Build a 230 kV swtichyard (colora tap) at the confluence of the following lines: Conowingo-Nottingham 230 kV, Conowingo-Colora 230 kV, and Colora-Clary 230 kV
P2014_1-11E | Greenfield | ITC | 45.4 | AEP/APS | Baseline Thermal; Gen Deliv | 133, 195, 196, 197, 204, 205; 232,234,799, 1042, 358, 828, 719, 1108, 1109 | Build 138 kV switchyard (Liberty) at the confluence of the following lines: Windsor-Dutch Fork 138 kV, Windsor-Lagonda 138 kV, Tidd-Fort Henry 138 kV, and West Liberty-Battle 138 kV. Reconductor Fort Henry-Sand Hill, Kammer-Big Grave Creek, and Big Grave Creek-Aston Switch 138kV lines.
P2014_1-11F | Greenfield | ITC | 104 | AEP/OVEC | Gen Deliv | 164, 165 | Build Kyger Creek-Sporn 345 kV line. Replace/upgrade Sporn XFMR #3
P2014_1-12A | Greenfield | PHI | 54.675 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978 | New BL England-Lewis 138 kV line
P2014_1-12B | Upgrade | PHI | 37.49 | AE | Gen Deliv | 807 | Rebuild of #1 Mickelton-Monroe 230 kV
P2014_1-12C | Upgrade | PHI | 4.18 | AE | Gen Deliv | 812 | Reconductor of #2 Mickleton-Monroe 230 kV
P2014_1-12D | Upgrade | PHI | 4.204 | AE | Gen Deliv | 81, 83, 943 | Reconductor #1 Scull - #1 Mill 138 kV
P2014_1-12E | Upgrade | PHI | 14.645 | AE | Gen Deliv | 87, 88, 91, 951, 952 | Reconductor #2 Scull - #2 BL England 138 kV
P2014_1-12F | Upgrade | PHI | 9.079 | AE | Gen Deliv | 116, 117, 120, 977, 978 | Reconductor #2 Scull - #2 Mill 138 kV
P2014_1-12G | Upgrade | PHI | 3.956 | AE | Gen Deliv | 976, 132, 134 | Reconductor #1 Scull - BL England 138 Kv
P2014_1-12H | Upgrade | PHI | 15.806 | AE | Gen Deliv | 763 | Rebuild #1 BL England - Corson 138 kV
P2014_1-12I | Upgrade | PHI | 9.256 | AE | Gen Deliv | 964 | Rebuild #1 Mill - #1 Lewis 138 kV
P2014_1-12J | Upgrade | PHI | 7.98 | AE | Gen Deliv | new1 | Replace Middle 138/69 kV XFMR with 225 MVA nameplate xfmr
P2014_1-12K | Upgrade | PHI | 0.04 | DP&L | Gen Deliv | 804 | Replace Terminal equiptment at Silverside 69 kV substation
P2014_1-13A | Greenfield | NextEra Energy Transmission LLC | 68.81 | PPL/Penelec | Gen Deliv | 965, 971 | Build a new single circuit overhead 230 kV line from North Meshoppen-Lackawanna
P2014_1-13B | Greenfield | NextEra Energy Transmission LLC | 55.36 | PPL | Gen Deliv | 797, 801 | Build a new single circuit overhead 230 Kv line from Montour-Sunbury
P2014_1-14A | Greenfield | Northeast Transmission Development | 50.1 | DLCO/APS/ATSI | Baseline Thermal; Gen Deliv | 195, 196, 197; 719, 1108, 1109 | Build 500/138 kV Substation (Crows Run) Interconnecting Wylie Ridge-Cranberry 500 kV Line to Crescent-Valley 138 kV Line and Wolfe Run-Legionville 138 kV Line
P2014_1-14B | Greenfield | Northeast Transmission Development | 22.7 | PECO | Gen Deliv; N-1-1 Thermal | 170, 171, 807, 812, 1102; 2.3 | Approx 4 mile 230 kV transmission line from Delco 230 kV substation to Eddystone 230 kV substation
P2014_1-14C | Greenfield | Northeast Transmission Development | 24.1 | AEP/APS | Baseline Thermal; Gen Deliv | 204, 205; 133, 232, 234, 358, 799, 828, 1042 | Build 138 kV switching station (Garrison Run) interconnecting the Tidd – West Liberty 138 kV Line, Tidd - Fort Henry 138 kV Line, Windsor – Lagonda 138 kV Line, and Windsor – Dutch Fork 138 kV Line
P2014_1-14D | Greenfield | Northeast Transmission Development | 20.8 | AEP | Baseline Thermal; Gen Deliv | 204, 205; 232, 234, 358, 799, 828, 1042 | Approximately 9-mile 138 kV transmission line from Kammer 138 kV substation to Holloway 138 kV substation
P2014_1-14E | Greenfield | Northeast Transmission Development | 49.8 | PPL | Gen Deliv | 797, 801 | Approximately 18-mile 230 kV transmission line from Montour 230 kV substation to a new 230 kV switching station ("Furman") on the Sunbury - Susquehanna 230 kV Line.
P2014_1-14E1 | Greenfield | Northeast Transmission Development | 80.9 | PPL | Gen Deliv | 797, 801 | Approximately 18-mile 230 kV transmission line from Montour 230 kV substation to a new 500/230 kV substation (“Furman”) on the Sunbury – Susquehanna 500 and 230 KV Lines
P2014_1-14F | Greenfield | Northeast Transmission Development | 32 | DEOK/Dayton | Baseline Thermal; Gen Deliv | 124; 1037 | Build 345/138 kV Substation (Paddys Run) Interconnecting Miami Fort-West Milton 345 kV Line to Willey 138 kV
P2014_1-14G | Greenfield | Northeast Transmission Development | 12.8 | AEP/APS | Baseline Thermal; Gen Deliv | 204, 205; 232, 234, 358,799,828, 1042 | Approximately 4-mile 138 kV transmission line from Tidd 138 kV substation to Windsor 138 kV substation
P2014_1-14H | Greenfield | Northeast Transmission Development | 46 | AEP | Gen Deliv | 105, 106, 108, 110, 192, 209, 211, 212, 219, 220, 221, 222, 273, 274, 275, 276, 301, 773, 774, 775, 794, 795, 822, 823, 831, 832, 988, 1085, 1132 | Approximately 26-mile 138 kV transmission line from Clinch River 138 kV substation to a new 138 kV switching station ("West Fork") on the Richlands-Whitewood 138 kV Line.
P2014_1-14H1 | Greenfield | Northeast Transmission Development | 53.8 | AEP | Gen Deliv | 105, 106, 108, 110, 192, 209, 211, 212, 219, 220, 221, 222, 273, 274, 275, 276, 301, 773, 774, 775, 794, 795, 822, 823, 831, 832, 988, 1085, 1132 | Approximately 26-mile 138 kV transmission line from Clinch River 138 kV substation to a new 138 kV switching station ("West Fork") on the Richlands-Whitewood 138 kV Line + second ckt Clinch River-West Fork
P2014_1-14I | Greenfield | Northeast Transmission Development | 51.6 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978 | Approximately 13.7 mile 138 kV transmission line from BL England 138 kV substation to Cardiff 138 kV substation
P2014_1-14J | Greenfield | Northeast Transmission Development | 33.8 | AEP/OVEC | Gen Deliv | 164, 165 | Build 345/138 kV Substation (Swisher Hill) Interconnecting Kyger Creek-DOE 345 kV Line to Sporn-Mercerville 138 kV Line
P2014_1-14J1 | Greenfield | Northeast Transmission Development | 46.6 | AEP/OVEC | Gen Deliv | 164, 165 | Build 345/138 kV Substation (Swisher Hill) Interconnecting Kyger Creek-DOE 345 kV Line to Sporn-Mercerville 138 kV Line + 138 kV line from Gavin - new (Swisher Hill) substation
P2014_1-14K | Greenfield | Northeast Transmission Development | 32.5 | ATSI | Baseline Thermal; Gen Deliv | 99, 100, 101; 754, 918, 919, 920, 921, 1057 | Approximately 5-mile 345 kV transmission line from Lake Avenue 345 kV substation to a new 345 kV switching station ("Case") on the Avon Lake-Juniper 345 kV Line.
P2014_1-15A | Greenfield | PSEG | 98 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978 | Build a new 138 kV line from BL England-Cardiff including 1 138/230 kV XFMR at Cardiff
P2014_1-15B | Greenfield | PSEG | 134 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978 | Build a new 230 kV line from BL England-Cardiff including 1 138/230 kV XFMR at BL England
P2014_1-15C | Greenfield | PSEG | 225 | AE | Gen Deliv | 81, 83, 87, 88, 91, 116, 117, 120, 132, 134, 763, 943, 951, 952, 964, 976, 977, 978 | Build a new 230 kV line from Dennis-Cardiff with a tap at BL England, include 1 230/138 kV XFMR at BL England
P2014_1-15D | Greenfield | PSEG | 101 | PSEG/PECO | Gen Deliv | 807, 812, 1102 | Build new 230 kV Underground ckt from new station at Eagle Point to Penrose
P2014_1-15E | Greenfield | PSEG | 92 | PSEG | Gen Deliv | 1102 | Build a new 230 kV underground circuit from Gloucester-Cuthbert
P2014_1-15F | Greenfield | PSEG | 92 | AEP/OVEC | Gen Deliv | 164, 165 | Construct a new station tapping the Sporn-Tristate line and construct a line from the new station to Kyger Creek

## Flowgates from Results V4
2014 RTEP Proposal Window 1
Proposal Window: |  | 2014 RTEP Proposal Window 1
Window Opening Date: |  | 2014-06-27
Window Closing Date: |  | 2014-07-28
Current Spreadsheet Version |  | V3 - 8/11/2014
Analysis Type | Flowgate # | From Bus # | From Bus Name | To Bus # | To Bus Name | CKT | KVs | Areas | Rating | Cont Type | Comment
N-1 Thermal | 99 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
N-1 Thermal | 100 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
N-1 Thermal | 101 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
N-1 Thermal | 124 | 250057 | 08M.FORT | 250131 | 08WILEY2 | 1 | 138/138 | 212/212 | 198 | Multiple | ****
N-1 Thermal | 133 | 235428 | 01WINDSR | 243131 | 05TILTON | 1 | 138/138 | 201/205 | 205 | Single | ****
N-1 Thermal | 175 | 272378 | ROSCOE BE;BT | 271638 | HARLEM ; B | 1 | 138/138 | 222/222 | 175 | Single | ****
N-1 Thermal | 195 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | Multiple | ***
N-1 Thermal | 196 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | Multiple | ***
N-1 Thermal | 197 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | Multiple | ***
N-1 Thermal | 204 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | Multiple | ****
N-1 Thermal | 205 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | Multiple | ****
N-1 Thermal | 222 | 221231 | RIV982-2 | 221147 | RIVERSDE | 1 | 115/115 | 232/232 | 437 | Multiple | *
N-1 Thermal | 366 | 314211 | 3ACCA | 313832 | 3HERM159 | 1 | 115/115 | 345/345 | 180 | Single | ****
N-1 Thermal | 429 | 314234 | 3NRTHEST | 314213 | 3CARVER | 1 | 115/115 | 345/345 | 159 | Single | ****
Gen Deliv/CMO | 81 | 227905 | SCULL#1 | 227903 | MILL #1 | 1 | 138/138 | 234/234 | 262 | single | ****
Gen Deliv/CMO | 83 | 227905 | SCULL#1 | 227903 | MILL #1 | 1 | 138/138 | 234/234 | 262 | single | ****
Gen Deliv/CMO | 87 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | single | ****
Gen Deliv/CMO | 88 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | single | ****
Gen Deliv/CMO | 91 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 219 | single | ****
Gen Deliv/CMO | 105 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | single | *
Gen Deliv/CMO | 106 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | single | *
Gen Deliv/CMO | 108 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | single | *
Gen Deliv/CMO | 110 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | single | *
Gen Deliv/CMO | 116 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | single | ****
Gen Deliv/CMO | 117 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | single | ****
Gen Deliv/CMO | 120 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 219 | single | ****
Gen Deliv/CMO | 132 | 228110 | BLE | 227905 | SCULL#1 | 1 | 138/138 | 234/234 | 307 | single | ****
Gen Deliv/CMO | 134 | 228110 | BLE | 227905 | SCULL#1 | 1 | 138/138 | 234/234 | 307 | single | ****
Gen Deliv/CMO | 164 | 248005 | 06KYGER | 242528 | 05SPORN | 2 | 345/345 | 206/205 | 971 | single | ****
Gen Deliv/CMO | 165 | 248005 | 06KYGER | 242528 | 05SPORN | 2 | 345/345 | 206/205 | 971 | single | ****
Gen Deliv/CMO | 170 | 213489 | CHICHST1 | 213588 | EDDYSTN4 | 1 | 230/230 | 230/230 | 863 | single | *
Gen Deliv/CMO | 171 | 213489 | CHICHST1 | 213588 | EDDYSTN4 | 1 | 230/230 | 230/230 | 863 | single | *
Gen Deliv/CMO | 190 | 272378 | ROSCOE BE;BT | 271638 | HARLEM ; B | 1 | 138/138 | 222/222 | 175 | single | ****
Gen Deliv/CMO | 192 | 242605 | 05CLNCHR | 242606 | 05CLNLFD | 1 | 138/138 | 205/205 | 223 | single | *
Gen Deliv/CMO | 209 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 296 | single | *
Gen Deliv/CMO | 211 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | single | *
Gen Deliv/CMO | 212 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | single | *
Gen Deliv/CMO | 219 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | single | ***
Gen Deliv/CMO | 220 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | single | ***
Gen Deliv/CMO | 221 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | single | ***
Gen Deliv/CMO | 222 | 242606 | 05CLNLFD | 242639 | 05FLETCH | 1 | 138/138 | 205/205 | 223 | single | ***
Gen Deliv/CMO | 232 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 205 | single | ****
Gen Deliv/CMO | 234 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | single | ****
Gen Deliv/CMO | 273 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | single | ****
Gen Deliv/CMO | 274 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | single | ****
Gen Deliv/CMO | 275 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | single | ****
Gen Deliv/CMO | 276 | 242639 | 05FLETCH | 242801 | 05SKEGGB | 1 | 138/138 | 205/205 | 223 | single | ****
Gen Deliv/CMO | 289 | 314211 | 3ACCA | 313832 | 3HERM159 | 1 | 115/115 | 345/345 | 169.2 | single | ****
Gen Deliv/CMO | 301 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 296 | single | *
Gen Deliv/CMO | 315 | 213844 | NOTTNGHM | 213553 | DALEVLLE | 1 | 230/230 | 230/230 | 519 | single | *
Gen Deliv/CMO | 320 | 314234 | 3NRTHEST | 314213 | 3CARVER | 1 | 115/115 | 345/345 | 149.46 | single | ****
Gen Deliv/CMO | 358 | 243026 | 05KAMMR1 | 243143 | 05WBELLA | 1 | 138/138 | 205/205 | 296 | single | ***
Gen Deliv/CMO | 719 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | Multiple | **
Gen Deliv/CMO | 720 | 239070 | 02RICHLD | 238521 | 02NAOMI | 1 | 138/138 | 202/202 | 194 | Multiple | ****
Gen Deliv/CMO | 754 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
Gen Deliv/CMO | 763 | 228110 | BLE | 228111 | MDLE TP | 1 | 138/138 | 234/234 | 286 | Multiple | ****
Gen Deliv/CMO | 773 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | Multiple | *
Gen Deliv/CMO | 774 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | Multiple | *
Gen Deliv/CMO | 775 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | Multiple | *
Gen Deliv/CMO | 790 | 239030 | 02OTTAWA | 238874 | 02LAKVEW | 1 | 138/138 | 202/202 | 375 | Multiple | ****
Gen Deliv/CMO | 794 | 242605 | 05CLNCHR | 242606 | 05CLNLFD | 1 | 138/138 | 205/205 | 310 | Multiple | ****
Gen Deliv/CMO | 795 | 242605 | 05CLNCHR | 242606 | 05CLNLFD | 1 | 138/138 | 205/205 | 310 | Multiple | ****
Gen Deliv/CMO | 797 | 208040 | MONT | 208034 | MILT | 1 | 230/230 | 229/229 | 802 | Multiple | ****
Gen Deliv/CMO | 799 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | Multiple | ****
Gen Deliv/CMO | 801 | 208034 | MILT | 208109 | SUNB | 1 | 230/230 | 229/229 | 730.61 | Multiple | ****
Gen Deliv/CMO | 802 | 238874 | 02LAKVEW | 238768 | 02GRNFLD | 1 | 138/138 | 202/202 | 316 | Multiple | *
Gen Deliv/CMO | 804 | 231215 | SILVERSD | 231205 | DARLEY | 1 | 69/69 | 235/235 | 123 | Multiple | ****
Gen Deliv/CMO | 807 | 228401 | MCKLTON | 228402 | MONROE | 2 | 230/230 | 234/234 | 478 | Multiple | ****
Gen Deliv/CMO | 812 | 228401 | MCKLTON | 228402 | MONROE | 1 | 230/230 | 234/234 | 478 | Multiple | ****
Gen Deliv/CMO | 822 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | Multiple | *
Gen Deliv/CMO | 823 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | Multiple | *
Gen Deliv/CMO | 828 | 243026 | 05KAMMR1 | 243143 | 05WBELLA | 1 | 138/138 | 205/205 | 296 | Multiple | ***
Gen Deliv/CMO | 831 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 384 | Multiple | *
Gen Deliv/CMO | 832 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 384 | Multiple | *
Gen Deliv/CMO | 843 | 206322 | 28PARLIN | 206298 | 28WILLIAMS | 1 | 230/230 | 228/228 | 813 | Multiple | *
Gen Deliv/CMO | 844 | 206322 | 28PARLIN | 206298 | 28WILLIAMS | 1 | 230/230 | 228/228 | 813 | Multiple | *
Gen Deliv/CMO | 846 | 206298 | 28WILLIAMS | 206292 | 28FRENEAU | 1 | 230/230 | 228/228 | 813 | Multiple | *
Gen Deliv/CMO | 847 | 206298 | 28WILLIAMS | 206292 | 28FRENEAU | 1 | 230/230 | 228/228 | 813 | Multiple | *
Gen Deliv/CMO | 918 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
Gen Deliv/CMO | 919 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
Gen Deliv/CMO | 920 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
Gen Deliv/CMO | 921 | 239728 | 02BLKRVR | 238915 | 02LRN Q2 | 1 | 138/138 | 202/202 | 270 | Multiple | ****
Gen Deliv/CMO | 943 | 227905 | SCULL#1 | 227903 | MILL #1 | 1 | 138/138 | 234/234 | 262 | Multiple | ****
Gen Deliv/CMO | 951 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | Multiple | ****
Gen Deliv/CMO | 952 | 228110 | BLE | 227906 | SCULL#2 | 1 | 138/138 | 234/234 | 307 | Multiple | ****
Gen Deliv/CMO | 964 | 227903 | MILL #1 | 227902 | LEWIS #1 | 1 | 138/138 | 234/234 | 262 | Multiple | ****
Gen Deliv/CMO | 965 | 200706 | 26N.MESHPN | 200708 | 26OXBOW | 1 | 230/230 | 226/226 | 617 | Multiple | ****
Gen Deliv/CMO | 971 | 200708 | 26OXBOW | 208009 | LACK | 1 | 230/230 | 226/229 | 624 | Multiple | ****
Gen Deliv/CMO | 976 | 228110 | BLE | 227905 | SCULL#1 | 1 | 138/138 | 234/234 | 307 | Multiple | ****
Gen Deliv/CMO | 977 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | Multiple | ****
Gen Deliv/CMO | 978 | 227906 | SCULL#2 | 227904 | MILL #2 | 1 | 138/138 | 234/234 | 307 | Multiple | ****
Gen Deliv/CMO | 988 | 246766 | 05ELKGAZ | 242788 | 05SALTV1 | 1 | 138/138 | 205/205 | 321 | Multiple | *
Gen Deliv/CMO | 993 | 270717 | DRESDEN ; R | 275180 | DRESDEN ;3M | 1 | 345/138 | 222/222 | 530 | Multiple | **
Gen Deliv/CMO | 1037 | 250057 | 08M.FORT | 250131 | 08WILEY2 | 1 | 138/138 | 212/212 | 198 | Multiple | ****
Gen Deliv/CMO | 1042 | 243131 | 05TILTON | 235428 | 01WINDSR | 1 | 138/138 | 205/201 | 284 | Multiple | ****
Gen Deliv/CMO | 1057 | 238551 | 02AVON | 238552 | 02AVON | 92 | 345/138 | 202/202 | 602 | Multiple | **
Gen Deliv/CMO | 1085 | 242605 | 05CLNCHR | 242700 | 05LEBANO | 1 | 138/138 | 205/205 | 384 | Multiple | *
Gen Deliv/CMO | 1099 | 221231 | RIV982-2 | 221147 | RIVERSDE | 1 | 115/115 | 232/232 | 437 | Multiple | *
Gen Deliv/CMO | 1102 | 219110 | GLOUCSTR_2 | 219755 | CUTHBERT_4 | 2 | 230/230 | 231/231 | 711 | Multiple | ****
Gen Deliv/CMO | 1108 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | Multiple | **
Gen Deliv/CMO | 1109 | 253936 | 15CRESCN | 253935 | 15CRESCN | 1 | 345/138 | 215/215 | 371 | Multiple | **
Gen Deliv/CMO | 1128 | 206322 | 28PARLIN | 206298 | 28WILLIAMS | 1 | 230/230 | 228/228 | 813 | Multiple | *
Gen Deliv/CMO | 1132 | 242700 | 05LEBANO | 246766 | 05ELKGAZ | 1 | 138/138 | 205/205 | 384 | Multiple | *
Gen Deliv/CMO | new1 | 228113 | MIDDLE#1 | 228122 | MIDDLE#1 | 1 | 138/69 | 234/234 | 193 | Multiple | **
N-1-1 Thermal | 1.1 | 204540 | 27JACKSON | 204548 | 27N.HANOVR | 1 | 115/115 | 227/227 | 131 | C3 | *
N-1-1 Thermal | 1.2 | 204540 | 27JACKSON | 204548 | 27N.HANOVR | 1 | 115/115 | 227/227 | 131 | C3 | *
N-1-1 Thermal | 2.3 | 213571 | EDDYREA1 | 213759 | LLAN13 | 1 | 138/138 | 230/230 | 311 | C3 | *
N-1-1 Thermal | 1.4 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | C3 | ****
N-1-1 Thermal | 1.5 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | C3 | ****
N-1-1 Thermal | 2.6 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | C3 | ****
N-1-1 Thermal | 1.7 | 271638 | HARLEM ; B | 272378 | ROSCOE BE;BT | 1 | 138/138 | 222/222 | 175 | C3 | ****
N-1-1 Thermal | 1.8 | 221011 | NWEST2 | 221061 | N.WEST | Z | 115/115 | 232/232 | 350 | C3 | *
Note: Comments in Column N description
| * | Terminal Equipment Limit
| ** | Transformer
| *** | Sag/Clearance Limitation
| **** | Conductor Limit

## Revision History
PJM 2014 RTEP Proposal Window #1 Tracking Spreadsheet
Proposal Window: | 2014 RTEP Proposal Window 1
Window Opening Date: | 2014-06-27
Window Closing Date: | 2014-07-28
Current Spreadsheet Version | V3 - 8/11/2014
Version 1: Posted 8/5
Version 2: Posted 8/6 Revisions include Project 2014_1-4C Proposing Entity name updated to say "Dominion High Voltage MidAtlantic"
Version 3: Posted 8/11 Revisions include Project 2014_1-7J Updated to show "Upgrade", not "Greenfield"