## 2018-2019 Parameters
2018-2019 RPM Base Residual Auction Planning Parameters | [5 empty] | 2015-08-26 | #4368641
Added Post-Clearing BRA Credit Rates
| RTO | Notes:
Installed Reserve Margin (IRM) | 15.7% | From 2014 Reserve Requirement Study.
Pool-Wide Average EFORd | 6.35% | Includes OMC outages
Forecast Pool Requirement (FPR) | 1.0835 | Based on Pool-Wide EFORd including OMC outages
Demand Resource (DR) Factor | NA | DR Factor eliminated
Preliminary Forecast Peak Load | 161418.4 | Load data: from 2015 Load Report with adjustments due to load served outside PJM.
Short-Term Resource Procurement Target | NA | STRPT eliminated
Base Capacity Resource Pre-Clearing BRA Credit Rate, $/MW | 32912.42 | Capacity Performance Resource Credit Rates are based on the Net CONE of the modeled LDA in which the planned resource is located (see pre-clearing credit rate applicable to each modeled LDA below)
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL
CETO | NA | -1900 | 2850 | 5160 | 5800 | 2350 | 1360 | 3470 | 4520 | 3340 | 860 | 4550 | -500
CETL | NA | 7883 | 8375 | 9888 | 7926 | 3761 | 1702 | 7045 | 9240 | 4557 | 5227 | 6527 | 4538
Reliability Requirement | 174896.8 | 69853.6 | 38535.2 | 16211.6 | 12416.1 | 6379.1 | 3149.7 | 8181.2 | 16048.1 | 6029.7 | 28045.8 | 8706.7 | 10040.1
Total Peak Load of FRR Entities | 13188.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343.3 | 0 | 0
Preliminary FRR Obligation | 14289.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0
Reliability Requirement adjusted for FRR | 160607.4 | 69853.6 | 38535.2 | 16211.6 | 12416.1 | 6379.1 | 3149.7 | 8181.2 | 16048.1 | 6029.7 | 27704.676 | 8706.7 | 10040.1
Short-Term Resource Procurement Target | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Net CONE, $/MW-Day (UCAP Price) | 300.57 | 271.67 | 284.82 | 243.17 | 297.99 | 297.99 | 258.32 | 250.74 | 271.72 | 271.72 | 320.29 | 235.59 | 284.79
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 450.86 | 407.51 | 427.23 | 381.19 | 446.99 | 446.99 | 387.48 | 381.19 | 407.58 | 407.58 | 480.44 | 381.19 | 427.19
Point (b) UCAP Price, $/MW-Day | 225.43 | 203.75 | 213.62 | 182.38 | 223.49 | 223.49 | 193.74 | 188.06 | 203.79 | 203.79 | 240.22 | 176.69 | 213.59
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Point (a) UCAP Level, MW | 160329.8 | 69732.9 | 38468.6 | 16183.6 | 12394.6 | 6368.1 | 3144.3 | 8167.1 | 16020.4 | 6019.3 | 27656.8 | 8691.6 | 10022.7
Point (b) UCAP Level, MW | 164633 | 71604.5 | 39501.1 | 16617.9 | 12727.3 | 6539 | 3228.6 | 8386.3 | 16450.3 | 6180.8 | 28399.1 | 8924.9 | 10291.8
Point (c) UCAP Level, MW | 172823 | 75166.6 | 41466.1 | 17444.6 | 13360.5 | 6864.3 | 3389.3 | 8803.5 | 17268.7 | 6488.3 | 29811.9 | 9368.9 | 10803.7
Participant-Funded ICTRs Awarded | NA | 892 | NA | NA | NA | NA | 72 | NA | NA | NA | NA | NA | NA
Capacity Performance Resource Pre-Clearing BRA Credit Rate, $/MW | 54854.03 | 49579.78 | 51979.65 | 44378.53 | 54383.18 | 54383.18 | 47143.4 | 45760.05 | 49588.9 | 49588.9 | 58452.93 | 42995.18 | 51974.18
Participant-Funded ICTRs Awarded | NA | 892 | NA | NA | NA | NA | 72 | NA | NA | NA | NA | NA | NA
FRR Load Requirement (% Obligation):
Minimum Internal Resource Requirement | NA | 97% | 86.4% | 43% | 40.8% | 48.7% | 55.8% | 16.1% | 48.6% | 30.6% | 91.7% | 28.5% | 69.7%
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and FRR load.
LDA/Zone | CETO | CETL | CETL to CETO Ratio % | 2014 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load
RTO | NA | NA | NA | 156414.7 | 161418.4 | NA | 13188.2 | 148230.2
AE | 640 | > 736 | > 115% | 2610 | 2634 | 1.0092 | 0 | 2634
AEP | 1710 | > 1967 | > 115% | 22760 | 23224 | 1.0204 | 11945.3 | 11278.7
APS | 2520 | > 2898 | > 115% | 8350 | 8713 | 1.0435 | 0 | 8713
ATSI | 4520 | 9240 | 204.4% | 12760 | 12924 | 1.0129 | 0 | 12924
ATSI-CLEVELAND | 3340 | 4557 | 136.4% | NA | 4444.6 | NA | 0 | 4444.6
BGE | 4550 | 6527 | 143.5% | 6940 | 7062 | 1.0176 | 0 | 7062
COMED | 860 | 5227 | 607.8% | 21970 | 22959 | 1.045 | 343.3 | 22615.7
DAYTON | 920 | > 1058 | > 115% | 3290 | 3506 | 1.0657 | 0 | 3506
DEOK | 4130 | > 4750 | > 115% | 5310 | 5425 | 1.0217 | 878 | 4547
DLCO | 1590 | > 1829 | > 115% | 2830 | 2908 | 1.0276 | 0 | 2908
DOM | -1320 | * | * | 19090 | 20557 | 1.0768 | 0 | 20557
DPL | 1030 | > 1185 | > 115% | 4020 | 4164 | 1.0358 | 0 | 4164
DPL SOUTH | 1360 | 1702 | 125.1% | NA | 2396 | NA | 0 | 2396
EKPC | 630 | > 725 | > 115% | 2144.7 | 2259.4 | 1.0535 | 21.6 | 2237.8
JCPL | 3280 | > 3772 | > 115% | 6090 | 6236 | 1.024 | 0 | 6236
METED | 1190 | > 1369 | > 115% | 2850 | 2958 | 1.0379 | 0 | 2958
PECO | 2850 | > 3278 | > 115% | 8380 | 8622 | 1.0289 | 0 | 8622
PENLC | 230 | > 265 | > 115% | 2770 | 2923 | 1.0552 | 0 | 2923
PEPCO | 3470 | 7045 | 203% | 6540 | 6500 | 0.99388 | 0 | 6500
PL (incl. UGI) | -500 | 4538 | * | 7145 | 7287 | 1.0199 | 0 | 7287
PS | 5800 | 7926 | 136.7% | 10160 | 10146 | 0.99862 | 0 | 10146
PS NORTH | 2350 | 3761 | 160% | NA | 4963.4 | NA | 0 | 4963.4
RECO | NA | NA | NA | 405 | 411 | 1.0148 | 0 | 411
EMAAC | 2850 | 8375 | 293.9% | NA | 32213 | NA | 0
SWMAAC | 5160 | 9888 | 191.6% | NA | 13562 | NA | 0
Western MAAC | -7320 | * | * | NA | 13168 | NA | 0
MAAC | -1900 | 7883 | * | NA | 58943 | NA | 0
Western PJM | 4800 | > 5520 | > 115% | NA | 81918.4 | NA | 13188.2
* LDA has adequate internal resources to meet the reliability criterion.
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation/Limiting Facility
MAAC | Thermal / Sandy Spring - High Ridge 230 kV
EMAAC | Voltage / Low voltage magnitude at Cochranville 230 kV
SWMAAC | Thermal / Conastone - Northwest '2322' 230 kV
PS | Thermal / Roseland - Cedar Grove 230 kV
PSNORTH | Thermal / Roseland - Cedar Grove 230 kV
DPLSOUTH | Thermal / Red Lion - Cedar Creek 230 kV
PEPCO | Thermal / Burches Hill -Talbert '068' 230 kV
ATSI | Thermal / Tidd - Collier 345 kV
ATSI-CLEVELAND | Turned off all internal generation
COMED | Thermal / Loretto - Wilton 345 kV Blue line
BGE | Thermal / Pumphrey 230/115 kV transformer
PL | Thermal / Wescoville 500/138 kV transformer

## Net CONE
RPM CONE and E&AS Values for 2018/2019 Base Residual Auction
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price / (1 - Pool-Wide Average EFORd)
Pool-Wide Average EFORd for 2018/2019 including OMC outages |  |  |  | 6.35%
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, ComEd, Dayton, DEOK, Dominion, Duquesne (DLCo), EKPC
CONE Area 4: MetEd, Penelec, PPL
Zone/LDA | 2018/2019 BRA CONE: Levelized Revenue Requirement, $/MW-Year | Gross CONE, $/MW-Day, UCAP Price | Historic (2012-2014) Net Energy Revenue Offset, $/MW-Year | Ancillary Services Offset, $/MW-Year per Tariff | Net CONE, $/MW-Day, ICAP Price | Net CONE, $/MW-Day, UCAP Price | VRR Curve Point (a) UCAP Price, $/MW-Day * | LDA Modeled with VRR Curve
CONE Area 1 | 132200 | 386.75
AE |  | 386.75 | 30237.69 | 2199 | 273.3241 | 291.86
DPL |  | 386.75 | 41700.87 | 2199 | 241.9182 | 258.32 | 387.48 | DPL SOUTH
JCPL |  | 386.75 | 35116.56 | 2199 | 259.9574 | 277.58
PE |  | 386.75 | 31570.45 | 2199 | 269.6727 | 287.96
PSEG |  | 386.75 | 28139.67 | 2199 | 279.0721 | 297.99 | 446.99 | PS, PSEG NORTH
RECO |  | 386.75 | 29093.82 | 2199 | 276.458 | 295.2
EMAAC |  |  |  |  | 266.73 | 284.82 | 427.23 | EMAAC
CONE Area 2 | 130300 | 381.19
BGE |  | 381.19 | 47570.74 | 2199 | 220.6308 | 235.59 | 381.19 | BGE
PEPCO |  | 381.19 | 42390.95 | 2199 | 234.8221 | 250.74 | 381.19 | PEPCO
SWMAAC |  |  |  |  | 227.73 | 243.17 | 381.19 | SWMAAC
CONE Area 4 | 130300 | 381.19
METED |  | 381.19 | 31279.76 | 2199 | 265.2637 | 283.25
PENELEC |  | 381.19 | 51175.41 | 2199 | 210.755 | 225.05
PPL |  | 381.19 | 30751.95 | 2199 | 266.7097 | 284.79 | 427.19 | PPL
MAAC |  | 384.22 |  |  | 254.42 | 271.67 | 407.51 | MAAC
CONE Area 3 | 128900 | 377.1
AEP |  |  | 27932.34 | 2199 | 270.5991 | 288.95
APS |  |  | 36061.54 | 2199 | 248.3273 | 265.17
ATSI |  |  | 33819.55 | 2199 | 254.4697 | 271.72 | 407.58 | ATSI, ATSI CLEVELAND
COMED |  |  | 17220.33 | 2199 | 299.947 | 320.29 | 480.44 | COMED
DAYTON |  |  | 30598.15 | 2199 | 263.2955 | 281.15
DEOK |  |  | 26214.06 | 2199 | 275.3067 | 293.97
DLCO |  |  | 28704.07 | 2199 | 268.4847 | 286.69
DOM |  |  | 27255.94 | 2199 | 272.4522 | 290.93
EKPC |  |  | 46685.96 | 2199 | 219.2193 | 234.08
RTO | 130425 | 381.56 | 25483.54 | 2199 | 281.4862 | 300.57 | 450.86 | RTO
* VRR Curve Point (a) UCAP Price is the higher of 1.5 Net CONE or Gross CONE.

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2018/2019 Model
Upgrade ID | Description | Transmission Owner
b1813.3 | Build approximately 21 miles new 230 kV Acahela – Pocono line | PPL
b2269 | Rebuild approximately 23.7 miles of the Susquehanna - Jenkins 230kV circuit. This replaces a temporary SPS that is already planned to mitigate the violation until this solution is implemented | PPL
b2371 | Install 75 MVAR capacitor at the Erie East 230 kV substation | PENELEC
b2373 | Build a 2nd Loudoun - Brambleton 500 kV line within the existing ROW. The Loudoun - Brambleton 230 kV line will be relocated as an underbuild on the new 500 kV line | Dominion
b2436 | PSEG Northern NJ 345 kV Project | PSEG
b2436.10 | Convert the Bergen - Marion 138 kV path to double circuit 345 kV and associated substation upgrades | PSEG
b2436.21 | Convert the Marion - Bayonne "L" 138 kV circuit to 345 kV and any associated substation upgrades | PSEG
b2436.22 | Convert the Marion - Bayonne "C" 138 kV circuit to 345 kV and any associated substation upgrades | PSEG
b2436.50 | Construct a new North Ave - Airport 345 kV circuit and any associated substation upgrades | PSEG
b2436.60 | Relocate the underground portion of North Ave - Linden "T" 138 kV circuit to Bayway, convert it to 345 kV, and any associated substation upgrades | PSEG
b2436.70 | Construct a new Airport - Bayway 345 kV circuit and any associated substation upgrades | PSEG
b2436.81 | Relocate the overhead portion of Linden - North Ave "T" 138 kV circuit to Bayway, convert it to 345 kV, and any associated substation upgrades | PSEG
b2436.83 | Convert the Bayway - Linden "Z" 138 kV circuit to 345 kV and any associated substation upgrades | PSEG
b2436.90 | Relocate Farragut - Hudson "B" and "C" 345 kV circuits to Marion 345 kV and any associated substation upgrades | PSEG
b2436.91 | Relocate the Hudson 2 generation to inject into the 345 kV at Marion and any associated upgrades | PSEG
b2437.10 | New Bergen 345/230 kV transformer and any associated substation upgrades | PSEG
b2437.11 | New Bergen 345/138 kV transformer #1 and any associated substation upgrades | PSEG
b2437.20 | New Bayway 345/138 kV transformer #1 and any associated substation upgrades | PSEG
b2437.21 | New Bayway 345/138 kV transformer #2 and any associated substation upgrades | PSEG
b2437.30 | New Linden 345/230 kV transformer and any associated substation upgrades | PSEG
b2441 | Install +250/-100 MVAR SVC at the Erie South 230 kV station | PENELEC
b2443 | Construct new underground 230 kV line from Glebe to Station C, rebuild Glebe Substation, construct 230 kV high-side bus at Station C with option to install 800 MVA PAR | Dominion
b2443.3 | Glebe - Station C PAR | Dominion
b2449 | Rebuild the 7-mile 345 kV line between Meadow Lake and Reynolds 345 kV stations | AEP
b2461 | Wreck and rebuild existing Remington CT - Warrrenton 230 kV (approx. 12 miles) as a double-circuit 230 kV line | Dominion
b2471 | Replace Midlothian 500 kV breaker 563T576 and motor operated switches with 3 breaker 500 kV ring bus. Terminate Lines #563 Carson - Midlothian, #576 Midlothian - North Anna, Transformer #2 in new ring | Dominion
b2479 | New Orchard - Cardiff 230 kV line (remove, rebuild and reconfigure existing 138 kV line) and associated substation upgrades, environmental work | AEC
Key Transmission Upgrades included for 2017/2018 model but not included for 2018/2019 model
Upgrade ID | Description | Transmission Owner
None

## Base Capacity Constraints
2018/2019 Demand Rresource Constraints
Forecast Pool Requirement | 1.0835
Pool-Wide Average EFORd for 2018/2019 including OMC outages | 6.35%
Demand Resource Factor | NA
Quantities are in Unforced Capacity Megawatts | PJM Region | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL
Reliability Requirement adjusted for FRR | 160607.4 | 69853.6 | 38535.2 | 16211.6 | 12416.1 | 6379.1 | 3149.7 | 8181.2 | 16048.1 | 6029.7 | 27704.676 | 8706.7 | 10040.1
Preliminary Peak Load Forecast | 161418.4 | 58943 | 32213 | 13562 | 10146 | 4963.4 | 2396 | 6500 | 12924 | 4444.6 | 22959 | 7062 | 7287
FRR Peak Load | 13188.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343.3 | 0 | 0
Peak Load Forecast adjusted for FRR | 148230.2 | 58943 | 32213 | 13562 | 10146 | 4963.4 | 2396 | 6500 | 12924 | 4444.6 | 22615.7 | 7062 | 7287
Base Capacity DR Constraint
Percent of Preliminary Forecast Peak Load | 8.3% | 18.4% | 16.2% | 7.4% | 11.7% | 4.5% | 10.4% | 7.1% | 15.2% | 15.5% | 13.3% | 8.8% | 13%
Base Capacity DR Constraint as Unforced Capacity | 13330.416 | 11751.1123 | 5654.2513 | 1087.3876 | 1286.2033 | 242.003 | 269.9909 | 500.0352 | 2128.4794 | 746.4372 | 3259.0468 | 673.3476 | 1026.4104
Base Capacity Constraint
Percent of Preliminary Forecast Peak Load | 18.9% | 30.3% | 44.4% | 22.2% | 50.7% | 38.8% | 19.5% | 23.5% | 28.7% | 24.6% | 52.5% | 22.1% | 16.8%
Base Capacity Constraint as Unforced Capacity | 26236.5231 | 16725.6362 | 13394.3587 | 2819.5805 | 4817.3766 | 1803.511 | 437.5515 | 1430.5038 | 3473.6546 | 1023.9425 | 11119.2916 | 1461.5974 | 1146.4783
DR Constraints for FRR Load (ICAP as % of peak load)
Base Capacity DR Constraint | 8.3% | 18.4% | 16.2% | 7.4% | 11.7% | 4.5% | 10.4% | 7.1% | 15.2% | 15.5% | 13.3% | 8.8% | 13%
Base Capacity Constraint | 18.9% | 30.3% | 44.4% | 22.2% | 50.7% | 38.8% | 19.5% | 23.5% | 28.7% | 24.6% | 52.5% | 22.1% | 16.8%

## Cap Import Limits
2018/2019 Capacity Import Limits in Megawatts
External Source Zone
| Simultaneous | North | West 1 | West 2 | South 1 | South 2
First Contingency Total Transfer Capability (FCTTC) | 7707 | 168 | 1276 | 5193 | 670 | 362
Capacity Benefit Margin (CBM) | 3500 | 76 | 579 | 2358 | 304 | 164
Confirmed NEDTS* | 11740 | 188 | 3097 | 5433 | 2196 | 826
Approved CIL Exception Requests* | 6029.3 | 0 | 2016 | 3139 | 603.3 | 271
Capacity Import Limit (CIL) for use in BRA ** | 0 | 92 | 0 | 0 | 0 | 0
Notes:
* Updated on 8/6/2015 to reflect approved CIL exception requests and confirmed NEDTS values as of 8/4/2015.
** In addition to ensuring that the CIL used in the auction plus the granted exceptions to not exceed the granted Network External Designated (NED) transmission service less the CBM, PJM is also ensuring that the CIL used in the auction plus the granted exceptions does not exceed the FCTTC less the CBM. Because the simultaneous limit is zero, no imports will be cleared in the auction other than those for which a CIL exception was granted.

## Credit Rates
2018-2019 Pre-Clearing BRA Credit Rates
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL
Net CONE, $/MW-Day (UCAP Price) | 300.57 | 271.67 | 284.82 | 243.17 | 297.99 | 297.99 | 258.32 | 250.74 | 271.72 | 271.72 | 320.29 | 235.59 | 284.79
Base Capacity DR/EE Resources Credit Rate, $/MW | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42
Base Capacity Resources Credit Rate, $/MW | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42 | 32912.42
Capacity Performance Resources Credit Rate, $/MW | 54854.03 | 49579.78 | 51979.65 | 44378.53 | 54383.18 | 54383.18 | 47143.4 | 45760.05 | 49588.9 | 49588.9 | 58452.93 | 42995.18 | 51974.18
2018-2019 Post-Clearing BRA Credit Rates
Pool-Wide Average EFORd | 6.35%
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL
Net CONE, $/MW-Day (UCAP Price) | 300.57 | 271.67 | 284.82 | 243.17 | 297.99 | 297.99 | 258.32 | 250.74 | 271.72 | 271.72 | 320.29 | 235.59 | 284.79
Base Capacity DR/EE Resources
Resource Clearing Price, $/MW-Day | 149.98 | 149.98 | 210.63 | 59.95 | 210.63 | 210.63 | 210.63 | 41.09 | 149.98 | 149.98 | 200.21 | 59.95 | 75
Post-Clearing Credit Rate, $/MW | 10948.54 | 10948.54 | 15375.99 | 7300 | 15375.99 | 15375.99 | 15375.99 | 7300 | 10948.54 | 10948.54 | 14615.33 | 7300 | 7300
Base Capacity Resources
Resource Clearing Price, $/MW-Day | 149.98 | 149.98 | 210.63 | 149.98 | 210.63 | 210.63 | 210.63 | 149.98 | 149.98 | 149.98 | 200.21 | 149.98 | 75
Post-Clearing Credit Rate, $/MW | 10948.54 | 10948.54 | 15375.99 | 10948.54 | 15375.99 | 15375.99 | 15375.99 | 10948.54 | 10948.54 | 10948.54 | 14615.33 | 10948.54 | 7300
Capacity Performance Resources
Resource Clearing Price, $/MW-Day | 164.77 | 164.77 | 225.42 | 164.77 | 225.42 | 225.42 | 225.42 | 164.77 | 164.77 | 164.77 | 215 | 164.77 | 164.77
Post-Clearing Credit Rate, $/MW | 54854.03 | 49579.78 | 51979.65 | 44378.53 | 54383.18 | 54383.18 | 47143.4 | 45760.05 | 49588.9 | 49588.9 | 58452.93 | 42995.18 | 51974.18