## Notes
Thermal analysis column headings
Column Heading | Title | Description
Reserved(FG# assinged by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Fr Bus | From Bus Number | PSSE model bus number corresponding to the FROM bus of a facility identified as a potential violation
Fr Name | From Bus Name | PSSE model bus name corresponding to the FROM bus of a facility identified as a potential violation
To Bus | To Bus Number | PSSE model bus number corresponding to the TO bus of a facility identified as a potential violation
To Name | To Bus Name | PSSE model bus name corresponding to the TO bus of a facility identified as a potential violation
Tert Bus | Tertiary Bus Number | PSSE model bus number corresponding to the tertiary bus of a facility identified as a potential violation
Tert Name | Tertiary Bus Name | PSSE model bus name corresponding to the tertiary bus of a facility identified as a potential violation
CKT | Circuit | Circuit number of identified potential violation
KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Rating | Facility Rating | Applicable thermal rating (MVA) of facility
DC Ld(%) | Direct Current Loading percentage | Percentage above Line Rating determined from DC testing
AC Ld(%) | Alternating Current Loading percentage | Percentage above Line Rating determined from AC testing
Cont Type | Contingency Type | N-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Conductor Rating (MVA) | Conductor Rating | Normal/Long Term Emergency/Short Term Emergency/Load Dump ratings of conductor
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Magnitude analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Upper/Lower Limit | High/Low Voltage Limit (P.U.) | Threshold of Per Unit High/Low voltage, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Type | Contingency 2 Type | N-1-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower)
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Drop analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Vdrop (%) | Voltage Drop | The percentage that the voltage has dropped as a result of the contingency
Delta Voltage Limit | Voltage Drop Limit | Threshold of percentage drop, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Short Circuit analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | Short Circuit model bus number where breaker is located
Bus Name | Bus Name | Aspen bus name and voltage where breaker is located
Bus KV | BUS Voltage | Nominal BUS voltage
Area | Area Number | Area number of bus identified as potential violation
Breaker | Breaker Name | Breaker name as given by Transmission Owner
Rating Type | Type of Breaker | Symmetrical (S) or Total (T) rated type of breaker
DUTY_P | Duty Percentage | The percentage of the asymmetrical fault current divided by breaker capacity
DUTY_A | Asymmetrical Fault Current | The combination of the symmetrical component and the direct current component of the current.
BKR_CAPA (A) | Breaker Capacity | Breaker’s derated interrupting capability, (A)
Pre-fault Voltage (KV) | Pre-fault KV | Voltage on the bus prior to fault event
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Stability analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis dynamics case info. | Analysis dynamics case info. | Dynamics case year, loading condition, MMWG Series. For example, MMWG 2018 Series 2023 SLL case.
Stability issue category | Stability issue category | Stability issue category: transient stability or damping or dynamic voltage recovery or voltage ride through
Bus # | Bus number | Bus number of the identified plant or station in the analysis power flow model.
Bus Name | Bus name | Bus name of the identified plant or station in the analysis power flow model.
Area | Area | Area number of the identified plant or station.
Stability Contingency description | Contingency description | Detailed contingency description that causes the identified potential stability issue including sequence and fault clearing times.
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Other analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Facility Name | Facility Name | Facilities such as line, substation, generator, etc.
Violations details | Violations details | TO to describe the details of the violation
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Purpose of FERC FORM 715 VIOLATION SUBMISSIONS:
PJM seeks Transmission Owner (TO) criteria violation submissions on facilities in accordance with Local TO criteria. This would also include violations which are not power flow violations of criteria.
Criteria applied by Transmission Owner:
FERC Form 715 Analysis (Thermal/Voltage Magnitude/Voltage Drop/Short Circuit/Stability/Other)
TERMINOLOGY USED IN TEMPLATE:
Descriptions of the column headings used in each Excel tab are provided below.
ANALYSIS PROCEDURE:
Transmission Owners are expected to identify FERC Form 715 violations. All violations are to be captured and recorded in the applicable Excel tab. Please use the corresponding tabs based on the type of violation below:
  * FERC Form 715 Thermal tab should be used to enter thermal violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Magnitude tab should be used to enter voltage magnitude violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Drop tab should be used to enter voltage drop/rise violations associated with FERC Form 715 criteria
  * FERC Form 715 Short Circuit tab should be used to enter short circuit violations associated with FERC Form 715 criteria
  * FERC Form 715 Stability tab should be used to enter stability violations associated with FERC Form 715 criteria
  * FERC Form 715 Other tab should be used to enter violations associated with FERC Form 715 criteria which can not be included in the other tabs
TRANSMISSION OWNER CRITERIA:
In addition to the NERC and PJM criteria included in RTEP studies, PJM also considers Transmission Owner specific criteria. Individual TO criteria can be found at the following link:
http://pjm.com/planning/planning-criteria/to-planning-criteria.aspx

## FERC Form 715 Thermal
Reserved(FG# assigned by PJM) | Analysis Case | Fr Bus | Fr Name | To Bus | To Name | Tert Bus | Tert Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Cont 1 Name | Cont 2 Name | Conductor Rating (MVA) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
AEP -T1 | 2026 RTEP Light Load case | 244200 | 05LOVEDALE | 244213 | 05SEWAGEPL |  |  | 1 | 35 | 205 | 30 |  | 101.99 | N-1-1 | 242633 05EDENSR 138 242849 05W.KINGSPT1 138 1_SRT-A | AEP_P1-2_#5686_171_SRT-A | 30/30/43/43 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T2 | 2026 RTEP Light Load case | 244213 | 05SEWAGEPL | 244219 | 05WKINGSP |  |  | 1 | 35 | 205 | 30 |  | 101.63 | N-1-1 | 242633 05EDENSR 138 242849 05W.KINGSPT1 138 1_SRT-A | AEP_P1-2_#5686_171_SRT-A | 30/30/42/42 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T3 | 2026 RTEP Light Load case | 244219 | 05WKINGSP | 244218 | 05WKINGSEQ |  |  | 1 | 35/999 | 205 | 60 |  | 121.78 | N-1-1 | 242633 05EDENSR 138 242849 05W.KINGSPT1 138 1_SRT-A | AEP_P1-2_#5686_171_SRT-A | N/A | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T4 | 2026 RTEP Light Load case | 244219 | 05WKINGSP | 244218 | 05WKINGSEQ |  |  | 1 | 35/999 | 205 | 60 |  | 117.86 | N-1-1 | 242633 05EDENSR 138 242678 05INDIAS 138 1_SRT-A | AEP_P1-2_#5686_171_SRT-A | N/A | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T5 | 2026 RTEP Light Load case | 244219 | 05WKINGSP | 244218 | 05WKINGSEQ |  |  | 1 | 35/999 | 205 | 60 |  | 106.46 | N-1-1 | 242678 05INDIAS 138 242732 05NBRSTL 138 1_SRT-A | AEP_P1-2_#5686_171_SRT-A | N/A | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T6 | 2026 RTEP Light Load case | 244471 | 05BECCO | 244517 | 05SLAGLE |  |  | 1 | 46 | 205 | 23 |  | 124.3 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | 23/23/32/32 | Yes | Part 4: Thermal Limits |  | Overlap with AEP-2020-AP044
AEP -T7 | 2026 RTEP Light Load case | 244482 | 05DEHUE | 244509 | 05PINE GAP |  |  | 1 | 46 | 205 | 27 |  | 109.54 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | 27/27/34/34 | Yes | Part 4: Thermal Limits |  | Overlap with AEP-2020-AP044
AEP -T8 | 2026 RTEP Light Load case | 244482 | 05DEHUE | 244517 | 05SLAGLE |  |  | 1 | 46 | 205 | 23 |  | 127.54 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | 23/23/32/32 | Yes | Part 4: Thermal Limits |  | Overlap with AEP-2020-AP044
AEP -T9 | 2026 RTEP Light Load case | 244715 | 05HURRICAN | 244722 | 05MILTON |  |  | 1 | 69 | 205 | 40 |  | 101.02 | N-1-1 | 242622 05DARRH2 138 242866 05MERRIT 138 1_SRT-A | AEP_P1-2_#6059_5683_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Potential M-3 need identified, awaiting field and engineering analysis
AEP -T10 | 2026 RTEP Light Load case | 244715 | 05HURRICAN | 244732 | 05TEAYS |  |  | 1 | 69 | 205 | 40 |  | 116.36 | N-1-1 | 242622 05DARRH2 138 242866 05MERRIT 138 1_SRT-A | AEP_P1-2_#6059_5683_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Potential M-3 need identified, awaiting field and engineering analysis
AEP -T11 | 2026 RTEP Light Load case | 244715 | 05HURRICAN | 244732 | 05TEAYS |  |  | 1 | 69 | 205 | 40 |  | 100.03 | N-1-1 | 242573 05CABELL 138 242866 05MERRIT 138 1_SRT-A | AEP_P1-2_#6059_5683_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Potential M-3 need identified, awaiting field and engineering analysis
AEP -T12 | 2026 RTEP Light Load case | 244732 | 05TEAYS | 247774 | 05PUTNAM VLG |  |  | 1 | 69 | 205 | 50 |  | 105.66 | N-1-1 | 242622 05DARRH2 138 242866 05MERRIT 138 1_SRT-A | AEP_P1-2_#6059_5683_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T13 | 2026 RTEP Light Load case | 244863 | 05BANCROFT | 244873 | 05WINFIELD |  |  | 1 | 69 | 205 | 50 |  | 100.06 | N-1-1 | 242622 05DARRH2 138 242866 05MERRIT 138 1_SRT-A | AEP_P1-2_#6059_5683_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T14 | 2026 RTEP Light Load case | 244873 | 05WINFIELD | 247774 | 05PUTNAM VLG |  |  | 1 | 69 | 205 | 50 |  | 105.67 | N-1-1 | 242622 05DARRH2 138 242866 05MERRIT 138 1_SRT-A | AEP_P1-2_#6059_5683_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T15 | 2026 RTEP Light Load case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 105.77 | N-1-1 | 245983 05GRISTMILL 138 245994 05GEMINI 138 1_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T16 | 2026 RTEP Light Load case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 105.77 | N-1-1 | AEP_P1-2_#14698_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T17 | 2026 RTEP Light Load case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 105.68 | N-1-1 | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T18 | 2026 RTEP Light Load case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 100.77 | N-1-1 | 243122 05SW LIM 138 243152 05WMOULT 138 1_SRT-A | AEP_P1-2_#14698_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T19 | 2026 RTEP Light Load case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 100.77 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-2_#14698_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T20 | 2026 RTEP Light Load case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 100.7 | N-1-1 | 243122 05SW LIM 138 243152 05WMOULT 138 1_SRT-A | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T21 | 2026 RTEP Light Load case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 100.7 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T22 | 2026 RTEP Light Load case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 105.28 | N-1-1 | 245983 05GRISTMILL 138 245994 05GEMINI 138 1_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T23 | 2026 RTEP Light Load case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 105.28 | N-1-1 | AEP_P1-2_#14698_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T24 | 2026 RTEP Light Load case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 105.19 | N-1-1 | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T25 | 2026 RTEP Light Load case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 100.25 | N-1-1 | 243122 05SW LIM 138 243152 05WMOULT 138 1_SRT-A | AEP_P1-2_#14698_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T26 | 2026 RTEP Light Load case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 100.25 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-2_#14698_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T27 | 2026 RTEP Light Load case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 100.18 | N-1-1 | 243122 05SW LIM 138 243152 05WMOULT 138 1_SRT-A | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T28 | 2026 RTEP Light Load case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 100.18 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T29 | 2026 RTEP Summer case | 243676 | 05BELLF2 | 244660 | 05BELLEFNT |  |  | 3 | 138/69 | 205 | 168 |  | 100.34 | N-1-1 | AEP_P1-2_#6051_2845_SRT-A | AEP_P1-3_#11483_05BELLF1 138_2_SRT-A | N/A | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T30 | 2026 RTEP Summer case | 243676 | 05BELLF2 | 244660 | 05BELLEFNT |  |  | 3 | 138/69 | 205 | 168 |  | 100.24 | N-1-1 | AEP_P1-3_#11466_05KENOVA 138_8_SRT-A | AEP_P1-3_#11483_05BELLF1 138_2_SRT-A | N/A | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T31 | 2026 RTEP Summer case | 243676 | 05BELLF2 | 244660 | 05BELLEFNT |  |  | 3 | 138/69 | 205 | 168 |  | 100.15 | N-1-1 | AEP_P1-3_#11483_05BELLF1 138_2_SRT-A | AEP_P1-2_#6051_2845_SRT-A | N/A | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T32 | 2026 RTEP Summer case | 243676 | 05BELLF2 | 244660 | 05BELLEFNT |  |  | 3 | 138/69 | 205 | 168 |  | 100.24 | N-1-1 | AEP_P1-3_#11483_05BELLF1 138_2_SRT-A | AEP_P1-3_#11466_05KENOVA 138_8_SRT-A | N/A | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T33 | 2026 RTEP Summer case | 244030 | 05CAMPBEL1 | 244073 | 05ROANOKE |  |  | 1 | 69 | 205 | 46 |  | 125.62 | N-1-1 | AEP_P1-2_#11307_334_SRT-A | AEP_P1-3_#12037_05HUNTCT 138_1_SRT-A | 46/46/65/65 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T34 | 2026 RTEP Summer case | 244030 | 05CAMPBEL1 | 244073 | 05ROANOKE |  |  | 1 | 69 | 205 | 46 |  | 125.63 | N-1-1 | AEP_P1-3_#12037_05HUNTCT 138_1_SRT-A | AEP_P1-2_#11307_334_SRT-A | 46/46/65/65 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T35 | 2026 RTEP Summer case | 244067 | 05MONTERAV | 244097 | 05HUNTCRT2 |  |  | 1 | 69 | 205 | 90 |  | 102.55 | N-1-1 | AEP_P1-2_#14669_SRT-A | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | 125/125/158/158 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T36 | 2026 RTEP Summer case | 244067 | 05MONTERAV | 244097 | 05HUNTCRT2 |  |  | 1 | 69 | 205 | 90 |  | 102.73 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | 125/125/158/158 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T37 | 2026 RTEP Summer case | 244685 | 0547TH ST | 244720 | 05KENOVA H |  |  | 1 | 69 | 205 | 90 |  | 100 | N-1-1 | AEP_P1-2_#5972_194_SRT-A | AEP_P1-2_#14753_SRT-A | 79/90/100/109 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Limited by one span of 4/0 CU conductor and risers. Potential M-3 need identified, awaiting field and engineering analysis
AEP -T38 | 2026 RTEP Summer case | 244685 | 0547TH ST | 244720 | 05KENOVA H |  |  | 1 | 69 | 205 | 90 |  | 100 | N-1-1 | AEP_P1-2_#14753_SRT-A | AEP_P1-2_#5972_194_SRT-A | 79/90/100/109 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Limited by one span of 4/0 CU conductor and risers. Potential M-3 need identified, awaiting field and engineering analysis
AEP -T39 | 2026 RTEP Summer case | 245478 | 05LEATHERW | 245489 | 05BROOMRD |  |  | 1 | 69 | 205 | 46 |  | 107.54 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2_SRT-A | AEP_P1-2_#12210_16598_SRT-A | 46/46/60/60 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2021-OH006 and b3274
AEP -T40 | 2026 RTEP Summer case | 245478 | 05LEATHERW | 245489 | 05BROOMRD |  |  | 1 | 69 | 205 | 46 |  | 104.46 | N-1-1 | AEP_P1-2_#12210_16598_SRT-A | AEP_P1-3_#11754_05WCAMBR 138_2_SRT-A | 46/46/60/60 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2021-OH006 and b3274
AEP -T41 | 2026 RTEP Summer case | 245489 | 05BROOMRD | 245493 | 05SALTFRKZ |  |  | 1 | 69 | 205 | 46 |  | 121.84 | N-1-1 | AEP_P1-2_#12210_16598_SRT-A | AEP_P1-3_#11754_05WCAMBR 138_2_SRT-A | 46/46/60/60 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2021-OH006 and b3274
AEP -T42 | 2026 RTEP Summer case | 245489 | 05BROOMRD | 245493 | 05SALTFRKZ |  |  | 1 | 69 | 205 | 46 |  | 115.73 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2_SRT-A | AEP_P1-2_#12210_16598_SRT-A | 46/46/60/60 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2021-OH006 and b3274
AEP -T43 | 2026 RTEP Summer case | 246184 | 05BRIMFLD8 | 246216 | 05PHILIPSZ |  |  | 1 | 69 | 205 | 50 |  | 106.8 | N-1-1 | AEP_P1-2_#5656_11838_SRT-A | AEP_P1-2_#7912_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T44 | 2026 RTEP Summer case | 246184 | 05BRIMFLD8 | 246216 | 05PHILIPSZ |  |  | 1 | 69 | 205 | 50 |  | 105.19 | N-1-1 | AEP_P1-2_#7912_SRT-A | AEP_P1-2_#5656_11838_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T45 | 2026 RTEP Summer case | 246216 | 05PHILIPSZ | 246226 | 05ALBION Z |  |  | 1 | 69 | 205 | 50 |  | 107 | N-1-1 | AEP_P1-2_#5656_11838_SRT-A | AEP_P1-2_#7912_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T46 | 2026 RTEP Summer case | 246216 | 05PHILIPSZ | 246226 | 05ALBION Z |  |  | 1 | 69 | 205 | 50 |  | 105.4 | N-1-1 | AEP_P1-2_#7912_SRT-A | AEP_P1-2_#5656_11838_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T47 | 2026 RTEP Summer case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 128.13 | N-1-1 | AEP_P1-2_#14698_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T48 | 2026 RTEP Summer case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 128.03 | N-1-1 | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T49 | 2026 RTEP Summer case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 123.72 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-2_#14698_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T50 | 2026 RTEP Summer case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 123.61 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T51 | 2026 RTEP Summer case | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 111.73 | N-1-1 | AEP_P1-2_#11795_904_SRT-A | AEP_P1-3_#11848_05HAVILAND2 138_4_SRT-A | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T52 | 2026 RTEP Summer case | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 111.73 | N-1-1 | AEP_P1-3_#11848_05HAVILAND2 138_4_SRT-A | AEP_P1-2_#11795_904_SRT-A | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T53 | 2026 RTEP Summer case | 245871 | 05DELPHOS | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 50 |  | 110.47 | N-1-1 | AEP_P1-2_#11795_904_SRT-A | AEP_P1-3_#11848_05HAVILAND2 138_4_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T54 | 2026 RTEP Summer case | 245871 | 05DELPHOS | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 50 |  | 110.47 | N-1-1 | AEP_P1-3_#11848_05HAVILAND2 138_4_SRT-A | AEP_P1-2_#11795_904_SRT-A | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T55 | 2026 RTEP Summer case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 118.02 | N-1-1 | AEP_P1-2_#14698_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T56 | 2026 RTEP Summer case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 117.93 | N-1-1 | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T57 | 2026 RTEP Summer case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 113.69 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-2_#14698_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T58 | 2026 RTEP Summer case | 245874 | 05E DELPHO | 247376 | 05ELIDA ROAD |  |  | 1 | 69 | 205 | 40 |  | 113.58 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T59 | 2026 RTEP Summer case | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 101.28 | N-1-1 | AEP_P1-2_#11794_903_SRT-A | AEP_P1-3_#11852_05NDELPH 138_1_SRT-A | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T60 | 2026 RTEP Summer case | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 101.28 | N-1-1 | AEP_P1-3_#12221_05W VAN WR 69.0_SRT-A | AEP_P1-3_#11852_05NDELPH 138_1_SRT-A | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T61 | 2026 RTEP Summer case | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 100.6 | N-1-1 | AEP_P1-3_#11852_05NDELPH 138_1_SRT-A | AEP_P1-2_#11794_903_SRT-A | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T62 | 2026 RTEP Summer case | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 100.6 | N-1-1 | AEP_P1-3_#11852_05NDELPH 138_1_SRT-A | AEP_P1-3_#12221_05W VAN WR 69.0_SRT-A | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T63 | 2026 RTEP Summer case | 243603 | 05ECHO VL SS | 243610 | 05LICK |  |  | 1 | 69 | 205 | 38 |  | 100.12 | N-1-1 | AEP_P1-2_#16427_SRT-A | AEP_P1-2_#5888_597_SRT-A | 75/75/94/94 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T64 | 2026 RTEP Summer case | 243819 | 05N PORTSM | 243826 | 05ORTELCRN |  |  | 1 | 69 | 205 | 34 |  | 120.81 | N-1-1 | AEP_P1-2_#5888_597_SRT-A | AEP_P1-2_#16428_SRT-A | 34/34/42/42 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T65 | 2026 RTEP Summer case | 243819 | 05N PORTSM | 243826 | 05ORTELCRN |  |  | 1 | 69 | 205 | 34 |  | 120.78 | N-1-1 | AEP_P1-2_#16428_SRT-A | AEP_P1-2_#5888_597_SRT-A | 34/34/42/42 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T66 | 2026 RTEP Winter case | 243753 | 05ALLEN | 244010 | 05STANVILLE |  |  | 1 | 46 | 205 | 47 |  | 122.8 | N-1-1 | AEP_P1-2_#5952_17038_SRT-A | AEP_P1-2_#15566_SRT-A | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T67 | 2026 RTEP Winter case | 243753 | 05ALLEN | 244010 | 05STANVILLE |  |  | 1 | 46 | 205 | 47 |  | 125.56 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#5952_17038_SRT-A | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T68 | 2026 RTEP Winter case | 243753 | 05ALLEN | 244010 | 05STANVILLE |  |  | 1 | 46 | 205 | 47 |  | 122.91 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11484_05THELMA 138_1_SRT-A | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T69 | 2026 RTEP Winter case | 243753 | 05ALLEN | 244010 | 05STANVILLE |  |  | 1 | 46 | 205 | 47 |  | 122.84 | N-1-1 | AEP_P1-3_#11484_05THELMA 138_1_SRT-A | AEP_P1-2_#15566_SRT-A | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T70 | 2026 RTEP Winter case | 243811 | 05THELMA | 243663 | 05THELMAEQ |  |  | 1 | 46/999 | 205 | 58 |  | 107.12 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | N/A | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T71 | 2026 RTEP Winter case | 243811 | 05THELMA | 243663 | 05THELMAEQ |  |  | 1 | 46/999 | 205 | 58 |  | 106.25 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | N/A | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T72 | 2026 RTEP Winter case | 243811 | 05THELMA | 243663 | 05THELMAEQ |  |  | 1 | 46/999 | 205 | 58 |  | 107.01 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | N/A | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T73 | 2026 RTEP Winter case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 56 |  | 104.76 | N-1-1 | AEP_P1-2_#14698_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T74 | 2026 RTEP Winter case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 56 |  | 104.7 | N-1-1 | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | AEP_P1-2_#7330_4842_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T75 | 2026 RTEP Winter case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 56 |  | 104.38 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-2_#14698_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T76 | 2026 RTEP Winter case | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 56 |  | 104.32 | N-1-1 | AEP_P1-2_#7330_4842_SRT-A | AEP_P1-3_#14700_05GRISTMILL 138_1_SRT-A | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP -T77 | 2026 RTEP Winter case | 243712 | 05CANNONSB | 244727 | 05S.NEAL |  |  | 1 | 69 | 205 | 95 |  | 100.97 | Bus | AEP_P2-2_#13014_05BELLEFNT 69.0_2_SRT-A |  | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T78 | 2026 RTEP Winter case | 243712 | 05CANNONSB | 244727 | 05S.NEAL |  |  | 1 | 69 | 205 | 95 |  | 103.07 | Breaker | AEP_P4_#13021_05BELLEFNT 69.0_AB_SRT-A |  | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T79 | 2026 RTEP Winter case | 243712 | 05CANNONSB | 244727 | 05S.NEAL |  |  | 1 | 69 | 205 | 95 |  | 102.68 | Breaker | AEP_P4_#13023_05BELLEFNT 69.0_H_SRT-A |  | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T80 | 2026 RTEP Winter case | 243712 | 05CANNONSB | 244727 | 05S.NEAL |  |  | 1 | 69 | 205 | 95 |  | 101.41 | Breaker | AEP_P4_#13015_05BELLEFNT 69.0_G_SRT-A |  | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T81 | 2026 RTEP Winter case | 243712 | 05CANNONSB | 244727 | 05S.NEAL |  |  | 1 | 69 | 205 | 95 |  | 101.02 | Breaker | AEP_P4_#13016_05BELLEFNT 69.0_I_SRT-A |  | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T82 | 2026 RTEP Winter case | 243712 | 05CANNONSB | 244727 | 05S.NEAL |  |  | 1 | 69 | 205 | 95 |  | 100.79 | Breaker | AEP_P4_#13019_05BELLEFNT 69.0_D_SRT-A |  | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP -T83 | 2026 RTEP Winter case | 243712 | 05CANNONSB | 244727 | 05S.NEAL |  |  | 1 | 69 | 205 | 95 |  | 100.23 | Single | 244660 05BELLEFNT 69.0 244670 05HOODSCRK 69.0 1_SRT-A |  | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion & Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.

## FERC Form 715 Voltage Magnitude
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Upper/Lower Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
AEP-VM1 | 2026 RTEP Light Load case | 244526 | 05THREEFRK | 46 | 205 | 0.9671 | 0.798 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM2 | 2026 RTEP Light Load case | 244520 | 05TONEYFRK | 46 | 205 | 0.9692 | 0.8006 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM3 | 2026 RTEP Light Load case | 244541 | 05CYCLONE | 46 | 205 | 0.9692 | 0.8006 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM4 | 2026 RTEP Light Load case | 244505 | 05PARDEE SS | 46 | 205 | 0.9693 | 0.8007 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM5 | 2026 RTEP Light Load case | 244537 | 05CRANEC2 | 46 | 205 | 0.9751 | 0.8076 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM6 | 2026 RTEP Light Load case | 244481 | 05LATROBE | 46 | 205 | 0.9842 | 0.8187 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM7 | 2026 RTEP Light Load case | 244471 | 05BECCO | 46 | 205 | 0.9991 | 0.8367 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM8 | 2026 RTEP Light Load case | 244517 | 05SLAGLE | 46 | 205 | 0.9999 | 0.8478 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM9 | 2026 RTEP Light Load case | 244482 | 05DEHUE | 46 | 205 | 1.0031 | 0.8838 | 1.05/0.92 | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM10 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9849 | 0.7613 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM11 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 0.9838 | 0.7728 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM12 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 0.9934 | 0.7987 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM13 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 0.9888 | 0.8029 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM14 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 0.9876 | 0.8057 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM15 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 0.9884 | 0.8067 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM16 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 0.9934 | 0.8471 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM17 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 0.9952 | 0.8504 | 1.05/0.92 | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM18 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9912 | 0.7746 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM19 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9912 | 0.7831 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM20 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 1.0009 | 0.7861 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM21 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 1.0009 | 0.7948 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM22 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 1.0221 | 0.8121 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM23 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 1.0229 | 0.8162 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM24 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 1.0241 | 0.8189 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM25 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 1.0249 | 0.8199 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM26 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 1.0221 | 0.8211 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM27 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 1.0229 | 0.8252 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM28 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 1.0241 | 0.8279 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM29 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 1.0249 | 0.8289 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM30 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 1.0197 | 0.8595 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM31 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 1.0212 | 0.8627 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM32 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 1.0197 | 0.8678 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM33 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 1.0212 | 0.8709 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM34 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9798 | 0.7766 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM35 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 0.9786 | 0.7883 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM36 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 0.9881 | 0.8148 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM37 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 0.9835 | 0.8189 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM38 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 0.9823 | 0.8217 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM39 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 0.9831 | 0.8226 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM40 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 0.9883 | 0.8619 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM41 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 0.9901 | 0.865 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.

## FERC Form 715 Voltage Drop
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Vdrop(%) | Delta Voltage Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
AEP-VD1 | 2026 RTEP Light Load case | 244526 | 05THREEFRK | 46 | 205 | 0.9671 | 0.798 | 16.904 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD2 | 2026 RTEP Light Load case | 244520 | 05TONEYFRK | 46 | 205 | 0.9692 | 0.8006 | 16.86 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD3 | 2026 RTEP Light Load case | 244541 | 05CYCLONE | 46 | 205 | 0.9692 | 0.8006 | 16.86 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD4 | 2026 RTEP Light Load case | 244505 | 05PARDEE SS | 46 | 205 | 0.9693 | 0.8007 | 16.861 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD5 | 2026 RTEP Light Load case | 244537 | 05CRANEC2 | 46 | 205 | 0.9751 | 0.8076 | 16.746 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD6 | 2026 RTEP Light Load case | 244481 | 05LATROBE | 46 | 205 | 0.9842 | 0.8187 | 16.558 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD7 | 2026 RTEP Light Load case | 244471 | 05BECCO | 46 | 205 | 0.9991 | 0.8367 | 16.239 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD8 | 2026 RTEP Light Load case | 244517 | 05SLAGLE | 46 | 205 | 0.9999 | 0.8478 | 15.208 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD9 | 2026 RTEP Light Load case | 244482 | 05DEHUE | 46 | 205 | 1.0031 | 0.8838 | 11.926 | 8% | N-1-1 | 244516 05SKINFORK 46.0 244526 05THREEFRK 46.0 1_SRT-A | AEP_P1-2_#12061_446_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD10 | 2026 RTEP Summer case | 243617 | 05SLATE | 69 | 205 | 1.0151 | 0.8966 | 11.858 | 8% | N-1-1 | AEP_P1-2_#11561_13999_SRT-A | AEP_P1-3_#14128_05BIERSR 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD11 | 2026 RTEP Summer case | 246705 | 05MILL8 | 69 | 205 | 1.0175 | 0.8992 | 11.833 | 8% | N-1-1 | AEP_P1-2_#11561_13999_SRT-A | AEP_P1-3_#14128_05BIERSR 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD12 | 2026 RTEP Summer case | 243608 | 05LATTAVL8 | 69 | 205 | 1.0042 | 0.9177 | 8.65 | 8% | N-1-1 | AEP_P1-2_#11561_13999_SRT-A | AEP_P1-3_#14128_05BIERSR 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD13 | 2026 RTEP Summer case | 246705 | 05MILL8 | 69 | 205 | 1.0182 | 0.9209 | 9.735 | 8% | N-1-1 | AEP_P1-2_#11562_13998_SRT-A | AEP_P1-3_#14128_05BIERSR 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD14 | 2026 RTEP Summer case | 243617 | 05SLATE | 69 | 205 | 0.9836 | 0.8963 | 8.728 | 8% | N-1-1 | AEP_P1-3_#14128_05BIERSR 138_3_SRT-A | AEP_P1-2_#11561_13999_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD15 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9849 | 0.7613 | 22.36 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD16 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 0.9838 | 0.7728 | 21.1 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD17 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 0.9934 | 0.7987 | 19.47 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD18 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 0.9888 | 0.8029 | 18.59 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD19 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 0.9876 | 0.8057 | 18.19 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD20 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 0.9884 | 0.8067 | 18.17 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD21 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 0.9934 | 0.8471 | 14.63 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD22 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 0.9952 | 0.8504 | 14.48 | 8% | N-1-1 | AEP_P1-2_#12051_357_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD23 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9912 | 0.7746 | 21.66 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD24 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9912 | 0.7831 | 20.81 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD25 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 1.0009 | 0.7861 | 21.48 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD26 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 1.0009 | 0.7948 | 20.61 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD27 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 1.0221 | 0.8121 | 21 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD28 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 1.0229 | 0.8162 | 20.67 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD29 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 1.0241 | 0.8189 | 20.52 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD30 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 1.0249 | 0.8199 | 20.5 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD31 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 1.0221 | 0.8211 | 20.1 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD32 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 1.0229 | 0.8252 | 19.77 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD33 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 1.0241 | 0.8279 | 19.62 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD34 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 1.0249 | 0.8289 | 19.6 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD35 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 1.0197 | 0.8595 | 16.02 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD36 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 1.0212 | 0.8627 | 15.85 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD37 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 1.0197 | 0.8678 | 15.19 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD38 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 1.0212 | 0.8709 | 15.03 | 8% | N-1-1 | AEP_P1-2_#15566_SRT-A | AEP_P1-2_#12051_357_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD39 | 2026 RTEP Winter case | 244616 | 05MCKINNEY | 46 | 205 | 0.9798 | 0.7766 | 20.32 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD40 | 2026 RTEP Winter case | 244626 | 05SALSBURY | 46 | 205 | 0.9786 | 0.7883 | 19.03 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD41 | 2026 RTEP Winter case | 243753 | 05ALLEN | 46 | 205 | 0.9881 | 0.8148 | 17.33 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD42 | 2026 RTEP Winter case | 243754 | 05EPRESTNS | 46 | 205 | 0.9835 | 0.8189 | 16.46 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD43 | 2026 RTEP Winter case | 243758 | 05MIDDLECR | 46 | 205 | 0.9823 | 0.8217 | 16.06 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD44 | 2026 RTEP Winter case | 243759 | 05PRESTNSB | 46 | 205 | 0.9831 | 0.8226 | 16.05 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD45 | 2026 RTEP Winter case | 244608 | 05KENWOOD | 46 | 205 | 0.9883 | 0.8619 | 12.64 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD46 | 2026 RTEP Winter case | 243756 | 05KENWDTAP | 46 | 205 | 0.9901 | 0.865 | 12.51 | 8% | N-1-1 | AEP_P1-3_#11474_05STANVILLE2 138_3_SRT-A | AEP_P1-2_#15566_SRT-A | No | AEP 715 Part 4 Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.

## FERC Form 715 Short Circuit
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | Bus KV | Area | Breaker | Rating Type | DUTY_P | DUTY_A | BKR_CAPA (A) | Pre-fault Voltage (KV) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
AEP-SC1 | 2023 short circuit case | 244660 | 05BELLEFNT 69.kV | 69 |  | I | IEEE - Symmetrical Current | 112.6 | 30398 | 27000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC2 | 2023 short circuit case | 244660 | 05BELLEFNT 69.kV | 69 |  | Z | IEEE - Symmetrical Current | 112 | 30240.5 | 27000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC3 | 2023 short circuit case | 244660 | 05BELLEFNT 69.kV | 69 |  | C | IEEE - Symmetrical Current | 115 | 31046.2 | 27000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC4 | 2023 short circuit case | 244660 | 05BELLEFNT 69.kV | 69 |  | JJ | IEEE - Symmetrical Current | 113.8 | 30719.6 | 27000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC5 | 2023 short circuit case | 244660 | 05BELLEFNT 69.kV | 69 |  | G | IEEE - Symmetrical Current | 106.5 | 28760.8 | 27000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC6 | 2023 short circuit case | 244660 | 05BELLEFNT 69.kV | 69 |  | AB | IEEE - Symmetrical Current | 100.4 | 27107.6 | 27000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC7 | 2023 short circuit case | 246691 | 05BEXLEY 40.kV | 40 |  | 43 | IEEE - Symmetrical Current | 138.1 | 15196.1 | 11000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC8 | 2023 short circuit case | 246691 | 05BEXLEY 40.kV | 40 |  | 42 | IEEE - Symmetrical Current | 132.3 | 14558.3 | 11000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC9 | 2023 short circuit case | 245984 | 05MILLERAV 34.5kV | 34.5 |  | A | IEEE - Symmetrical Current | 105.7 | 8454.1 | 8000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC10 | 2023 short circuit case | 245943 | 05NATRIUM 69.kV | 69 |  | E | IEEE - Symmetrical Current | 110 | 22009.4 | 21000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC11 | 2023 short circuit case | 245943 | 05NATRIUM 69.kV | 69 |  | C | IEEE - Symmetrical Current | 104.8 | 22009.3 | 21000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC12 | 2023 short circuit case | 245943 | 05NATRIUM 69.kV | 69 |  | L | IEEE - Symmetrical Current | 104.8 | 22009.3 | 21000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC13 | 2023 short circuit case | 245840 | 05S SIDE 34.5kV | 34.5 |  | B | IEEE - Symmetrical Current | 112.3 | 15949.3 | 14200 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC14 | 2023 short circuit case | 245840 | 05S SIDE 34.5kV | 34.5 |  | A | IEEE - Symmetrical Current | 106.4 | 15112.1 | 14200 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
AEP-SC15 | 2023 short circuit case | 245640 | 05W END 69.kV | 69 |  | H | IEEE - Symmetrical Current | 102.7 | 20540.4 | 20000 | 1.05 | N | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Stability
Reserved(FG# assigned by PJM) | Analysis dynamics case info | Stability issue category | Bus # | Bus Name | Area | Stability Contingency description | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment

## FERC Form 715 Other
Reserved(FG# assigned by PJM) | Analysis Case | Areas | Facility Name | Violations details | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment