## FERC Form 715 Voltage Drop
Reserved(FG# assigned by PJM) | Bus # | Bus Name | Base kV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base volt | Con Volt | % Vdrop | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
APS-VD45 | 235248 | 01SHINGL | 230 | 201 | 0.92 | 1.05 | AP_P1-2_WP-230-005A_SRT-A | AP_P1-3_WP-230-326T_SRT-A | 1.0146 | 0.8938 | 12.08 | Yes | FirstEnergy Transmission Planning Criteria |  | This violation was posted in 2025 RTEP results. It is reposted to accept window proposals. Note: the required in-service date for the proposed project should be 12/01/2025.
APS-VD46 | 235248 | 01SHINGL | 230 | 201 | 0.92 | 1.05 | AP_P1-3_WP-230-005_SRT-A | AP_P1-3_WP-230-326T_SRT-A | 1.0135 | 0.8946 | 11.89 | Yes | FirstEnergy Transmission Planning Criteria |  | This violation was posted in 2025 RTEP results. It is reposted to accept window proposals. Note: the required in-service date for the proposed project should be 12/01/2025.