## FERC Form 715 Thermal
Reserved(FG# assigned by PJM) | Analysis Case | Fr Bus | Fr Name | To Bus | To Name | Tert Bus | Tert Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Cont 1 Name | Cont 2 Name | Conductor Rating (MVA) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
ATSI-T1 | Sum | 238844 | 02JOHNSO | 239666 | 02REDMAN |  |  | 1 | 69 | 202 | 92 | 101.76 | 102.34 | P2-1 | ATSI_P2-1_OEC-69-002_SRT-A |  | 92 SE | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-T2 | Sum | 239667 | 02WFRD NO+ | 239727 | 02BASF |  |  | 1 | 69 | 202 | 92 | 99.39 | 100.12 | P2-1 | ATSI_P2-1_OEC-69-002_SRT-A |  | 92 SE | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-T3 | Sum | 239666 | 02REDMAN | 239667 | 02WFRD NO+ |  |  | 1 | 69 | 202 | 92 | 99.58 | 100.12 | P2-1 | ATSI_P2-1_OEC-69-002_SRT-A |  | 92 SE | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.

## FERC Form 715 Voltage Magnitude
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Upper/Lower Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
ATSI-VM1 | LL | 238747 | 02GALION | 69 | 202 | 1.0467 | 1.0511 | 0.90 / 1.05 | P1 | AEP_P1-4_05OHIOCT 345_SRT-A |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-VM2 | LL | 239155 | 02W.FREM | 69 | 202 | 1.0484 | 1.0548 | 0.90 / 1.05 | P1 | ATSI_P1-4_TE-345-001_SRT-A |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.