## Thermal
2026 RTEP PJM N-1 Thermal Result (Light Load)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusion | Comments
N1-LLT20 | 999337 | 26SHAWVL 2 | 200726 | 26SHAWVL 2 | 2A | 115/230 | 226/226 | 149 | 104.3624 | 106.12 | Bus | 'PN_P2-2_PN-230-013T_SRT-A' | Transformer rating is the same as basecase model | YES |  | Overlap with EOL: Shawville Bank 2A Transformer
N1-LLT21 | 999337 | 26SHAWVL 2 | 200726 | 26SHAWVL 2 | 2A | 115/230 | 226/226 | 149 | 104.4295 | 105.62 | Line_FB | 'PN_P2-3_PN-230-21DT_SRT-A' | Transformer rating is the same as basecase model | YES |  | Overlap with EOL: Shawville Bank 2A Transformer

## Voltage Magnitude
2026 RTEP PJM N-1 Voltage Magnitude Result (Light Load)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Low/High Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusion | Comment
N1-LLVM1 | 314912 | 8LEXNGTN | 500 | 345 | 0.9908 | 1.0392 | 1.01 | Line_FB | DVP_P4-2: 548T549_SRT-A | YES
N1-LLVM2 | 314912 | 8LEXNGTN | 500 | 345 | 1.0031 | 1.0392 | 1.01 | Single | DVP_P1-2: LN 548_SRT-SL | YES
N1-LLVM3 | 314901 | 8BATH CO | 500 | 345 | 0.9772 | 1.0336 | 1.01 | Line_FB | DVP_P4-2: 548T549_SRT-A | YES
N1-LLVM4 | 314901 | 8BATH CO | 500 | 345 | 0.9841 | 1.0336 | 1.01 | Line_FB | DVP_P4-2: 547T566_SRT-A | YES
N1-LLVM5 | 314901 | 8BATH CO | 500 | 345 | 0.9902 | 1.0336 | 1.01 | Single | DVP_P1-2: LN 548_SRT-SL | YES
N1-LLVM6 | 314901 | 8BATH CO | 500 | 345 | 0.9908 | 1.0336 | 1.01 | Line_FB | DVP_P4-2: H1T548_SRT-SL | YES
N1-LLVM7 | 314901 | 8BATH CO | 500 | 345 | 0.9953 | 1.0336 | 1.01 | Single | DVP_P1-2: LN 547_SRT-SL | YES
N1-LLVM8 | 314901 | 8BATH CO | 500 | 345 | 0.9956 | 1.0336 | 1.01 | Line_FB | DVP_P4-2: 54702_SRT-SL | YES

## Voltage Drop
2026 RTEP PJM N-1 Voltage Drop Result (Light Load)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusion | Comment
N1-LLVD1 | 314912 | 8LEXNGTN | 500 | 345 | 0.9742 | 1.0392 | 6.5 | Line_FB | DVP_P4-2: 548T549_SRT-A | YES
N1-LLVD2 | 314901 | 8BATH CO | 500 | 345 | 0.9597 | 1.0336 | 7.39 | Line_FB | DVP_P4-2: 548T549_SRT-A | YES
N1-LLVD3 | 314901 | 8BATH CO | 500 | 345 | 0.9627 | 1.0336 | 7.09 | Line_FB | DVP_P4-2: 547T566_SRT-A | YES