## Summary
2026 RTEP PJM Generation Deliverability Result (Light Load)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusion | Comment
GD-LL36 | 271908 | LASCO STA; B | 271986 | MAZON ; B | 1 | 138/138 | 222/222 | 230 | 275.53 | 267.58 | 119.80 | 116.34 | 'COMED_P7-1_345-L0101_B-S_+_345-L0102_R-S_SRT-A' | tower | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
GD-LL45 | 999337 | 26SHAWVL 2 | 200726 | 26SHAWVL 2 | 2A | 115/230 | 226/226 | 149 | 160.01 | 162.85 | 107.39 | 109.29 | 'PN_P2-2_PN-230-013T_SRT-A' | bus | Transformer rating is the same as basecase model | Yes |  | Overlap with EOL: Shawville Bank 2A Transformer
GD-LL46 | 999337 | 26SHAWVL 2 | 200726 | 26SHAWVL 2 | 2A | 115/230 | 226/226 | 149 | 160.11 | 162.13 | 107.46 | 108.81 | 'PN_P2-3_PN-230-21DT_SRT-A' | breaker | Transformer rating is the same as basecase model | Yes |  | Overlap with EOL: Shawville Bank 2A Transformer
Note on I4: New Rating is used. Original rating is 223.0