7/8/2021 Update:

- The 2026 Summer GenDeliv Result table is updated. The exclusion from competition language is removed for Flowgates # GD-S13, GD-S14, GD-S15 and GD-S38. The FG # GD-S13, GD-S14, GD-S15 and GD-S38 are eligible for competition.

7/14/2021 Update:

- The AEP FERC Form 715 violation table is updated. The AEP-T9 through AEP-T11 comments are updated as “Potential M-3 need identified, awaiting field and engineering analysis.”

- The DOM FERC Form 715 violation table is updated. Flowgates DOM-VM1 – DOM-VM6, DOM-VM10 – DOM-VM13, DOM-VM26 – DOM-VM31 & DOM-VD1 – DOM-VD8 are no longer valid due to an invalid contingency definition.

7/21/2021 Update:

- Updated the Summer N-1-1 Load Drop tab of 2026 Summer N-1-1_Result_V1.xlsx to include bus numbers and names for the load being lost.

8/5/2021 Update:

- The AEP FERC Form 715 violation table is updated. AEP corrected the ratings for Echo Valley – Lick 69kV line, see “Echo Valley - Lick Summer.idv” and “Echo Valley - Lick Winter.idv”. With the updated ratings, the AEP-T63 is not a violation anymore, there form is removed from the posted results.

- Two voltage drop violations (Flowgates: APS-VD45and APS-VD46) are added to FERC Form 715 APS results.  These two flowgates were posted in 2025 RTEP results. It is reposted to accept window proposals in 2026 RTEP window 1.  Related to these flowgates, there are contingency corrections for the outage of the Shingletown transformer #82, see "CON_update_for_ATSI_(for_all_cases).con"

- The Penelec FERC Form 715 spreadsheet is updated to reflect a new short circuit violations.

- Added a new JCPL FERC Form 715 short circuit violations.

8/24/2021 Update:

- The AEP FERC Form 715 violation table is updated to reflect new short circuit violations (AEP-SC1 – AEP-SC15).

- AEP corrected the short circuit model to remove the Beatty breaker 6W, see “Beatty 6W.CHF”. With the correction, the SC-2 is not a violation anymore, therefor is removed from the posted results.

9/29/2021 Update:

- AEP corrected the short circuit model in the Miller Ave area, see “WesternMarion_not_in_service.CHF”. With the correction, the AEP-SC9 is not a violation anymore, therefor is removed from the posted results.

- First Energy made a correction in Penelec (Yeagertown 46 kV) and as a result the four 46 kV breakers at yeagertown identified for First Energy FERC Form 715 are not overdutied and therefore, will be removed from the list.

- Updated JCPL First Energy FERC Form 715. Added flowgate #s for the JCPL short circuit violations.

- Loading for Flowgates # GD-S14, GD-S15 and GD-S36 changed due to Generation reactivation/deactivation/queue projects status changes. As a result, the flowgates will be excluded from window eligibility, as the circuit is limited by substation equipment.

- AEP corrected the ratings for the Campbell-Roanoke line 69kV line, see “CampbellAve-Roanoke69kV ConductorCorrection(Summer).idv” and “CampbellAve-Roanoke69kV ConductorCorrection(Winter).idv”. With the updated ratings, the Flowgates # AEP-T33 and AEP-T34 are not a violation anymore, there form is removed from the posted results.

- AEP corrected the ratings for the Cannonsburg-South Neal 69kV line, see “Cannonsburg - South Neal WIN MLSE upgrade.idv”. With the updated ratings, the T-77, T-78, T-79, T-80, T-81, T-82, and T-83 are not a violation anymore, there form is removed from the posted results.