## Summary
2026 RTEP Short Circuit Result
Flowgate # | TO | BUS_NO | BUS | BREAKER | RATINGTYPE | Notes | DUTY_P | DUTY_A | BKR_CAPA | PJM Accepting Proposals | Reason for Exclusion | Comments
SC-1 | DUQ | 800098 | CHWK138_Z53 138.kV | Z-53 LF_3 | T | 15000 MVA | 100.3 | 57945.6 | 57744.1 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
SC-2 | AEP | 243469 | 05BEATTY 138.kV | 6W | S | 50kA | 106.9 | 53432.2 | 50000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
SC-3 | AEP | 243529 | 05KENNY 138.kV | 102 | S | 40kA | 102 | 40806.4 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
SC-4 | AEP | 243529 | 05KENNY 138.kV | 106 | S | 40kA | 102 | 40806.4 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
SC-5 | AEP | 243481 | 05CANAL 138.kV | 3 | S | 40kA | 101.4 | 40562.1 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
SC-6 | AEP | 243526 | 05HYATT 138.kV | 101N | S | 50kA | 100.7 | 50335.5 | 50000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion