## Summer GenDeliv
2026 RTEP PJM Generation Deliverability Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
GD-S704 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 164 | 317.1 | 310.7 | 193.34 | 189.46 | DVP_P7-1: LN 2058-2181_SRT-A | Tower | N/A | NO | Pending coordination with external entity | Tie Line to Non PJM facility. Dominion summer emergency rating is 218 MVA and load dump rating is 228 MVA. DEP summer emergency rating is 164 MVA.
GD-S409 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 164 | 190 | 187.4 | 115.85 | 114.26 | DVP_P4-2: 2058T2167_SRT-A | Breaker | N/A | NO | Pending coordination with external entity | Tie Line to Non PJM facility. Dominion summer emergency rating is 218 MVA and load dump rating is 228 MVA. DEP summer emergency rating is 164 MVA.
GD-S419 | 242947 | 05WATERFORD | 242940 | 05MUSKNG | 1 | 345 | 205 | 1318 | 1443.5 | 1437.3 | 109.52 | 109.05 | AEP_P4_#8401_05MUSKNG 345_SA_SRT-SL | Breaker | SN/SE = 2684/2684 | NO | Substation Equipment Exclusion | Overlap with M3 Project AEP-2020-AEP001.
GD-S11 | 314122 | 3SOWEGO | 314112 | 3IND HIL | 1 | 115 | 345 | 168.3 | 168.7 | 181.2 | 100.24 | 107.71 | DVP_P1-3: 6OX-TX#3_SRT-A | Single | Conductor rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Segment overlap with candidate EOL facility - 115kV Line #183 Bristers-Ox (DOM-2021-0038)
GD-S12 | 314085 | 6REMNGCT | 314110 | 6ELK RUN | 1 | 230 | 345 | 984.2 | 1071.2 | 1058.8 | 108.85 | 107.58 | DVP_P1-2: LN 569_SRT-SL | Single | Conductor rating is the same as basecase model | YES |  | Overlap with M3 project DOM-2020-0026
GD-S13 | 200674 | 26TOWANDA | 200677 | 26NO MESHO | 1 | 115 | 226 | 245 | 269 | 262.8 | 109.8 | 107.28 | PN_P1-2_PN-230-013A_SRT-A | Single | Conductor rating is the same as basecase model | YES | Exclusion language removed for the flowgate due to the proximity to other violations in the area
GD-S14 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 515 | 537 | 519 | 104.35 | 100.79 | Base Case | Single | SN/SE = 546/666 | NO | Substation equipment Exclusion | Change in generation (deactivation/reactivation/queue status changes) resulted in the loading to deacreas and as a result, substation equpment replacement will address the violation
GD-S15 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 615 | 650 | 629 | 105.67 | 102.24 | PL_P1-2_001029_SRT-A | Single | SN/SE = 546/666 | NO | Substation equipment Exclusion | Change in generation (deactivation/reactivation/queue status changes) resulted in the loading to deacreas and as a result, substation equpment replacement will address the violation
GD-S429 | 200009 | JUNI | 208005 | JUNI BU2 | 2 | 500/230 | 229 | 814 | 882.3 | 868.6 | 108.39 | 106.71 | PL_P4-2_000140_SRT-A | Breaker | SN/SE = 776/1010 | NO | Substation Equipment Exclusion | Limited by substation conductor
GD-S16 | 314134 | 6CRANES | 314142 | 6STAFORD | 1 | 230 | 345 | 678.7 | 711.2 | 720.8 | 104.8 | 106.21 | DVP_P1-2: LN 568_SRT-SL | Single | Conductor rating is the same as basecase model | YES
GD-S17 | 314110 | 6ELK RUN | 314037 | 6GAINSVL | 1 | 230 | 345 | 984.2 | 1056.4 | 1044 | 107.34 | 106.07 | DVP_P1-2: LN 569_SRT-SL | Single | Conductor rating is the same as basecase model | YES |  | Overlap with M3 project DOM-2020-0026
GD-S436 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 549 | 580.5 | 578.1 | 105.74 | 105.31 | DVP_P4-2: 211T2124_SRT-A | Breaker | Conductor rating is the same as basecase model | YES
GD-S710 | 314582 | 3KELFORD | 314568 | 3EARLEYS | 1 | 115 | 345 | 175 | 179.5 | 182.6 | 102.6 | 104.34 | DVP_P7-1: LN 81-1024_SRT-A | Tower | Conductor rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-S712 | 239289 | 02HAYES | 239290 | 02HAYES | 1 | 345/138 | 202 | 493 | 508.1 | 511.8 | 103.07 | 103.81 | ATSI_P7-1_TE-345-030_SRT-A | Tower | Conductor rating is the same as basecase model | YES
GD-S18 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 449.3 | 464.6 | 463.5 | 103.41 | 103.16 | DVP_P1-2: LN 211_SRT-SL | Single | Conductor rating is the same as basecase model | YES
GD-S19 | 314583 | 6LAKEVEW | 314561 | 6CAROLNA | 1 | 230 | 345 | 375.1 | 385.4 | 386.4 | 102.77 | 103.03 | DVP_P1-2: LN 2201_SRT-A | Single | Conductor rating is the same as basecase model | YES |  | Overlap with M3 project EOL DOM-2021-0025
GD-S444 | 232275 | LORET_69 | 232288 | FRUITLND | 1 | 69 | 235 | 112 | 118.2 | 115 | 105.55 | 102.68 | DPL_P4-2_DP56_SRT-A | Breaker | SN/SE = 105/136 | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-S446 | 235504 | 01RIDGLY | 235484 | 01MESSCK | 1 | 138 | 201 | 268 | 277.5 | 274.2 | 103.53 | 102.31 | AP_P2-3_PE-500-018D_SRT-SL | Breaker | Conductor rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential overlap with Proposal submited for Market Efficiency FG# ME-3
GD-S448 | 235504 | 01RIDGLY | 235484 | 01MESSCK | 1 | 138 | 201 | 268 | 277.4 | 274.1 | 103.49 | 102.27 | AP_P2-3_PE-500-018C_SRT-SL | Breaker | Conductor rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential overlap with Proposal submited for Market Efficiency FG# ME-3
GD-S24 | 237056 | AA2-161 TAP | 235277 | 01YUKON | 1 | 138 | 201 | 365 | 381.3 | 373.2 | 104.46 | 102.25 | AP_P1-2_WP-138-118_SRT-A | Single | Conductor rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-S450 | 242938 | 05MARQUI | 243034 | 05MARQUI | 3 | 345/138 | 205 | 463 | 460.5 | 472.4 | 99.46 | 102.04 | AEP_P4_#6775_05MARQUI 345_D1_SRT-A | Breaker | SN/SE = 501/564 | NO | Substation Equipment Exclusion | Limited by CT
GD-S29 | 237053 | AA2-161 TAP | 235277 | 01YUKON | 1 | 138 | 201 | 365 | 380.1 | 372.3 | 104.13 | 102 | AP_P1-2_WP-138-120_SRT-A | Single | Conductor rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-S465 | 314902 | 8CARSON | 314282 | 6CARSON | 1 | 500/230 | 345 | 1039.7 | 1065.2 | 1055 | 102.45 | 101.47 | DVP_P4-2: 562T563_SRT-A | Breaker | Transformer rating is the same as basecase model | YES |  | There is a 2nd transformer at the station which may be placed in service to relieve the overload but may also cause additional violations.
GD-S30 | 314749 | 6CHARLVL | 314772 | 6PROFFIT | 1 | 230 | 345 | 550.8 | 566.9 | 558.1 | 102.91 | 101.31 | DVP_P1-2: LN 553_SRT-SL | Single | Conductor rating is the same as basecase model | YES |  | Overlap with Market Efficiency Window FG# ME-5
GD-S467 | 314134 | 6CRANES | 314142 | 6STAFORD | 1 | 230 | 345 | 830 | 830.9 | 839.9 | 100.11 | 101.2 | DVP_P4-2: 568T574_SRT-SL | Breaker | Conductor rating is the same as basecase model | YES
GD-S715 | 314085 | 6REMNGCT | 314110 | 6ELK RUN | 1 | 230 | 345 | 1204 | 1216.6 | 1214.8 | 101.04 | 100.9 | DVP_P7-1: LN 2039-2040_SRT-SL | Tower | Conductor rating is the same as basecase model | YES |  | Overlap with M3 project DOM-2020-0026
GD-S33 | 314303 | 6HOPEWLL | 314287 | 6CHESTF B | 1 | 230 | 345 | 449.3 | 449.6 | 453.1 | 100.05 | 100.84 | DVP_P1-2: LN 228_SRT-A | Single | Conductor rating is the same as basecase model | YES
GD-S34 | 314130 | 6BRISTER | 314156 | 3BRISTER | 1 | 230/115 | 345 | 224.7 | 207.3 | 225.9 | 92.27 | 100.57 | DVP_P1-3: 6OX-TX#3_SRT-A | Single | SN/SE = 248.7/260.2 | NO | Substation Equipment Exclusion | Limited by wave trap on low side of transformer
GD-S37 | 314085 | 6REMNGCT | 314110 | 6ELK RUN | 1 | 230 | 345 | 984.2 | 996.8 | 987.4 | 101.28 | 100.33 | DVP_P1-2: LN 539_SRT-SL | Single | Conductor rating is the same as basecase model | YES |  | Overlap with M3 project DOM-2020-0026
GD-S485 | 213543 | CROYDON30 | 219102 | BURLING | 1 | 230 | 230/231 | 906 | 910.7 | 908.9 | 100.52 | 100.32 | PECO_P4_EMILI120_SRT-A | Breaker | Conductor rating is the same as basecase model | YES
GD-S38 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 615 | 598 | 579 | 97.22 | 94.13 | PN_P1-2_PN-115-037_SRT-A | Single | SN/SE = 546/666 | NO | Substation equipment Exclusion | Change in generation (deactivation/reactivation/queue status changes) resulted in the loading to deacreas and as a result, substation equpment replacement will address the violation
GD-S674 | 213543 | CROYDON30 | 219102 | BURLING | 1 | 230 | 230/231 | 906 | 910 | 908.9 | 100.44 | 100.32 | PECO_P2-2_EMI138B2_SRT-A | Bus | Conductor rating is the same as basecase model | YES
GD-S486 | 213543 | CROYDON30 | 219102 | BURLING | 1 | 230 | 230/231 | 906 | 911 | 908.9 | 100.55 | 100.32 | PECO_P4_EMILI130_SRT-A | Breaker | Conductor rating is the same as basecase model | YES
GD-S39 | 314282 | 6CARSON | 314285 | 6CHAPARRAL T | 1 | 230 | 345 | 559.3 | 568.9 | 560 | 101.71 | 100.12 | DVP_P1-2: LN 563_SRT-SL | Single | Conductor rating is the same as basecase model | YES |  | Segment overlap with candidate EOL facility - 230kV Line #249 Carson-Locks
GD-S717 | 314085 | 6REMNGCT | 314110 | 6ELK RUN | 1 | 230 | 345 | 1204 | 1220.9 | 1205.3 | 101.4 | 100.11 | DVP_P7-1: LN 569-2101_SRT-SL | Tower | Conductor rating is the same as basecase model | YES |  | Overlap with M3 project DOM-2020-0026
Note
The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO