## N-1-1 Thermal Summer
PJM N-1-1 Thermal Result (2026 Summer)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | Initial AC (%) | SCD AC (%) | Contingency 1 | Contingency 2 | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons For Exclusions | Comments
N2-ST1 | 221136 | CHES.PK1 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 156.0 | 110.06 | 107.52 | 'BG_P1_NEAST_230-3_SRT-A' | 'BG_P1_NEAST_230-2_SRT-A' | SN/SE = 143/186 | NO | Substation Equipment and Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST2 | 221136 | CHES.PK1 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 156.0 | 110.06 | 107.52 | 'BG_P1_NEAST_230-2_SRT-A' | 'BG_P1_NEAST_230-3_SRT-A' | SN/SE = 143/186 | NO | Substation Equipment and Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST3 | 238543 | 02ASH_2 | 239097 | 02SBRNQ3 | 1 | 138/138 | 202/202 | 103.0 | 101.99 | 101.71 | ATSI_P1-2_CEI-138-087_SRT-A' | 'BASE CASE' | SN/SE = 148 /151 | NO | Substation Equipment and Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST4 | 130807 | WESTOVER115 | 200680 | 26LAUREL L | 1 | 115/115 | 102/226 | 128.0 | 107.52 | 100.02 | 'PN_P1-2_PN-230-013A_SRT-A' | 'PL_P1-2_001029_SRT-A' | N/A | NO |  | Tie Line to Non PJM facility. FE's ratingis 134/162 MVA (SN/SE).
N2-ST5 | 130807 | WESTOVER115 | 200680 | 26LAUREL L | 1 | 115/115 | 102/226 | 128.0 | 118.63 | 100.01 | 'PN_P1-2_PN-230-013A_SRT-A' | 'PN_P1-2_PN-115-037_SRT-A' | N/A | NO |  | Tie Line to Non PJM facility. FE's ratingis 134/162 MVA (SN/SE).
Note
The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO

## Summer N-1-1 Volt Mag
PJM N-1-1 Voltage Magnitude Results (2026 Summer)
FG # | Bus # | Bus Name | Base kV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Reasons For Exclusions | Comments
N2-SVM1 | 200908 | 26CHAPMAN+ | 230 | 226 | 0.92 | 1.05 | PN_P1-1_PN-230-035_SRT-A | PN_P1-2_PN-230-033_SRT-A | 1.0278 | 1.0501 | YES
N2-SVM2 | 200701 | 26GROVER | 230 | 226 | 0.92 | 1.05 | PN_P1-1_PN-230-035_SRT-A | PN_P1-2_PN-230-033_SRT-A | 1.029 | 1.0705 | YES
N2-SVM3 | 200701 | 26GROVER | 230 | 226 | 0.92 | 1.05 | PN_P1-2_PN-230-033_SRT-A | PN_P1-1_PN-230-035_SRT-A | 1.0264 | 1.0703 | YES
N2-SVM4 | 200909 | 26LOBO+ | 230 | 226 | 0.92 | 1.05 | PN_P1-1_PN-230-035_SRT-A | PN_P1-2_PN-230-033_SRT-A | 1.0278 | 1.0558 | YES
N2-SVM5 | 200909 | 26LOBO+ | 230 | 226 | 0.92 | 1.05 | PN_P1-2_PN-230-033_SRT-A | PN_P1-1_PN-230-035_SRT-A | 1.0304 | 1.0556 | YES
N2-SVM6 | 200857 | 26MARSHALL | 230 | 226 | 0.92 | 1.05 | PN_P1-1_PN-230-035_SRT-A | PN_P1-2_PN-230-033_SRT-A | 1.0276 | 1.0665 | YES
N2-SVM7 | 200857 | 26MARSHALL | 230 | 226 | 0.92 | 1.05 | PN_P1-2_PN-230-033_SRT-A | PN_P1-1_PN-230-035_SRT-A | 1.0298 | 1.0663 | YES
N2-SVM8 | 204520 | 27ALLEN | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0131 | 0.8612 | YES
N2-SVM9 | 204520 | 27ALLEN | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0057 | 0.8618 | YES
N2-SVM10 | 204526 | 27DILLSBRG | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0096 | 0.8577 | YES
N2-SVM11 | 204526 | 27DILLSBRG | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0008 | 0.8583 | YES
N2-SVM12 | 204528 | 27GARDNERS | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0144 | 0.8659 | YES
N2-SVM13 | 204528 | 27GARDNERS | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0028 | 0.8664 | YES
N2-SVM14 | 204534 | 27GLADES | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9957 | 0.9145 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM15 | 204534 | 27GLADES | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9856 | 0.9145 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM16 | 204546 | 27MOUNTAIN | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0174 | 0.8665 | YES
N2-SVM17 | 204546 | 27MOUNTAIN | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0103 | 0.8671 | YES
N2-SVM18 | 204552 | 27P.P.G.I. | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0167 | 0.8656 | YES
N2-SVM19 | 204552 | 27P.P.G.I. | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0095 | 0.8662 | YES
N2-SVM20 | 204687 | 27PROSPECT | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 1.0026 | 0.9088 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM21 | 204687 | 27PROSPECT | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9909 | 0.9088 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM22 | 204555 | 27QUEEN ST | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9948 | 0.9146 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM23 | 204555 | 27QUEEN ST | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.985 | 0.9146 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM24 | 204681 | 27REDFRONT+ | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 1.0029 | 0.9089 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM25 | 204681 | 27REDFRONT+ | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9916 | 0.9089 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM26 | 204556 | 27ROUND TP | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.015 | 0.8606 | YES
N2-SVM27 | 204556 | 27ROUND TP | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0051 | 0.8612 | YES
N2-SVM28 | 204573 | 27SPRNGWOD | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9954 | 0.9132 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM29 | 204573 | 27SPRNGWOD | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9854 | 0.9132 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM30 | 204561 | 27VIOLET H | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9945 | 0.9171 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM31 | 204561 | 27VIOLET H | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.985 | 0.9171 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM32 | 204562 | 27W.HELLAM | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9991 | 0.9097 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM33 | 204562 | 27W.HELLAM | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.988 | 0.9097 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM34 | 204564 | 27WHITEFRD | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9953 | 0.9198 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM35 | 204564 | 27WHITEFRD | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9859 | 0.9198 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM36 | 204565 | 27WINDSOR | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9964 | 0.908 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM37 | 204565 | 27WINDSOR | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9853 | 0.9081 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM38 | 204525 | 27XROADS | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9928 | 0.9157 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM39 | 204525 | 27XROADS | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9829 | 0.9157 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM40 | 204567 | 27YOE | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9974 | 0.9108 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM41 | 204567 | 27YOE | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.987 | 0.9109 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM42 | 204568 | 27YOE TAP | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 0.9993 | 0.9085 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM43 | 204568 | 27YOE TAP | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.988 | 0.9086 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM44 | 204570 | 27YORKANA | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 1.0036 | 0.9087 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM45 | 204570 | 27YORKANA | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9917 | 0.9087 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM46 | 204701 | 27YORKANAB | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-230-218T_SRT-A | ME_P1-3_ME-115-021_SRT-A | 1.0033 | 0.9088 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM47 | 204701 | 27YORKANAB | 115 | 227 | 0.92 | 1.05 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.992 | 0.9088 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingencies.
N2-SVM48 | 200672 | 26MANSFIEL | 115 | 226 | 0.92 | 1.05 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 0.9969 | 0.8945 | YES
N2-SVM49 | 200671 | 26NILES VA | 115 | 226 | 0.92 | 1.05 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 0.9935 | 0.8976 | YES
N2-SVM50 | 200670 | 26SABINSVI | 115 | 226 | 0.92 | 1.05 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 0.9982 | 0.9129 | YES

## Summer N-1-1 Volt Drop
PJM N-1-1 Voltage Drop Results (2026 Summer)
FG # | Bus # | Bus Name | Base kV | Area | %Vdrop Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | %Vdrop | PJM Accepting Proposals | Reasons For Exclusions | Comment
N2-SVD1 | 200504 | 26CARLISLE | 115 | 226 | 10 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 0.9899 | 0.8606 | 12.174 | YES
N2-SVD2 | 200504 | 26CARLISLE | 115 | 226 | 10 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 0.9812 | 0.8591 | 13.092 | YES
N2-SVD3 | 204520 | 27ALLEN | 115 | 227 | 10 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0131 | 0.798 | 20.764 | YES
N2-SVD4 | 204520 | 27ALLEN | 115 | 227 | 10 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0035 | 0.7962 | 21.8 | YES
N2-SVD5 | 204526 | 27DILLSBRG | 115 | 227 | 10 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0096 | 0.795 | 20.589 | YES
N2-SVD6 | 204526 | 27DILLSBRG | 115 | 227 | 10 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 0.999 | 0.7931 | 21.824 | YES
N2-SVD7 | 204528 | 27GARDNERS | 115 | 227 | 10 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0144 | 0.8057 | 19.705 | YES
N2-SVD8 | 204528 | 27GARDNERS | 115 | 227 | 10 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0007 | 0.8039 | 21.126 | YES
N2-SVD9 | 204546 | 27MOUNTAIN | 115 | 227 | 10 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0174 | 0.8039 | 20.631 | YES
N2-SVD10 | 204546 | 27MOUNTAIN | 115 | 227 | 10 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0076 | 0.8021 | 21.531 | YES
N2-SVD11 | 204552 | 27P.P.G.I. | 115 | 227 | 10 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0167 | 0.803 | 20.652 | YES
N2-SVD12 | 204552 | 27P.P.G.I. | 115 | 227 | 10 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0069 | 0.8011 | 21.562 | YES
N2-SVD13 | 204687 | 27PROSPECT | 115 | 227 | 10 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9888 | 0.8998 | 10.278 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingency. Tested and no issue
N2-SVD14 | 204681 | 27REDFRONT+ | 115 | 227 | 10 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9896 | 0.8999 | 10.298 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingency. Tested and no issue
N2-SVD15 | 204556 | 27ROUND TP | 115 | 227 | 10 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | 1.0127 | 0.7973 | 20.785 | YES
N2-SVD16 | 204556 | 27ROUND TP | 115 | 227 | 10 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | 1.0035 | 0.7955 | 21.952 | YES
N2-SVD17 | 204570 | 27YORKANA | 115 | 227 | 10 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.9897 | 0.8997 | 10.384 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingency. Tested and no issue
N2-SVD18 | 204701 | 27YORKANAB | 115 | 227 | 10 | ME_P1-3_ME-115-021_SRT-A | ME_P1-2_ME-230-218T_SRT-A | 0.99 | 0.8997 | 10.359 | NO |  | Baseline RTEP b3311 adds a 72 MVAR capacitor bank at Yorkana. This resolves the low voltages for this contingency. Tested and no issue
N2-SVD19 | 200672 | 26MANSFIEL | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 0.9969 | 0.7538 | 24.31 | YES
N2-SVD20 | 200671 | 26NILES VA | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 0.9935 | 0.7576 | 23.59 | YES
N2-SVD21 | 200670 | 26SABINSVI | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 0.9982 | 0.7772 | 22.1 | YES
N2-SVD22 | 203348 | 26HECTOR | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 1.0016 | 0.7895 | 21.21 | YES
N2-SVD23 | 200669 | 26GOLD | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 1.0029 | 0.797 | 20.59 | YES
N2-SVD24 | 200671 | 26NILES VA | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-033_SRT-A | 0.9935 | 0.814 | 17.95 | YES
N2-SVD25 | 200923 | 26TENGASVM | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 1.0087 | 0.82 | 18.87 | YES
N2-SVD26 | 235234 | 01POTTER | 115 | 201 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 1.0101 | 0.825 | 18.51 | YES
N2-SVD27 | 200663 | 26TWOMILE | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 1.0115 | 0.8574 | 15.41 | YES
N2-SVD28 | 200944 | 26PIERCEBRK | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 1.0124 | 0.871 | 14.14 | YES
N2-SVD29 | 200668 | 26FARM VLY | 115 | 226 | 10 | PN_P1-3_PN-115-116_SRT-A ADJUST FOR N-1-1 | PN_P1-2_PN-115-102_SRT-A | 1.0128 | 0.8775 | 13.53 | YES

## Summer N-1-1 Load Drop
N-1-1 Analysis Load Drop Summary (Summer 2026 Case)
FG # | First Cont Name | Second Cont Name | TotalLoadLoss | PJM Accepting Proposals | Reasons For Exclusions | Comment
N2-SLD1 | DVP_P1-2: LN 2157_SRT-A | DVP_P1-2: LN 252_SRT-SL | 307.03 | YES
N2-SLD2 | DVP_P1-2: LN 252_SRT-SL | DVP_P1-2: LN 2157_SRT-A | 307.03 | YES
PSSE Bus | Bus Name | ID | MW
314186 | 6FULLER ROAD 230 | 1 | 14.8
314105 | 6AQUIA 230 | 1 | 28.3
314140 | 6GARSVL 230 | 1 | 53.2
314142 | 6STAFORD 230 | 1 | 69.3
314142 | 6STAFORD 230 | 2 | 58.2
314142 | 6STAFORD 230 | SA | -0.868
314134 | 6CRANES 230 | 1 | 21.5
314134 | 6CRANES 230 | 2 | 62.6
307.032