## N-1 Thermal
PJM N-1 Thermal Result (Summer 2026 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
N1-ST31 | 200009 | JUNI | 208005 | JUNI BU2 | 2 | 500/230 | 229/229 | 814 | 105.1474 | 103.47 | Line_FB | 'PL_P4-2_000140_SRT-A' | SN/SE = 776/1010 | NO | Substation Equipment Exclusion | Limited by substation conductor
N1-ST33 | 314109 | 6CUBRUN | 314092 | 6WALNEY | 1 | 230/230 | 345/345 | 823 | 101.9077 | 102.48 | Line_FB | 'DVP_P4-2: 2172T2210_SRT-A' | Conductor Rating is the same as basecase model | YES |  | Overlap with M3 project DOM-2021-0002
N1-ST47 | 314122 | 3SOWEGO | 314112 | 3IND HIL | 1 | 115/115 | 345/345 | 179 | 94.2458 | 101.6 | Line_FB | 'DVP_P4-5: OX L142_SRT-A' | Conductor Rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Segment overlap with candidate EOL facility - 115kV Line #183 Bristers-Ox (DOM-2021-0038)
N1-ST48 | 314122 | 3SOWEGO | 314112 | 3IND HIL | 1 | 115/115 | 345/345 | 179 | 94.2458 | 101.55 | Single | 'DVP_P1-3: 6OX-TX#3_SRT-A' | Conductor Rating is the same as basecase model | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Segment overlap with candidate EOL facility - 115kV Line #183 Bristers-Ox (DOM-2021-0038)
N1-ST49 | 314085 | 6REMNGCT | 314110 | 6ELK RUN | 1 | 230/230 | 345/345 | 1047 | 102.3878 | 101.04 | Tower | 'DVP_P7-1: LN 569-2101_SRT-SL' | Conductor Rating is the same as basecase model | YES |  | Overlap with M3 project DOM-2020-0026
N1-ST129 | 314130 | 6BRISTER | 314156 | 3BRISTER | 1 | 230/115 | 345/345 | 239 | 88.28 | 94.7 | Single | 'DVP_P1-3: 6OX-TX#3_SRT-A' | SN/SE = 248.7/260.2 | NO | Substation Equipment Exclusion | Limited by wave trap on low side of transformer.

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Summer 2026 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Comments
N1-SVM1 | 200857 | 26MARSHALL | 230 | 226 | 1.0576 | 1.0297 | 1.05 | Line_FB | PN_P2-3_PN-230-3262B_SRT-A | YES
N1-SVM2 | 200701 | 26GROVER | 230 | 226 | 1.0602 | 1.0289 | 1.05 | Line_FB | PN_P2-3_PN-230-3262B_SRT-A | YES