## GD-W248
****** PJM Winter Generator Deliverability Detailed Report ****** PJM [TARA Ver 2101.1.0.0 64-bit - Fri Jun 25 13:09:20 2021]
FG Index [All Queue] | 248 | FG ID | 27 | Monitored Facility:232107 TOWNSEND 138 232100 CHURCH 138 1 / Contingency:DPL_P7_1_DBL_1NCB_FSA_SRT-A[Tower]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
389 | 94.78 | 100.28 | AC | 351.88 | 13.08 | -1.66 | 5.36 | 0.04 | 368.71 | 390.1 | 9e-06 | 0 | 12713.6 | 0 | 12668.3 | 0.09284 | 53.87 | 45.37 | 8.5 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | FRMP | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited? | Ramping Limit
233935 | AB2-179 C | 0.38 | 235 | 75 | 0 | 37.6 | 3.48 | 37.6 | FiftyFifty | 0.28836 | 9.8394 | 10.8424 |  | 0 | 1 | 1 | CAPACITY | AB2-179 |  |  | 1
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 1.15 | 12.4 | FiftyFifty | 0.28836 | 3.2449 | 3.5757 |  | 0 | 1 | 1 | NEW | AB2-179 |  |  | 1
AF2-085 | BATEXP_AF2-085->PJM |  |  | LTF |  | 20 |  | 20 | LTF/CMTX | 0.00143 | 0.0286 | 0.0286 | 0.0002
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 94.5 |  | 94.5 | CLTF | 0.00139 | 0.1316 | 0.1316 | 0.0009
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 682 |  | 682 | LTF/CBM | 0.00138 | 0.9428 | 0.9428 | 0.0065
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 1348 |  | 1348 | LTF/CBM | 0.00135 | 1.8248 | 1.8248 | 0.0128
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  | 175 | CLTF | 0.00136 | 0.2378 | 0.2378 | 0.0017
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  | 140 | CLTF | 0.00136 | 0.1903 | 0.1903 | 0.0013
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 18 |  | 18 | LTF/CBM | 0.00136 | 0.0244 | 0.0244 | 0.0002
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1063 |  | 1063 | LTF/CBM | 0.00134 | 1.4273 | 1.4273 | 0.0101
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  | 158.9 | CLTF | 0.00135 | 0.2142 | 0.2142 | 0.0015
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 59.6 |  | 59.6 | CLTF | 0.00135 | 0.0803 | 0.0803 | 0.0006
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 32.9 |  | 32.9 | CLTF | 0.00134 | 0.0442 | 0.0442 | 0.0003
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  | 10.5 | CLTF | 0.00135 | 0.0142 | 0.0142 | 0.0001
AC1-212 | BATEXP_AC1-212->PJM |  |  | LTF |  | 1.9 |  | 1.9 | LTF/CMTX | 0.00134 | 0.0025 | 0.0025 | 0
AA2-082 | BATEXP_AA2-082->PJM |  |  | LTF |  | 2 |  | 2 | LTF/CMTX | 0.00059 | 0.0012 | 0.0012 | 0
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 389 |  | 389 | LTF/CBM | 0.00043 | 0.1666 | 0.1666 | 0.0037
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.0003 | 0.0313 | 0.0313 | -0.001
AD2-210 | BATEXP_AD2-210->PJM |  |  | LTF |  | 8 |  | 8 | LTF/CMTX | 0.00012 | 0.001 | 0.001 | 0.0001
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 | 8.5 | Adder/OL | -0.19541 | -1.661 | -1.9541 | 0.0001 | 0.1042 |  | 1 | ENERGY |  |  |  | 1
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 38.35 |  |  | 0.02531 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 30.66 |  |  | 0.02531 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 29.58 |  |  | 0.02531 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 9.57 |  |  | 0.02531 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 20.25 |  |  | 0.02214 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 9.25 |  |  | 0.02196 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 12.37 |  |  | 0.02092 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 12.32 |  |  | 0.02092 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.21 |  |  | 0.02059 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.01937 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 7.64 |  |  | 0.01937 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 81.14 |  |  | 0.01937 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 67.49 |  |  | 0.01922 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.01922 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.01922 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 33.74 |  |  | 0.01922 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.0192 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.0192 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.01882 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.01882 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 164.17 |  |  | 0.01882 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 0.01182 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 8.32 |  |  | 0.00874 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 99.67 |  |  | 0.00874 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.007 |  |  |  | 0.036 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.007 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213893 | PHLISST1 | 20 | 230 | 58 | 232.3 | 267 | 143.61 |  |  | 0.00699 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00699 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 20.98 |  |  | 0.00516 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.00512 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.00512 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00504 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 18.29 |  |  | 0.00503 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00502 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 222.4 | 119.62 |  |  | 0.00501 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00501 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00501 |  |  |  | 0.036 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.0046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 87.67 |  |  | 0.00378 |  |  |  | 0.036 |  | 1 | CAPACITY | GRAYS FERRY |  |  | 1
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.0037 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00358 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00358 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 28 |  |  | 0.00288 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00238 |  |  |  | 0 |  | 1 | NEW | AA2-072 |  |  | 1
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.0023 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.0023 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 139.8 | 75.19 |  |  | 0.00227 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 61.1 |  |  | 0.00227 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 55.94 |  |  | 0.00227 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 27.97 |  |  | 0.00227 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223402 | AF1-300 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | AF1-300 |  |  | 1
223401 | AF1-299 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | AF1-299 |  |  | 1
946362 | AF1-300 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW | AF1-300 |  |  | 1
946352 | AF1-299 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW | AF1-299 |  |  | 1
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.4 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00216 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00214 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00214 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00213 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00213 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 75 |  |  | 0.00213 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220904 | CRANE G2 | 20 | 232 | 12 | 0 | 14 | 0 |  |  | 0.0021 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.2 | 16.24 |  |  | 0.00199 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 29.8 | 16.03 |  |  | 0.00199 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 57 |  |  | 0.00197 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 93.64 |  |  | 0.00195 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208904 | HOLT 696 | 13.2 | 229 | 60 | 16 | 58.4 | 41.06 |  |  | 0.00195 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208903 | HOLT 695 | 13.2 | 229 | 60 | 19 | 53.2 | 37.4 |  |  | 0.00195 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 0.45 |  |  | 0.00195 |  |  |  | 0 |  | 1 | CAPACITY | V4-027 |  |  | 1
208254 | AF2-280 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00195 |  |  |  | 0 |  | 1 | NEW | AF2-280 |  |  | 1
208474 | KINZ 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00195 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208253 | AF2-280 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00195 |  |  |  | 0 |  | 1 | MTX | AF2-280 |  |  | 1
916007 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 0.1 | 0.06 |  |  | 0.00195 |  |  |  | 0 |  | 1 | NEW | V4-027 |  |  | 1
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 68.9 |  |  | 0.00194 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 289.09 |  |  | 0.00194 |  |  |  | 0.1042 |  | 1 | CAPACITY | Wagner3 |  |  | 1
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.00194 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 7.15 |  |  | 0.00194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 7.34 |  |  | 0.00194 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 642.7 |  |  | 0.00194 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 638.9 |  |  | 0.00194 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 80.49 |  |  | 0.00186 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 53.78 |  |  | 0.00186 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00186 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 68.19 |  |  | 0.00186 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 45.34 |  |  | 0.00186 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 44.99 |  |  | 0.00186 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208876 | WLAN | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00185 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208769 | SISO | 12.5 | 229 | 2 | 2.5 | 1.6 | 0 |  |  | 0.00185 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
209030 | FRFA O01 | 12.5 | 229 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00181 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208527 | AF2-279 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00181 |  |  |  | 0 |  | 1 | NEW | AF2-279 |  |  | 1
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 2 | 1.22 |  |  | 0.00181 |  |  |  | 0 |  | 1 | NEW | V3-051 |  |  | 1
208526 | AF2-279 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00181 |  |  |  | 0 |  | 1 | MTX | AF2-279 |  |  | 1
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 1119.7 |  |  | 0.00176 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213798 | MERCK 3 | 13.8 | 230 | 29 | 13 | 42 | 22.59 |  |  | 0.00174 |  |  |  | 0 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
213797 | MERCK 2 | 13.8 | 230 | 29 | 4 | 32 | 17.21 |  |  | 0.00174 |  |  |  | 0.1042 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
214030 | WAYNEJCT | 13.8 | 230 | 29 | 0 | 8.8 | 4.73 |  |  | 0.00175 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 2.75 |  |  | 0.00174 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.64 |  |  | 0.00168 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223967 | METZ E69 | 69 | 233 | 56 | 0 | 20 | 0 |  |  | 0.00162 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226895 | WOAKV2-037 E | 69 | 233 | 29 | 0 | 4.5 | 0 |  |  | 0.00162 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
226920 | AE1-012 E | 115 | 233 | 75 | 0 | 0.34 | 0.03 |  |  | 0.00161 |  |  |  | 0 |  | 1 | NEW | AE1-012 |  |  | 1
226919 | AE1-012 C | 115 | 233 | 75 | 0 | 0.22 | 0.02 |  |  | 0.00161 |  |  |  | 0 |  | 1 | CAPACITY | AE1-012 |  |  | 1
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 11.01 |  |  | 0.00157 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 10.83 |  |  | 0.00157 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227024 | SMECOCT | 13.8 | 238 | 57 | 0 | 80.2 | 43.14 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 1.86 |  |  | 0.00157 |  |  |  | 0 |  | 1 | NEW | AC2-101 |  |  | 1
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 1.58 |  |  | 0.00157 |  |  |  | 0 |  | 1 | NEW | AC2-120 |  |  | 1
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 13.12 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227282 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 1.14 |  |  | 0.00157 |  |  |  | 0 |  | 1 | CAPACITY | AC2-101 |  |  | 1
227280 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 0.97 |  |  | 0.00157 |  |  |  | 0 |  | 1 | CAPACITY | AC2-120 |  |  | 1
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 9.68 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0.16 |  |  | 0.00158 |  |  |  | 0 |  | 1 | NEW | AB2-157 |  |  | 1
226910 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00158 |  |  |  | 0 |  | 1 | CAPACITY | AB2-157 |  |  | 1
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.91 |  |  | 0.00158 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 182.23 |  |  | 0.00157 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.00157 |  |  |  | 0.036 |  | 1 | CAPACITY | WALDORF |  |  | 1
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.00157 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.00157 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 619.4 |  |  | 0.00157 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 613.3 |  |  | 0.00157 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.87 |  |  | 0.00155 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 866 |  |  | 0.00155 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 841.8 |  |  | 0.00155 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 327.3 | 176.05 |  |  | 0.00154 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.00154 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-035 |  |  | 1
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.00154 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 43.03 |  |  | 0.00155 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.00155 |  |  |  | 0.036 |  | 1 | CAPACITY | PANDA |  |  | 1
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.00155 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
226704 | AOCX4-046 E | 13.8 | 233 | 58 | 0 | 19.5 | 0 |  |  | 0.00155 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.00155 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226924 | AE1-015 E | 69 | 233 | 75 | 0 | 0.75 | 0.07 |  |  | 0.00155 |  |  |  | 0 |  | 1 | NEW | AE1-015 |  |  | 1
226923 | AE1-015 C | 69 | 233 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00155 |  |  |  | 0 |  | 1 | CAPACITY | AE1-015 |  |  | 1
226922 | AE1-013 E | 69 | 233 | 75 | 0 | 0.5 | 0.05 |  |  | 0.00155 |  |  |  | 0 |  | 1 | NEW | AE1-013 |  |  | 1
226921 | AE1-013 C | 69 | 233 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00155 |  |  |  | 0 |  | 1 | CAPACITY | AE1-013 |  |  | 1
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00152 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.00149 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.00149 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 0.33 |  |  | 0.00149 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 52 |  |  | 0.00149 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 229.53 |  |  | 0.00146 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 188.28 |  |  | 0.00146 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00146 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-039 |  |  | 1
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00146 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00146 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00146 |  |  |  | 0.036 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 1.07 |  |  | 0.00146 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 1.07 |  |  | 0.00146 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
314088 | 6VANDORN | 230 | 345 | 1 | 7 | 21 | 14.08 |  |  | 0.00146 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00146 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00146 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316052 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00146 |  |  |  | 0 |  | 1 | CAPACITY | AC2-072 |  |  | 1
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00146 |  |  |  | 0 |  | 1 | NEW | AC2-072 |  |  | 1
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 1.07 | 0.16 |  |  | 0.00146 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 2 |  |  | 0.00145 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316045 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00145 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 2 |  |  | 1
316044 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00145 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 1 |  |  | 1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00145 |  |  |  | 0 |  | 1 | NEW | AC1-158 2 |  |  | 1
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00145 |  |  |  | 0 |  | 1 | NEW | AC1-158 1 |  |  | 1
925672 | AC1-043 E | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 3.62 |  |  | 0.00145 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 170 | 127.52 |  |  | 0.00145 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 120.47 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 120.39 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 120.09 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 119.87 |  |  | 0.00145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 113.79 |  |  | 0.00145 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.1 | 113.34 |  |  | 0.00145 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 112.29 |  |  | 0.00145 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316267 | AC1-143 C | 0.38 | 345 | 75 | 0 | 41.2 | 6.18 |  |  | 0.00145 |  |  |  | 0 |  | 1 | CAPACITY | AC1-143 |  |  | 1
316254 | AC1-120 C | 0.6 | 345 | 75 | 0 | 39.6 | 5.94 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AC1-120 |  |  | 1
926004 | AC1-076_E | 0.6 | 345 | 75 | 0 | 39.42 | 5.91 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AC1-076 |  |  | 1
316257 | AC1-043 C | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
237026 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 2.22 |  |  | 0.00145 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
316164 | AC1-076_C | 0.6 | 345 | 75 | 0 | 23.8 | 3.57 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AC1-076 |  |  | 1
926486 | AC1-120 E | 0.6 | 345 | 75 | 0 | 20.4 | 3.06 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AC1-120 |  |  | 1
926615 | AC1-143 E | 0.38 | 345 | 75 | 0 | 18.8 | 2.82 |  |  | 0.00145 |  |  |  | 0 |  | 1 | NEW | AC1-143 |  |  | 1
316170 | AC1-121 C | 0.6 | 345 | 75 | 0 | 13.6 | 2.04 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AC1-121 |  |  | 1
316234 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AE1-124 |  |  | 1
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 1.83 |  |  | 0.00145 |  |  |  | 0 |  | 1 | NEW | AB2-029 |  |  | 1
316006 | AB2-029 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.00145 |  |  |  | 0 |  | 1 | CAPACITY | AB2-029 |  |  | 1
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AE1-124 |  |  | 1
926502 | AC1-121 E | 0.6 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AC1-121 |  |  | 1
961102 | AF2-401 E | 115 | 345 | 75 | 0 | 5.8 | 0.87 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AF2-401 |  |  | 1
204555 | 27QUEEN ST | 115 | 227 | 75 | 0 | 5 | 0.46 |  |  | 0.00145 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
316302 | AF2-401 C | 115 | 345 | 75 | 0 | 3.52 | 0.53 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AF2-401 |  |  | 1
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 8.7 |  |  | 0.00145 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 948.9 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 948.5 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00143 |  |  |  | 0.036 |  | 1 | NEW | AC1-107 |  |  | 1
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316169 | AC1-164 GEN | 0.44 | 345 | 75 | 192.1 | 220.8 | 33.12 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC1-164 |  |  | 1
926785 | AC1-164_E | 0.44 | 345 | 75 | 91 | 104.6 | 15.69 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-164 |  |  | 1
316192 | AB2-158 C | 230 | 345 | 75 | 0 | 71 | 10.65 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AB2-158 |  |  | 1
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 127.52 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316201 | AC1-065 C | 0.39 | 345 | 75 | 0 | 49.4 | 7.41 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC1-065 |  |  | 1
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 165.2 | 123.92 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 165.1 | 123.84 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 118.52 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
313053 | 6PAPERMILL | 230 | 345 | 77 | 12 | 37 | 0 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 98.04 |  |  | 0.00143 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 96.46 |  |  | 0.00143 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 126.7 | 95.04 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 124.8 | 93.61 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-065 |  |  | 1
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.00144 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.00144 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
316280 | AD1-041 C | 0.55 | 345 | 75 | 0 | 30 | 4.5 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AD1-041 |  |  | 1
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 0.75 |  |  | 0.00144 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 0.72 |  |  | 0.00144 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 4.08 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AB2-158 |  |  | 1
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 64.51 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 64.43 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 64.21 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 64.14 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 57.83 |  |  | 0.00144 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00144 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00144 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
934146 | AD1-041 E | 0.55 | 345 | 75 | 0 | 20 | 3 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AD1-041 |  |  | 1
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 49.66 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 45.01 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316312 | AB1-027 C | 230 | 345 | 75 | 0 | 17.5 | 2.63 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AB1-027 |  |  | 1
316304 | AE2-227 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE2-227 |  |  | 1
316233 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE1-074 |  |  | 1
316223 | AC1-118 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AC1-118 |  |  | 1
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 1.97 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AD2-030 |  |  | 1
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 12.7 | 1.9 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC2-137 |  |  | 1
316314 | AB2-024 C | 230 | 345 | 75 | 0 | 11.13 | 1.67 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AB2-024 |  |  | 1
316004 | AC1-112 C | 230 | 345 | 75 | 0 | 10.9 | 1.63 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC1-112 |  |  | 1
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
942152 | AE2-227 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE2-227 |  |  | 1
315086 | 1SPRUNCD | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.00143 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315085 | 1SPRUNCC | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.00143 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316050 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 1.38 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC2-070 |  |  | 1
316059 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AD1-063 |  |  | 1
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | 0.00144 |  |  |  | 0 |  | 1 | CAPACITY | AC2-138 |  |  | 1
316303 | AF2-085 | 230 | 345 | 76 | 0 | 20 | 13.41 |  |  | 0.00143 |  |  |  | 0.05 |  | 1 | CAPACITY |  |  |  | 1
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 7.5 | 1.13 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB1-027 |  |  | 1
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC2-137 |  |  | 1
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AC1-118 |  |  | 1
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AD2-030 |  |  | 1
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE1-074 |  |  | 1
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.1 | 10.8 |  |  | 0.00143 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHARLES CITY_LF |  |  | 1
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-024 |  |  | 1
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0.92 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-112 |  |  | 1
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00144 |  |  |  | 0 |  | 1 | NEW | AC2-138 |  |  | 1
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AD1-063 |  |  | 1
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 9.99 |  |  | 0.00143 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHESTERFIELD LF_A |  |  | 1
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 7.38 |  |  | 0.00143 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0.57 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC2-070 |  |  | 1
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 4 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 6.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 20 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 787.1 | 23.61 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 448.57 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
316294 | AC1-161 C | 0.44 | 345 | 75 | 0 | 168.2 | 25.23 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC1-161 |  |  | 1
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 395.08 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 16.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AB2-190 |  |  | 1
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00142 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
926755 | AC1-161 E | 0.44 | 345 | 75 | 0 | 71.8 | 0 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-161 |  |  | 1
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00142 |  |  |  | 0.036 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 11.81 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AA1-139 |  |  | 1
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 10.77 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AB2-134 |  |  | 1
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 10.59 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-134 |  |  | 1
932596 | AC2-079 E | 0.64 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC2-079 |  |  | 1
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 7.5 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-015 |  |  | 1
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 7.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-190 |  |  | 1
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
316185 | AD1-033 C | 0.6 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AD1-033 |  |  | 1
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | 0.00142 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 6.15 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-015 |  |  | 1
932586 | AC2-078 E | 0.64 | 345 | 75 | 0 | 37.2 | 5.58 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC2-078 |  |  | 1
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 94.51 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AA1-139 |  |  | 1
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 0.89 |  |  | 0.00143 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 83.11 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316311 | AC2-079 C | 0.64 | 345 | 75 | 0 | 32.3 | 4.84 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC2-079 |  |  | 1
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 82.06 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 80.64 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 4.56 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
315099 | 1CHESPKB | 13.8 | 345 | 20 | 0 | 24.7 | 0 |  |  | 0.00143 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
934065 | AD1-033 E | 0.6 | 345 | 75 | 0 | 28 | 4.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AD1-033 |  |  | 1
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 65.18 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 65.11 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00143 |  |  |  | 0.036 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
316289 | AC2-078 C | 0.64 | 345 | 75 | 0 | 22.8 | 3.42 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC2-078 |  |  | 1
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 41.2 | 22.16 |  |  | 0.00143 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 2.85 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 0.45 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316301 | AE2-228 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE2-228 |  |  | 1
316321 | Z2-027 C | 230 | 345 | 75 | 0 | 13.8 | 2.07 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | Z2-027 |  |  | 1
316315 | AB2-025 C | 230 | 345 | 75 | 0 | 13.65 | 2.05 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-025 |  |  | 1
316159 | AE1-175 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE1-175 |  |  | 1
316241 | AE2-078 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE2-078 |  |  | 1
316242 | AE2-079 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE2-079 |  |  | 1
316247 | AF1-033 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AF1-033 |  |  | 1
316313 | AB2-026 C | 230 | 345 | 75 | 0 | 13.07 | 1.96 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AB2-026 |  |  | 1
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 1.95 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-022 |  |  | 1
316036 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC1-147 |  |  | 1
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 1.86 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | Y1-086 |  |  | 1
316240 | AF1-291 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AF1-291 |  |  | 1
316236 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE1-162 |  |  | 1
316258 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE1-075 |  |  | 1
316305 | AF2-043 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AF2-043 |  |  | 1
316244 | AE2-225 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE2-225 |  |  | 1
316316 | AC1-027 C | 115 | 345 | 75 | 0 | 11.2 | 1.68 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC1-027 |  |  | 1
923213 | AB1-125_E | 0.6 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB1-125 |  |  | 1
942162 | AE2-228 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE2-228 |  |  | 1
316057 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AC2-196 |  |  | 1
316150 | AD2-215 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AD2-215 |  |  | 1
316246 | AF1-032 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AF1-032 |  |  | 1
316072 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 1.46 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AD1-144 |  |  | 1
316245 | AE2-229 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | AE2-229 |  |  | 1
946262 | AF1-291 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AF1-291 |  |  | 1
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE1-162 |  |  | 1
942132 | AE2-225 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE2-225 |  |  | 1
957492 | AF2-043 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AF2-043 |  |  | 1
316320 | Y1-086 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | Y1-086 |  |  | 1
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-147 |  |  | 1
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 1.05 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-022 |  |  | 1
943622 | AF1-033 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AF1-033 |  |  | 1
940892 | AE2-078 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE2-078 |  |  | 1
940902 | AE2-079 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE2-079 |  |  | 1
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 1 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC2-196 |  |  | 1
316160 | AE1-175 E | 230 | 345 | 75 | 0 | 6.6 | 0.99 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE1-175 |  |  | 1
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AC1-027 |  |  | 1
237006 | AB1-125_C | 0.6 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB1-125 |  |  | 1
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AB2-026 |  |  | 1
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-025 |  |  | 1
942172 | AE2-229 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE2-229 |  |  | 1
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | Z2-027 |  |  | 1
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0.88 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AE1-075 |  |  | 1
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 10.06 |  |  | 0.00143 |  |  |  | 0.44065 |  | 1 | CAPACITY |  |  |  | 1
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AD1-144 |  |  | 1
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AD2-215 |  |  | 1
943612 | AF1-032 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | AF1-032 |  |  | 1
961092 | AF2-400 E | 115 | 345 | 75 | 0 | 4.43 | 0.66 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | af2-400 |  |  | 1
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 7.56 |  |  | 0.00143 |  |  |  | 0.1097 |  | 1 | CAPACITY | VIRGINIA BEACH LF_A |  |  | 1
314541 | 3WATKINS | 115 | 345 | 75 | 0 | 4 | 0.6 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 6.71 |  |  | 0.00143 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 258.69 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
316300 | AF2-400 C | 115 | 345 | 75 | 0 | 2.71 | 0.41 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AF2-400 |  |  | 1
901082 | W1-029 E | 230 | 345 | 74 | 0 | 169 | 167.31 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | W1-029 |  |  | 1
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | W1-029 |  |  | 1
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 10.4 |  |  | 0.00143 |  |  |  | 0 |  | 1 | NEW | Z1-068 |  |  | 1
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.49 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY | Z1-068 |  |  | 1
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 52.8 | 52.8 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 4.5 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 843.5 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 844.6 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 15.2 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 11.9 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 12.9 |  |  | 0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53 | 53 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 422.31 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 301.17 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
316011 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 12.6 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 1
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00142 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 185.28 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
923994 | AB2-040_E | 0.6 | 345 | 75 | 0 | 69.51 | 10.43 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-040 |  |  | 1
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 67 | 10.05 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AA1-065 |  |  | 1
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AA2-088 |  |  | 1
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00142 |  |  |  | 0.036 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 8.4 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AA2-178 |  |  | 1
316274 | AC1-208 C | 0.38 | 345 | 75 | 0 | 55.4 | 8.31 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC1-208 |  |  | 1
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 8.22 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AA2-053 |  |  | 1
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00142 |  |  |  | 0.036 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 7.64 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AA1-063A |  |  | 1
316327 | AA2-057 C | 0.63 | 345 | 75 | 0 | 50 | 7.5 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AA2-057 |  |  | 1
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 6.68 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC1-054 |  |  | 1
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-174 |  |  | 1
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 6.06 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB1-173 |  |  | 1
316174 | AB2-169_C | 0.63 | 345 | 75 | 0 | 39 | 5.85 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AB2-169 |  |  | 1
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AA2-088 |  |  | 1
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-174 |  |  | 1
316210 | AC1-098 C | 0.6 | 345 | 75 | 0 | 37.6 | 5.64 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC1-098 |  |  | 1
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 1
925122 | AB2-169 E | 0.63 | 345 | 75 | 0 | 35 | 5.25 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-169 |  |  | 1
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 1 |  |  | 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 2 |  |  | 1
927146 | AC1-208 E | 0.38 | 345 | 75 | 0 | 24.5 | 0 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-208 |  |  | 1
919710 | AA2-057 E | 0.63 | 345 | 75 | 0 | 24.9 | 3.73 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AA2-057 |  |  | 1
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AA2-178 |  |  | 1
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AA1-065 |  |  | 1
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AA1-063A |  |  | 1
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 3.38 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AA2-053 |  |  | 1
926206 | AC1-098 E | 0.6 | 345 | 75 | 0 | 22.4 | 3.36 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-098 |  |  | 1
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 74.1 | 55.58 |  |  | 0.00141 |  |  |  | 0.036 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 3.08 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-054 |  |  | 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-100 2 |  |  | 1
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-100 1 |  |  | 1
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 37.51 |  |  | 0.00142 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 45.9 | 34.43 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
316051 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AC2-071 |  |  | 1
316317 | KELFORD C | 115 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | Z2-043 |  |  | 1
316212 | AC1-099 C | 0.6 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC1-099 |  |  | 1
316181 | AB2-040 GEN | 0.6 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-040 |  |  | 1
316322 | AB2-045 C | 230 | 345 | 75 | 0 | 11.43 | 1.72 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AB2-045 |  |  | 1
316005 | AA1-067 C | 230 | 345 | 75 | 0 | 10.5 | 1.58 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AA1-067 |  |  | 1
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 34.7 | 26.03 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 1.39 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-036 |  |  | 1
316074 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AD1-157 |  |  | 1
316034 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 1.29 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC1-036 |  |  | 1
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 1.17 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AC1-116 |  |  | 1
926214 | AC1-099 E | 0.6 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-099 |  |  | 1
917332 | KELFORD E | 115 | 345 | 75 | 0 | 7 | 1.05 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | Z2-043 |  |  | 1
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | Z2-030 |  |  | 1
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AC2-071 |  |  | 1
316243 | AE2-151 C | 115 | 345 | 75 | 0 | 6.5 | 0.98 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AE2-151 |  |  | 1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-045 |  |  | 1
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB1-173 |  |  | 1
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 15.7 | 10.53 |  |  | 0.00141 |  |  |  | 0.1097 |  | 1 | CAPACITY | AMELIA LF_1-A |  |  | 1
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AD1-157 |  |  | 1
313853 | 3PONTONDP | 115 | 345 | 65 | 0 | 4 | 0 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
316035 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 0.7 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | AC1-116 |  |  | 1
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0.68 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AA1-067 |  |  | 1
237077 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | Z2-030 |  |  | 1
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 1.87 |  |  | 0.00141 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
941542 | AE2-151 E | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AE2-151 |  |  | 1
316318 | V4-068 C | 115 | 345 | 75 | 0 | 3.2 | 0.48 |  |  | 0.00142 |  |  |  | 0 |  | 1 | CAPACITY | V4-068 |  |  | 1
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | 0.00142 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0.27 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | V4-068 |  |  | 1
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0.22 |  |  | 0.00142 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 0.76 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 1.44 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.39 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 11 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 48 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 50.3 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 437.1 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.2 | 441.2 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316299 | AC2-112 C | 0.6 | 345 | 75 | 0 | 103.1 | 15.47 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC2-112 |  |  | 1
315131 | 1EDGECMA | 13.8 | 345 | 11 | 7.5 | 58 | 0 |  |  | 0.00141 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 9.9 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AB2-059 |  |  | 1
314860 | 4E MILL | 138 | 345 | 77 | 0 | 50 | 0 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEWENERGY | Covington |  |  | 1
316049 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 8.4 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AB1-081 |  |  | 1
932855 | AC2-112 E | 0.6 | 345 | 75 | 0 | 46.9 | 0 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC2-112 |  |  | 1
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 8.16 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AB2-060 |  |  | 1
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | Z2-088 |  |  | 1
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | Z2-088 |  |  | 1
314859 | 4WSTVACO | 138 | 345 | 2 | 0 | 40.5 | 0 |  |  | 0.0014 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316263 | AC1-034 C | 0.55 | 345 | 75 | 0 | 42.75 | 6.41 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC1-034 |  |  | 1
316003 | AC1-222 C | 0.6 | 345 | 75 | 0 | 38.8 | 5.82 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AC1-222 |  |  | 1
909222 | X2-060 E | 138 | 345 | 64 | 0 | 30 | 0 |  |  | 0.0014 |  |  |  | 0 |  | 1 | ENERGY | Covington |  |  | 1
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 5.18 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 5.1 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-059 |  |  | 1
925595 | AC1-034 E | 0.55 | 345 | 75 | 0 | 32.25 | 4.84 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-034 |  |  | 1
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-043 |  |  | 1
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 0.76 |  |  | 0.0014 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 0.75 |  |  | 0.0014 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
927264 | AC1-222 E | 0.6 | 345 | 75 | 0 | 25.9 | 3.88 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AC1-222 |  |  | 1
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 3.84 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-060 |  |  | 1
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB1-081 |  |  | 1
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 1.46 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AD1-085 |  |  | 1
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 2.84 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AB2-043 |  |  | 1
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 2.54 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 0.9 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AD1-085 |  |  | 1
316238 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
316237 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
316239 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
316248 | AF1-058 C | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AF1-058 |  |  | 1
316054 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AC2-074 |  |  | 1
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AE1-099 |  |  | 1
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AE1-098 |  |  | 1
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0.63 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | W1-116 |  |  | 1
316319 | Z2-044 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | Z2-044 |  |  | 1
237025 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
943902 | AF1-058 E | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AF1-058 |  |  | 1
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0.44 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AB1-096 |  |  | 1
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 0.39 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | W1-116 |  |  | 1
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AE1-098 |  |  | 1
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AE1-099 |  |  | 1
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0.79 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | AC2-074 |  |  | 1
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0.54 |  |  | 0.00141 |  |  |  | 0 |  | 1 | NEW | Z2-044 |  |  | 1
237030 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 0.23 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY | AB1-096 |  |  | 1
918234 | AA1-038_E | 0.69 | 345 | 74 | 0 | 66.7 | 66.03 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AA1-038 |  |  | 1
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 0.72 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.44 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315616 | AA1-038_C | 0.69 | 345 | 74 | 0 | 9.9 | 9.8 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AA1-038 |  |  | 1
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 15 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 30 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 45.6 |  |  | 0.00141 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 5.5 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 108.79 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | K11 |  |  | 1
316222 | AC1-221 C | 0.6 | 345 | 75 | 0 | 51.2 | 7.68 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AC1-221 |  |  | 1
316283 | AC2-100 C | 0.57 | 345 | 75 | 0 | 45.6 | 6.84 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AC2-100 |  |  | 1
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 5.74 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AC1-075 |  |  | 1
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 18.41 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | K11 |  |  | 1
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 3.26 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AC1-075 |  |  | 1
932763 | AC2-100 E | 0.57 | 345 | 75 | 0 | 16.4 | 2.46 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AC2-100 |  |  | 1
927255 | AC1-221 E | 0.6 | 345 | 75 | 0 | 14.6 | 2.19 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AC1-221 |  |  | 1
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 0.36 |  |  | 0.00139 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | W4-102 |  |  | 1
316205 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 1.92 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AC1-080 |  |  | 1
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
237003 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0.76 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | W4-102 |  |  | 1
237024 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0.51 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 1.08 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AC1-080 |  |  | 1
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | AA1-109 |  |  | 1
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | AA1-109 |  |  | 1
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0.24 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | AA1-095 |  |  | 1
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 0.21 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | AA1-095 |  |  | 1
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 81.18 |  |  | 0.0014 |  |  |  | 0 |  | 1 | NEW | T157 |  |  | 1
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.61 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 20.3 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY | T157 |  |  | 1
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 502.2 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 502.3 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 502.8 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 503.8 |  |  | 0.0014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 553 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM2 |  |  | 1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 522.9 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 548.2 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM1 |  |  | 1
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 107.08 |  |  | 0.00138 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 105.41 |  |  | 0.00138 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 67.13 |  |  | 0.00138 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 41.06 |  |  | 0.00138 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 39.39 |  |  | 0.00138 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AC1-145 |  |  | 1
925665 | AC1-042 E | 0.4 | 345 | 75 | 0 | 26.04 | 3.91 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AC1-042 |  |  | 1
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.2 | 27.3 |  |  | 0.00138 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
316217 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 2.85 |  |  | 0.00138 |  |  |  | 0 |  | 1 | CAPACITY | AC1-145 |  |  | 1
316197 | AC1-042 C | 0.4 | 345 | 75 | 0 | 15.96 | 2.39 |  |  | 0.00138 |  |  |  | 0 |  | 1 | CAPACITY | AC1-042 |  |  | 1
244012 | 05PINNACLE | 4 | 205 | 75 | 0 | 11 | 0.8 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0.73 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AB2-097 |  |  | 1
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | AA1-092 |  |  | 1
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | AA1-092 |  |  | 1
205931 | AF2-100 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | AF2-100 |  |  | 1
205930 | AF2-099 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY | AF2-099 |  |  | 1
958062 | AF2-100 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | AF2-100 |  |  | 1
958052 | AF2-099 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00139 |  |  |  | 0 |  | 1 | NEW | AF2-099 |  |  | 1
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 52.4 |  |  | 0.00139 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270173 | AC1-122_C | 0.6 | 205 | 75 | 0 | 54.4 | 3.97 |  |  | 0.00138 |  |  |  | 0 |  | 1 | CAPACITY | AC1-122 |  |  | 1
926516 | AC1-122_E | 0.6 | 205 | 75 | 0 | 21.5 | 1.57 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AC1-122 |  |  | 1
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 2.01 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 1.23 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
237038 | AE2-054 C | 34.5 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 20.6 | 11.08 |  |  | 0.00137 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AD1-060 |  |  | 1
940672 | AE2-054 E | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
270130 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00138 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0.46 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | AC2-136 |  |  | 1
237080 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00138 |  |  |  | 0 |  | 1 | CAPACITY | AD1-060 |  |  | 1
237034 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 0.4 |  |  | 0.00137 |  |  |  | 0 |  | 1 | CAPACITY | AC2-136 |  |  | 1
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 10.07 |  |  | 0.00138 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 4.44 |  |  | 0.00137 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 33.02 |  |  | 0.00138 |  |  |  | 0 |  | 1 | CAPACITY | P.H. GLATFELTER_IPP |  |  | 1
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 2.22 |  |  | 0.00138 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270205 | AE1-176 | 138 | 205 | 60 | 0 | 2.4 | 1.33 |  |  | 0.00138 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
205916 | AD1-020_C | 0.6 | 227 | 75 | 0 | 54 | 4.99 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 134.03 |  |  | 0.00136 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | 0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | 0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 30.18 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 64 | 34.42 |  |  | 0.00136 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
242587 | 05CELAN | 138 | 205 | 77 | 0 | 81.6 | 58.39 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
205917 | AD1-020 ES | 0.55 | 227 | 75 | 0 | 21.5 | 1.99 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00137 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00137 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237037 | AE1-188 C | 34.5 | 201 | 75 | 0 | 20.5 | 1.5 |  |  | 0.00137 |  |  |  | 0 |  | 1 | CAPACITY | AE1-188 |  |  | 1
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | 0.00137 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | 0.00137 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | AB1-127 |  |  | 1
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | AB1-128 |  |  | 1
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | 0.00136 |  |  |  | 0.0975 |  | 1 | MTX | AA1-100 |  |  | 1
939592 | AE1-188 E | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | AE1-188 |  |  | 1
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 20.5 | 11.03 |  |  | 0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270183 | AB2-010_C | 138 | 205 | 75 | 0 | 10 | 0.73 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
235043 | AF1-166 C | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.00137 |  |  |  | 0 |  | 1 | CAPACITY | AF1-166 |  |  | 1
270182 | AB2-011_C | 138 | 205 | 75 | 0 | 8 | 0.58 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
237001 | AB1-127 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00137 |  |  |  | 0 |  | 1 | CAPACITY | AB1-127 |  |  | 1
237002 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00137 |  |  |  | 0 |  | 1 | CAPACITY | AB1-128 |  |  | 1
945012 | AF1-166 E | 34.5 | 201 | 75 | 0 | 6.4 | 0.47 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | AF1-166 |  |  | 1
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 12.2 | 6.77 |  |  | 0.00137 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | 0.00137 |  |  |  | 0.0789 |  | 1 | ENERGY |  |  |  | 1
270111 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 4.51 |  |  | 0.00137 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.1 | 5.05 |  |  | 0.00137 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | 0.00137 |  |  |  | 0 |  | 1 | MTX | AD2-205 |  |  | 1
923762 | AB2-010_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
923772 | AB2-011_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
205922 | AF2-268 E | 115 | 227 | 75 | 0 | 2 | 0.19 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 2.75 |  |  | 0.00137 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 85.93 |  |  | 0.00135 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 44.3 |  |  | 0.00135 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 55.94 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | U2-073 A |  |  | 1
939134 | AE1-143 C | 0.64 | 320 | 75 | 0 | 64.14 | 4.68 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | AE1-143 |  |  | 1
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 44.38 |  |  | 0.00135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 93.75 |  |  | 0.00136 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG2 |  |  | 1
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 125.1 | 93.15 |  |  | 0.00136 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG1 |  |  | 1
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 38.84 |  |  | 0.00135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
939135 | AE1-143 E | 0.64 | 320 | 75 | 0 | 31.86 | 2.33 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | AE1-143 |  |  | 1
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 26.98 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | S14 |  |  | 1
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 25.15 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | U2-030 |  |  | 1
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 78.63 |  |  | 0.00136 |  |  |  | 0 |  | 1 | CAPACITY | CRG2 |  |  | 1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 104.7 | 77.96 |  |  | 0.00136 |  |  |  | 0 |  | 1 | CAPACITY | CRG1 |  |  | 1
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 24.52 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | U2-073 B |  |  | 1
916001 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 44.5 | 21.44 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | N47 |  |  | 1
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | 0.00135 |  |  |  | 0.1097 |  | 1 | ENERGY |  |  |  | 1
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 19.81 |  |  | 0.00135 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 14.6 | 7.03 |  |  | 0.00136 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 A |  |  | 1
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 6.74 |  |  | 0.00136 |  |  |  | 0 |  | 1 | CAPACITY | S14 |  |  | 1
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00136 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | 0.00135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 5.16 |  |  | 0.00136 |  |  |  | 0 |  | 1 | CAPACITY | N47 |  |  | 1
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 8.4 | 4.05 |  |  | 0.00136 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 B |  |  | 1
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 3.76 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | U2-030 |  |  | 1
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 3.05 |  |  | 0.00135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
208885 | WNHO | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208697 | PRIN B34 | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
342070 | 2PINE GROVE | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 2.4 | 1.61 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342442 | 2W GLASGOW | 69 | 320 | 77 | 0 | 1 | 0.67 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 610.3 |  |  | 0.00136 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 1122.1 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237068 | AA2-119 GEN | 20.5 | 201 | 58 | 0 | 600 | 0 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | NEW | Harrison |  |  | 1
276658 | AB1-122 CT1 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-122 |  |  | 1
276660 | AB1-122 CT2 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-122 |  |  | 1
276640 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | AC1-204 |  |  | 1
276642 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-204 |  |  | 1
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 194.77 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 289.95 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet8 |  |  | 1
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 293.58 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet7 |  |  | 1
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 127.94 |  |  | 0.00134 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 127.17 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 113.58 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.1 | 113.46 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 272.1 | 103.92 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-079 |  |  | 1
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 95.86 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 92.04 |  |  | 0.00134 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | X2-052 |  |  | 1
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
276174 | W4-005 E | 0.69 | 222 | 74 | 0 | 260.4 | 125.46 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | W4-005 |  |  | 1
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 77.49 |  |  | 0.00134 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 202.7 | 77.41 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Z1-079 |  |  | 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | 0.00135 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | 0.00135 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 160.3 | 184.3 | 70.39 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 69.62 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 69.62 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 158.6 | 182.3 | 69.62 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 68.74 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 156.6 | 180 | 68.74 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251832 | 08HLCRTG | 0.38 | 212 | 75 | 0 | 120 | 8.76 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-014 |  |  | 1
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 155.8 | 179.1 | 68.4 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 154.7 | 177.8 | 67.9 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247225 | 05FTHLG2 | 18 | 205 | 57 | 151.2 | 173.8 | 66.38 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247224 | 05FTHLG1 | 18 | 205 | 57 | 151.1 | 173.7 | 66.34 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247232 | 05RIVRG3 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247231 | 05RIVRG2 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 64.77 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 64.28 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | NELSON |  |  | 1
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 63.89 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 63.82 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 197.5 | 95.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Q57 |  |  | 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 63.01 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 62.67 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 61.87 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.00135 |  |  |  | 0.036 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 1.46 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 89.13 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | X2-022 |  |  | 1
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 263.89 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK8 |  |  | 1
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 174.1 | 83.88 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | S06 |  |  | 1
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 83.83 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Z2-087 |  |  | 1
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | U3-002 |  |  | 1
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | V3-007 |  |  | 1
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | U2-090 |  |  | 1
293516 | O-009 E | 0.69 | 222 | 74 | 0 | 169.6 | 81.71 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O09 |  |  | 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 6.79 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 163.2 | 78.63 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | S27 |  |  | 1
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 162.2 | 78.15 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | S28 |  |  | 1
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 244.23 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK7 |  |  | 1
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 77.09 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O50 |  |  | 1
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 76.89 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Q01 3 |  |  | 1
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 73.43 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P10 |  |  | 1
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 227.1 |  |  | 0.00135 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 223.38 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 47.32 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 46.9 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 46.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 46.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 46.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 46.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 45.87 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | S37 |  |  | 1
293519 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | S36 |  |  | 1
930062 | AB1-014 E | 0.38 | 212 | 75 | 0 | 77.5 | 5.66 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AB1-014 |  |  | 1
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 209.23 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet9 |  |  | 1
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 137 | 66.01 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | L05_CE22 |  |  | 1
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 113.7 | 43.42 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 1.03 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 131.6 | 63.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O22 2 |  |  | 1
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 42.01 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 62.88 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AA1-018 |  |  | 1
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 108.1 | 41.28 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O51 1 |  |  | 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O51 2 |  |  | 1
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 106.7 | 40.75 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 60.22 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Q01 4 |  |  | 1
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 90.5 | 104 | 39.72 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253317 | AC1-085 B_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253314 | AC1-085 A_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
936570 | AD2-072_C | 0.6 | 320 | 75 | 0 | 63.75 | 0 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | AD2-072 |  |  | 1
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 88.4 | 101.6 | 38.8 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 38.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 57.82 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | N15 |  |  | 1
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 87.5 | 100.6 | 38.42 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 114.9 | 55.36 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O22 1 |  |  | 1
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 54.49 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC2-176 |  |  | 1
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 41.94 |  |  | 0.00134 |  |  |  | 0.39467 |  | 1 | CAPACITY |  |  |  | 1
924049 | AB2-047 E2 | 0.69 | 222 | 74 | 0 | 109.6 | 52.81 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
924048 | AB2-047 E1 | 0.69 | 222 | 74 | 0 | 107.9 | 51.99 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P36 2 |  |  | 1
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P36 1 |  |  | 1
270186 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 4.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 32.12 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 31.16 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
930042 | AB1-006 E2 | 0.69 | 205 | 74 | 0 | 96.75 | 46.61 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.5 | 30.74 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 46.25 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | S71 |  |  | 1
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 80.3 | 30.67 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 30.59 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 29.56 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 29.06 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76 | 29.02 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 28.99 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 28.91 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 28.87 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 28.8 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 88.2 | 42.49 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | T127 4 |  |  | 1
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 42.26 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O29 1 |  |  | 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 42.21 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P26 |  |  | 1
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 27.95 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 27.88 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 41.39 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P59 |  |  | 1
251955 | 08MADSN4 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251953 | 08MADSN2 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251958 | 08MADSN7 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251957 | 08MADSN6 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251959 | 08MADSN8 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251956 | 08MADSN5 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251952 | 08MADSN1 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251954 | 08MADSN3 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 41.19 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | M24 |  |  | 1
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 84.8 | 40.86 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | T126 2 |  |  | 1
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 84.7 | 40.81 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | T126 3 |  |  | 1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 70.9 | 27.08 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243415 | 05WWVSTA | 69 | 205 | 61 | 69.8 | 96 | 53.26 |  |  | 0.00134 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 26.35 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 39.65 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Q01 21 |  |  | 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80.6 | 38.83 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P46 |  |  | 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P11 1 |  |  | 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | P11 2 |  |  | 1
247943 | T-127 E | 0.69 | 205 | 74 | 0 | 79.8 | 38.45 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | T127 5 |  |  | 1
247903 | 05FR-22G E | 0.69 | 205 | 74 | 0 | 78.8 | 37.97 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Q01 22 |  |  | 1
247900 | 05FR-11G E | 0.6 | 205 | 74 | 0 | 78.3 | 37.72 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Q01 11 |  |  | 1
930041 | AB1-006 E1 | 0.69 | 205 | 74 | 0 | 77.25 | 37.22 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 37.1 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Q01 12 |  |  | 1
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 22.88 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 22.8 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 22.19 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 22.07 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
252507 | AC2-088 C | 0.57 | 212 | 75 | 0 | 38.4 | 2.8 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
253197 | 09PIQUA3 | 69 | 209 | 77 | 0 | 38.3 | 2.77 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 31.32 |  |  | 0.00135 |  |  |  | 0.1042 |  | 1 | NEW | W2-048 |  |  | 1
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 20.47 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | 0.00135 |  |  |  | 0.0975 |  | 1 | MTX | M24 BAT |  |  | 1
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-068 |  |  | 1
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-069 |  |  | 1
936576 | AD2-072_E | 0.6 | 320 | 75 | 0 | 31.25 | 0 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | AD2-072 |  |  | 1
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 19.29 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-165 |  |  | 1
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-166 |  |  | 1
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 28.52 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O35 |  |  | 1
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 28.23 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 18.71 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 18.67 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 18.64 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916000 | 01BACKB E | 34.5 | 201 | 74 | 0 | 57.9 | 27.9 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | K19 |  |  | 1
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 36.56 |  |  | 0.00135 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
932665 | AC2-088 E | 0.57 | 212 | 75 | 0 | 31.6 | 2.31 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 56 | 26.98 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Z1-073 |  |  | 1
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 2.26 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC2-067 |  |  | 1
927209 | AC1-214 E2 | 0.69 | 222 | 74 | 0 | 55.15 | 26.57 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-214 2 |  |  | 1
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 0.39 |  |  | 0.00134 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 23.17 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O29 2 |  |  | 1
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 0.37 |  |  | 0.00134 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 1.93 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC2-067 |  |  | 1
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 22.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | WestBrooklyn |  |  | 1
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 21.97 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | W4-005 |  |  | 1
916212 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 44.75 | 21.56 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Z1-072 |  |  | 1
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 21.3 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | O29 3 |  |  | 1
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 21.15 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | AB1-150 |  |  | 1
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 20.96 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | U2-061 |  |  | 1
272363 | ESS H440 ; R | 138 | 222 | 2 | 0 | 22 | 0 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
274881 | WALNUT RG;1U | 0.69 | 222 | 74 | 0 | 42.4 | 20.43 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O09 |  |  | 1
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 25.91 |  |  | 0.00134 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Q57 |  |  | 1
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O50 |  |  | 1
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 25.52 |  |  | 0.00135 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00134 |  |  |  | 0.0975 |  | 1 | MTX | AA2-123 |  |  | 1
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00134 |  |  |  | 0.0975 |  | 1 | MTX | Z1-108 |  |  | 1
913222 | Y1-054 E | 138 | 212 | 58 | 0 | 20 | 0 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00134 |  |  |  | 0.0975 |  | 1 | MTX | Z1-107 |  |  | 1
237013 | AA2-103 E | 0.48 | 201 | 76 | 0 | 20 | 0 |  |  | 0.00134 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 40.5 | 21.78 |  |  | 0.00135 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 17.25 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | S28 |  |  | 1
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 11.46 |  |  | 0.00134 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 16.91 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O22 2 |  |  | 1
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | S37 |  |  | 1
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | S36 |  |  | 1
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 16.77 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | S27 |  |  | 1
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 24 | 27.6 | 10.54 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243352 | 05NTRDAM | 138 | 205 | 77 | 0 | 57.6 | 41.21 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 10.04 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-165 |  |  | 1
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-166 |  |  | 1
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 14.02 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Q01 4 |  |  | 1
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-068 |  |  | 1
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-069 |  |  | 1
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 13.2 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | N15 |  |  | 1
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 54.8 | 40.8 |  |  | 0.00135 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270681 | BRIGHTSTK; R | 345 | 222 | 74 | 0 | 26 | 12.53 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Z2-087 |  |  | 1
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 12.53 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | U2-090 |  |  | 1
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 12.53 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | V3-007 |  |  | 1
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 12.48 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | S06 |  |  | 1
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 12.38 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Q01 11 |  |  | 1
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 11.56 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 11.56 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | S71 |  |  | 1
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | 0.00134 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 10.98 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Sublette |  |  | 1
270180 | AB1-006 W1 | 0.65 | 205 | 74 | 0 | 22.75 | 10.96 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O51 1 |  |  | 1
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O51 2 |  |  | 1
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 10.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O29 1 |  |  | 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 10.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P26 |  |  | 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 9.73 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | T127 5 |  |  | 1
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P11 1 |  |  | 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P11 2 |  |  | 1
270839 | OTTER CRK; R | 345 | 222 | 74 | 0 | 19.5 | 9.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AA1-018 |  |  | 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 9.35 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P46 |  |  | 1
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.00134 |  |  |  | 0.0975 |  | 1 | MTX | Z1-106 |  |  | 1
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.00134 |  |  |  | 0.05 |  | 1 | MTX | Z1-106 |  |  | 1
251828 | CLNTESP1 | 0 | 212 | 76 | 0 | 10 | 0 |  |  | 0.00134 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 0.15 |  |  | 0.00134 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 8.86 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O22 1 |  |  | 1
251364 | 08LEBANO | 69 | 212 | 77 | 0 | 30.6 | 21.57 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.3 | 8.34 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | K28 |  |  | 1
270201 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 8.14 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC2-176 |  |  | 1
276656 | AB2-047 C2 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
276655 | AB2-047 C1 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 4.93 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 7.37 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | T126 3 |  |  | 1
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P36 1 |  |  | 1
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P36 2 |  |  | 1
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 7.32 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | T126 2 |  |  | 1
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 7.23 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | M24 |  |  | 1
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 14.8 | 7.13 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O35 |  |  | 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 14.4 | 6.94 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Z1-073 |  |  | 1
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 6.36 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 13 | 6.26 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | L05_CE22 |  |  | 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Q01 22 |  |  | 1
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Q01 21 |  |  | 1
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 6.17 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 8.21 |  |  | 0.00135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Q01 3 |  |  | 1
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Q01 12 |  |  | 1
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | 0.00135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 5.78 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O29 2 |  |  | 1
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 5.68 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | T127 4 |  |  | 1
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 5.64 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P59 |  |  | 1
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | 0.00134 |  |  |  | 0.0975 |  | 1 | MTX | Z1-065 |  |  | 1
251387 | 08MDDLTW | 69 | 212 | 77 | 0 | 22.5 | 16.62 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 5.35 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | O29 3 |  |  | 1
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 13.36 |  |  | 0.00135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276618 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 6.71 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 4.91 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | P10 |  |  | 1
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0.41 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | X3-005 |  |  | 1
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 9.7 | 4.67 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Z1-072 |  |  | 1
252509 | AD1-136 C | 0.57 | 212 | 75 | 0 | 5.4 | 0.39 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
276617 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 5.88 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276646 | AC1-214 C2 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 2 |  |  | 1
276645 | AC1-214 C1 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 1 |  |  | 1
935033 | AD1-136 E | 0.57 | 212 | 75 | 0 | 4.6 | 0.34 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 3.9 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | K19 |  |  | 1
237033 | AB1-150 C | 138 | 201 | 74 | 0 | 7.3 | 3.52 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | AB1-150 |  |  | 1
251346 | 08IVYDL1 | 69 | 212 | 77 | 0 | 12.5 | 8.81 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
276602 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 3.42 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | WestBrooklyn |  |  | 1
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 3.13 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | U2-061 |  |  | 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 10.1 | 6.78 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247622 | Y3-025 | 69 | 205 | 64 | 0 | 3.18 | 0 |  |  | 0.00135 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 0.25 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | X3-005 |  |  | 1
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.3 | 6.25 |  |  | 0.00134 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
927208 | AC1-214 E1 | 0.69 | 222 | 74 | 0 | 5.25 | 2.53 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-214 1 |  |  | 1
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 3.33 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
244415 | 05OLIV SLR C | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | OLIV SLR |  |  | 1
247967 | 05OLIV SLR E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | OLIV SLR |  |  | 1
249991 | 08BUFTN1 | 138 | 212 | 77 | 0 | 2.2 | 0 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Z2-113 |  |  | 1
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Z2-113 |  |  | 1
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 4.3 |  |  | 0.00134 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | 0.00135 |  |  |  | 0 |  | 1 | MTX | AB1-055 |  |  | 1
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | 0.00134 |  |  |  | 0 |  | 1 | MTX | Y3-099 |  |  | 1
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | 0.00134 |  |  |  | 0 |  | 1 | MTX | Y3-100 |  |  | 1
250091 | 08RCHLE3 | 138 | 212 | 77 | 0 | 6.7 | 4.72 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 3.89 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 2.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270181 | AB1-006 W2 | 0.69 | 205 | 74 | 0 | 3.25 | 1.57 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
276603 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 1.54 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Sublette |  |  | 1
205921 | AF2-151 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | AF2-151 |  |  | 1
205920 | AF2-101 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | AF2-101 |  |  | 1
342550 | 4BAVARIAN LF | 138 | 320 | 77 | 0 | 4.8 | 3.24 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253234 | 09VERSAL | 69 | 209 | 77 | 0 | 5.4 | 3.91 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.5 | 3.02 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.02 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0.11 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | V4-073 |  |  | 1
243353 | 05OLIVE | 138 | 205 | 77 | 0 | 5 | 3.58 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247604 | X1-042 | 12 | 205 | 64 | 0 | 3.8 | 2.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253029 | 09GRNVIL | 138 | 209 | 77 | 0 | 4.5 | 3.26 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Z2-116 |  |  | 1
247969 | Z2-116 E | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Z2-116 |  |  | 1
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Z2-115 |  |  | 1
247968 | Z2-115 E | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | Z2-115 |  |  | 1
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.6 | 1.44 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
958602 | AF2-151 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | AF2-151 |  |  | 1
958072 | AF2-101 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW | AF2-101 |  |  | 1
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.14 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
341584 | 2GRIFFIN | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
243362 | 05RANDOLPH1 | 138 | 205 | 77 | 0 | 4 | 3.06 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253303 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.07 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | V4-073 |  |  | 1
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 1.75 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251298 | 08CRITDN | 69 | 212 | 77 | 0 | 2.7 | 1.9 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
341329 | 2COLESBURG | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
342031 | 2PACTOLUS | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.48 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
341200 | 2BROMLEYEK | 69 | 320 | 77 | 0 | 2 | 1.35 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
250041 | 08HAMLTN | 138 | 212 | 77 | 0 | 2.2 | 1.55 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251542 | 08VERONA | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | 0.00135 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251269 | 08BEAVR2 | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.3 | 0.72 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246235 | 05BLUFFTON | 69 | 205 | 77 | 0 | 2 | 1.43 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253127 | 09CEDRVL | 69 | 209 | 77 | 0 | 1.8 | 1.3 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246477 | 05NILES | 69 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246476 | 05NILES | 34.5 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 800 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 800 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1330 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | AMG3 |  |  | 1
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274662 | QUAD CITI;1U | 18 | 222 | 48 | 132 | 909.5 | 909.5 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274663 | QUAD CITI;2U | 18 | 222 | 48 | 132 | 911.2 | 911.2 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1300 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | RKG2 |  |  | 1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1356 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | RKG1 |  |  | 1
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1407 | 1407 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | GVG2 |  |  | 1
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1389 | 1389 |  |  | 0.00135 |  |  |  | 0 |  | 1 | CAPACITY | GVG1 |  |  | 1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1308.8 | 1308.8 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | MTG1 |  |  | 1
274657 | BYRON ;2U | 25 | 222 | 45 | 658.5 | 1141.5 | 1141.5 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274656 | BYRON ;1U | 25 | 222 | 45 | 648.1 | 1168.5 | 1168.5 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 734 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 586 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 72.8 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 124.2 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 600 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274687 | WILL CNTY;4U | 20 | 222 | 15 | 49.4 | 510 | 510 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | WILL4 |  |  | 1
274660 | LASCO STA;1U | 25 | 222 | 49 | 135 | 1131.2 | 1131.2 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274661 | LASCO STA;2U | 25 | 222 | 49 | 132 | 1134.8 | 1134.8 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 1154 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 1183 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1186 | 1186 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 1014.5 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235587 | 01HARRN3 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235586 | 01HARRN2 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235585 | 01HARRN1 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 710 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235590 | 01PLEAS1 | 26 | 201 | 16 | 300 | 639 | 0 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235591 | 01PLEAS2 | 26 | 201 | 16 | 350 | 639 | 0 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY | Guernsey |  |  | 1
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 139.32 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 113.43 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 243 | 92.8 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247529 | 05COVRT2 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 2 |  |  | 1
247530 | 05COVRT3 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247528 | 05COVRT1 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 125.75 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | U2-072 |  |  | 1
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 170.9 | 65.27 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 170.8 | 65.23 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 57.21 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 57.17 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149 | 56.9 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247531 | 05COVRT4 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 114.1 | 131.2 | 50.11 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | Covert 2 |  |  | 1
925135 | AB2-170 E | 0.55 | 205 | 75 | 0 | 80.6 | 0 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | 0.00133 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | 0.00133 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.2 | 45.52 |  |  | 0.00133 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 57.82 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | T131 |  |  | 1
247549 | V3-028 C | 345 | 205 | 75 | 0 | 57 | 4.16 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | V3-028 |  |  | 1
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 30.93 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 30.55 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925133 | AB2-170 C | 0.55 | 205 | 75 | 0 | 49.4 | 0 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 30.17 |  |  | 0.00134 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 41.92 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | V1-011 |  |  | 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | R60 2 |  |  | 1
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | R60 1 |  |  | 1
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 84.83 | 40.87 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | R60 3 |  |  | 1
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 76.1 | 36.67 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | R49 |  |  | 1
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 31.8 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | AC1-173 |  |  | 1
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 20.96 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | U1-059 |  |  | 1
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 345.42 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris2 |  |  | 1
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 59.57 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 18.79 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | U2-072 |  |  | 1
253363 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | 0.00134 |  |  |  | 0.05 |  | 1 | MTX | AC1-212 |  |  | 1
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 291.92 |  |  | 0.00134 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris1 |  |  | 1
247521 | T131 | 0.69 | 205 | 74 | 26.1 | 30 | 14.45 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | T131 |  |  | 1
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 8.4 |  |  | 0.00133 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 11.03 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | R49 |  |  | 1
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | 0.00134 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW | V3-028 |  |  | 1
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 0.16 |  |  | 0.00133 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | 0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 7.95 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | R60 3 |  |  | 1
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | R60 2 |  |  | 1
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | R60 1 |  |  | 1
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 7.71 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | W1-056 |  |  | 1
247607 | V1-011 GEN | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | V1-011 |  |  | 1
253178 | 09MINSTR | 69 | 209 | 77 | 0 | 10 | 4.61 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
270191 | AC1-173 C | 0.65 | 205 | 74 | 0 | 9.9 | 4.77 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-173 |  |  | 1
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 4.63 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | U1-059 |  |  | 1
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | 0.00134 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
244357 | 05GRANGER EL | 34.5 | 205 | 2 | 0 | 3.2 | 0 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
270106 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | 0.00134 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 4.3 |  |  | 0.00133 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
243017 | 05HAVILAND1 | 138 | 205 | 77 | 0 | 4.5 | 3.22 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.16 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | W1-056 |  |  | 1
253128 | 09CELINA | 69 | 209 | 77 | 0 | 4 | 2.89 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253160 | 09JCKCEN | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253158 | 09INDI L | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | 0.00134 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253362 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.28 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AC1-212 |  |  | 1
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 749 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 552 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 545.5 |  |  | 0.00134 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 770.1 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 253.85 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 0 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
270122 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 185.22 |  |  | 0.00132 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | NEW | AB1-107 |  |  | 1
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 345.1 | 131.79 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 124.58 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 317.2 | 121.14 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY | OREGON |  |  | 1
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY | RONCO |  |  | 1
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 162.6 | 62.1 |  |  | 0.00132 |  |  |  | 0.036 |  | 1 | CAPACITY | FREMONT |  |  | 1
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | 0.00133 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | 0.00133 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | 0.00133 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | 0.00133 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 159.1 | 60.76 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | V4-010 |  |  | 1
918421 | AA1-056 | 345 | 202 | 58 | 0 | 46 | 0 |  |  | 0.00133 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 101.27 |  |  | 0.00133 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 1.46 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | 0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | 0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 12.53 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | V4-010 |  |  | 1
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 0.19 |  |  | 0.00133 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 0.19 |  |  | 0.00133 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | 0.00132 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | 0.00132 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 10.54 |  |  | 0.00133 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270174 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
943302 | AF1-001 E | 34.5 | 201 | 75 | 0 | 7.25 | 0.53 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEW | AF1-001 |  |  | 1
237039 | AF1-001 C | 34.5 | 201 | 75 | 0 | 6.5 | 0.47 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY | AF1-001 |  |  | 1
247454 | 05OGG STREET | 69 | 205 | 77 | 0 | 10 | 7.16 |  |  | 0.00133 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.77 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 790.2 |  |  | 0.00133 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 896 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00132 |  |  |  | 0.036 |  | 1 | NEW | AB1-069 |  |  | 1
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 280 | 106.93 |  |  | 0.00131 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | 0.00131 |  |  |  | 0.036 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | 0.00131 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
907202 | AC2-103 E2 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
907201 | AC2-103 E1 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 29.6 |  |  | 0.00131 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | 0.00131 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | 0.00131 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 28.95 |  |  | 0.00131 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 28.68 |  |  | 0.00131 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 19.51 |  |  | 0.00131 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 18.94 |  |  | 0.00131 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
916002 | 01ELLIOTTS E | 34.5 | 201 | 74 | 0 | 44.9 | 21.63 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEW | N32 |  |  | 1
237036 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 7.64 |  |  | 0.00131 |  |  |  | 0.1042 |  | 1 | CAPACITY | AD2-002 |  |  | 1
241885 | AC2-103 C1 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
241886 | AC2-103 C2 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
237048 | AF1-022 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY | AF1-022 |  |  | 1
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0.77 |  |  | 0.00131 |  |  |  | 0 |  | 1 | NEW | W1-045 |  |  | 1
943512 | AF1-022 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEW | AF1-022 |  |  | 1
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.1 | 0.47 |  |  | 0.00131 |  |  |  | 0 |  | 1 | CAPACITY | W1-045 |  |  | 1
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 9.4 |  |  | 0.00131 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 7.03 |  |  | 0.00131 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 6.96 |  |  | 0.00131 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 2.65 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY | N32 |  |  | 1
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 0.88 |  |  | 0.00132 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243158 | 05WOOSTE | 138 | 205 | 77 | 0 | 1 | 0.72 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245304 | 05WOOSTER | 23 | 205 | 77 | 0 | 1 | 0.72 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245305 | 05WOOSTER | 69 | 205 | 77 | 0 | 1 | 0.72 |  |  | 0.00132 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | 0.00131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 620.4 |  |  | 0.00131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | 0.00131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241951 | AB1-105 OP | 345 | 202 | 58 | 0 | 850 | 0 |  |  | 0.0013 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | 0.0013 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
253924 | 15SHELL | 138 | 215 | 58 | 0 | 98 | 0 |  |  | 0.0013 |  |  |  | 0.036 |  | 1 | ENERGY | Y3-103 |  |  | 1
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 216.9 |  |  | 0.0013 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 38.8 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253970 | 15BI2 | 13.8 | 215 | 58 | 83.2 | 95.6 | 36.51 |  |  | 0.0013 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
254026 | 15USSILL | 138 | 215 | 77 | 0 | 66 | 27.72 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.5 | 18.52 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 25 | 0.37 |  |  | 0.00131 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
254024 | 15CLAIRT | 138 | 215 | 77 | 0 | 35 | 14.7 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 6.91 |  |  | 0.0013 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
254304 | AE2-114 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AE2-114 |  |  | 1
254305 | AE2-115 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AE2-115 |  |  | 1
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 15.2 | 5.8 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | 0.0013 |  |  |  | 0.036 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0.53 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
941212 | AE2-115 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEW | AE2-115 |  |  | 1
941202 | AE2-114 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEW | AE2-114 |  |  | 1
254303 | AC2-168 C | 138 | 215 | 75 | 0 | 4.4 | 0.32 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 2.69 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254037 | 15UNIVRS | 138 | 215 | 77 | 0 | 1.1 | 0.46 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 627.1 |  |  | 0.00131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 567.5 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253900 | 15BVRVL1 | 22 | 215 | 44 | 781.7 | 898.5 | 898.5 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 899.3 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 156.58 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 307.6 | 117.47 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | 0.0013 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | 0.0013 |  |  |  | 0.036 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
239024 | 02NWCAG5 | 16.5 | 202 | 57 | 23 | 145 | 55.38 |  |  | 0.00129 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239023 | 02NWCAG4 | 14.4 | 202 | 57 | 20 | 93 | 35.52 |  |  | 0.00129 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | 0.0013 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 26.1 | 16.36 |  |  | 0.0013 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 7.55 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEW | Z1-035 |  |  | 1
237046 | AF1-021 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | AF1-021 |  |  | 1
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 13.77 |  |  | 0.00129 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
943502 | AF1-021 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | 0.0013 |  |  |  | 0 |  | 1 | NEW | AF1-021 |  |  | 1
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 0.04 |  |  | 0.00129 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 2.69 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 1.13 |  |  | 0.0013 |  |  |  | 0 |  | 1 | CAPACITY | Z1-035 |  |  | 1
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 124.5 |  |  | 0.00128 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | 0.00128 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | 0.00128 |  |  |  | 0.036 |  | 1 | CAPACITY | T-174 |  |  | 1
239022 | 02NWCAG3 | 14.4 | 202 | 57 | 20 | 92.3 | 35.25 |  |  | 0.00129 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916003 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 13.3 | 6.41 |  |  | 0.00129 |  |  |  | 0 |  | 1 | NEW | K20 |  |  | 1
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 0.82 |  |  | 0.00129 |  |  |  | 0 |  | 1 | CAPACITY | K20 |  |  | 1
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1247 |  |  | 0.00128 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237054 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 195.92 |  |  | 0.00128 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208947 | WSHO CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00128 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237043 | AE2-125 C | 25 | 201 | 75 | 0 | 8.28 | 0.6 |  |  | 0.00127 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
941312 | AE2-125 E | 25 | 201 | 75 | 0 | 5.52 | 0.4 |  |  | 0.00127 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.22 |  |  | 0.00128 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 2.55 |  |  | 0.00127 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
913142 | Y1-033 E OP1 | 0.7 | 226 | 74 | 0 | 34.02 | 20.77 |  |  | 0.00127 |  |  |  | 0 |  | 1 | NEW | Y1-033 |  |  | 1
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 3.05 |  |  | 0.00127 |  |  |  | 0 |  | 1 | CAPACITY | Y1-033 |  |  | 1
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 30 |  |  | 0.00126 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 171.69 |  |  | 0.00126 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 173.6 | 199.5 | 76.19 |  |  | 0.00125 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 167 | 191.9 | 73.29 |  |  | 0.00125 |  |  |  | 0.036 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 164.1 | 188.6 | 72.03 |  |  | 0.00125 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.00126 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.00126 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 89.82 |  |  | 0.00126 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
208942 | HARR CT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | 0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | 0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 7.45 |  |  | 0.00125 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
210323 | AF2-286 E | 13.8 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00126 |  |  |  | 0 |  | 1 | NEW | AF2-286 |  |  | 1
208348 | EELI | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00126 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210022 | LING 2 | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00125 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210322 | AF2-286 BAT | 13.8 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00126 |  |  |  | 0 |  | 1 | MTX | AF2-286 |  |  | 1
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 10.2 |  |  | 0.00125 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | 0.00124 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 25.64 |  |  | 0.00124 |  |  |  | 0 |  | 1 | NEW | K23 |  |  | 1
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 19.54 |  |  | 0.00124 |  |  |  | 0 |  | 1 | NEW | L13 |  |  | 1
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 17.58 |  |  | 0.00124 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | 0.00124 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 3.83 |  |  | 0.00124 |  |  |  | 0.0789 |  | 1 | CAPACITY | ALLEG LD_5 |  |  | 1
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 3.85 |  |  | 0.00124 |  |  |  | 0 |  | 1 | CAPACITY | Lookout Wind |  |  | 1
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 3.6 |  |  | 0.00124 |  |  |  | 0 |  | 1 | CAPACITY | L13 |  |  | 1
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 4.8 | 2.93 |  |  | 0.00124 |  |  |  | 0 |  | 1 | CAPACITY | K23 |  |  | 1
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 1.1 |  |  | 0.00124 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
204662 | 27AES GEN1 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00123 |  |  |  | 0.036 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204663 | 27AES GEN2 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00123 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204664 | 27AES GEN3 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00123 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 4.22 |  |  | 0.00124 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | 0.00123 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.7 |  |  | 0.00123 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 410 | 156.58 |  |  | 0.00122 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235619 | 01SBEND1 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00122 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235621 | 01SBEND3 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00122 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235622 | 01SBEND4 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00122 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235620 | 01SBEND2 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00122 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | 0.00123 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
916004 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.00122 |  |  |  | 0 |  | 1 | NEW | K22 |  |  | 1
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 3.77 |  |  | 0.00122 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
208580 | MGTN 2 | 12.5 | 229 | 77 | 0 | 4.8 | 2.98 |  |  | 0.00123 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.26 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.55 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY | K22 |  |  | 1
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.53 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 852.3 | 852.3 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY | Keys1 |  |  | 1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 851.6 | 851.6 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY | Keys2 |  |  | 1
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 28.78 |  |  | 0.00122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 28.78 |  |  | 0.00122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 44 | 26.86 |  |  | 0.00121 |  |  |  | 0 |  | 1 | NEW | P60 |  |  | 1
203939 | AE1-160 C | 34.5 | 226 | 75 | 0 | 12.7 | 1.17 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY | AE1-160 |  |  | 1
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 21.23 |  |  | 0.00121 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
237052 | AF1-210 C | 25 | 201 | 75 | 0 | 9.54 | 0.7 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY | AF1-210 |  |  | 1
203932 | AE1-123 | 34.5 | 226 | 55 | 0 | 18 | 9.68 |  |  | 0.00121 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
939292 | AE1-160 E | 34.5 | 226 | 75 | 0 | 7.3 | 0.68 |  |  | 0.00122 |  |  |  | 0 |  | 1 | NEW | AE1-160 |  |  | 1
945452 | AF1-210 E | 25 | 201 | 75 | 0 | 6.36 | 0.46 |  |  | 0.00122 |  |  |  | 0 |  | 1 | NEW | AF1-210 |  |  | 1
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 80.2 |  |  | 0.00122 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 5.19 |  |  | 0.00121 |  |  |  | 0 |  | 1 | CAPACITY | P60 |  |  | 1
210319 | WCAR 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00121 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | 0.00122 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 236.66 |  |  | 0.00121 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00121 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00121 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.0012 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.0012 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 26.2 | 15.99 |  |  | 0.00121 |  |  |  | 0 |  | 1 | NEW | K13 |  |  | 1
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 8.66 |  |  | 0.0012 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
203942 | AF2-270 E | 23 | 226 | 75 | 0 | 3.72 | 0.34 |  |  | 0.0012 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
209945 | AF2-278 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00121 |  |  |  | 0 |  | 1 | NEW | AF2-278 |  |  | 1
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 1.95 |  |  | 0.00121 |  |  |  | 0 |  | 1 | CAPACITY | K13 |  |  | 1
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | 0.00121 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
209944 | AF2-278 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00121 |  |  |  | 0 |  | 1 | MTX | AF2-278 |  |  | 1
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 850.6 |  |  | 0.0012 |  |  |  | 0 |  | 1 | CAPACITY | Cone1 |  |  | 1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 850 |  |  | 0.0012 |  |  |  | 0 |  | 1 | CAPACITY | Cone2 |  |  | 1
200805 | 26COLVER13 | 13.2 | 226 | 12 | 95.7 | 110 | 0 |  |  | 0.0012 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200503 | 26C.SLOPE | 115 | 226 | 11 | 17 | 50 | 0 |  |  | 0.0012 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 62.3 | 38.03 |  |  | 0.0012 |  |  |  | 0 |  | 1 | NEW | R32 |  |  | 1
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 54.4 | 33.21 |  |  | 0.0012 |  |  |  | 0 |  | 1 | NEW | O18 |  |  | 1
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 17.22 |  |  | 0.00119 |  |  |  | 0 |  | 1 | NEW | V3-030 |  |  | 1
200809 | 26SITHE | 138 | 226 | 60 | 0 | 36 | 25.31 |  |  | 0.00119 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203940 | AF1-140 C | 23 | 226 | 75 | 0 | 9.78 | 0.9 |  |  | 0.0012 |  |  |  | 0 |  | 1 | CAPACITY | AF1-140 |  |  | 1
944752 | AF1-140 E | 23 | 226 | 75 | 0 | 6.52 | 0.6 |  |  | 0.0012 |  |  |  | 0 |  | 1 | NEW | AF1-140 |  |  | 1
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 7.75 |  |  | 0.0012 |  |  |  | 0 |  | 1 | CAPACITY | R32 |  |  | 1
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.0012 |  |  |  | 0 |  | 1 | CAPACITY | O18 |  |  | 1
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 3.24 |  |  | 0.00119 |  |  |  | 0 |  | 1 | CAPACITY | V3-030 |  |  | 1
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 525.7 |  |  | 0.0012 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 620 |  |  | 0.00119 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 62 | 33.35 |  |  | 0.00118 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 39.07 |  |  | 0.00118 |  |  |  | 0 |  | 1 | NEW | N39 |  |  | 1
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.00118 |  |  |  | 0 |  | 1 | NEW | O38 |  |  | 1
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 31.6 | 19.29 |  |  | 0.00119 |  |  |  | 0 |  | 1 | NEW | Q53 |  |  | 1
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 11.1 | 6.78 |  |  | 0.00118 |  |  |  | 0 |  | 1 | CAPACITY | N39 |  |  | 1
957932 | AF2-087 E | 46 | 226 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00118 |  |  |  | 0 |  | 1 | NEW | AF2-087 |  |  | 1
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.1 | 5.56 |  |  | 0.00118 |  |  |  | 0 |  | 1 | CAPACITY | O38 |  |  | 1
203941 | AF2-087 C | 46 | 226 | 75 | 0 | 3.05 | 0.28 |  |  | 0.00118 |  |  |  | 0 |  | 1 | CAPACITY | AF2-087 |  |  | 1
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 3.91 |  |  | 0.00119 |  |  |  | 0 |  | 1 | CAPACITY | Q53 |  |  | 1
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 614 |  |  | 0.00119 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 650 |  |  | 0.00119 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 260.87 |  |  | 0.00118 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 41.7 | 25.46 |  |  | 0.00117 |  |  |  | 0 |  | 1 | NEW | Q36 |  |  | 1
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 32.1 | 17.27 |  |  | 0.00117 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 5.07 |  |  | 0.00117 |  |  |  | 0 |  | 1 | CAPACITY | Q36 |  |  | 1
203944 | AF2-271 E | 46 | 226 | 75 | 0 | 3 | 0.28 |  |  | 0.00117 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | 0.00117 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 164.5 |  |  | 0.00117 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 155.36 |  |  | 0.00117 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
203946 | AE2-131 C | 34.5 | 226 | 75 | 0 | 12 | 1.11 |  |  | 0.00116 |  |  |  | 0 |  | 1 | CAPACITY | AE2-131 |  |  | 1
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 21.09 |  |  | 0.00117 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
941352 | AE2-131 E | 34.5 | 226 | 75 | 0 | 8 | 0.74 |  |  | 0.00116 |  |  |  | 0 |  | 1 | NEW | AE2-131 |  |  | 1
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 14.76 |  |  | 0.00117 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 3.23 |  |  | 0.00117 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 5 | 4.26 |  |  | 0.00116 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237050 | AF1-155 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00116 |  |  |  | 0 |  | 1 | CAPACITY | AF1-155 |  |  | 1
944902 | AF1-155 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00116 |  |  |  | 0 |  | 1 | NEW | AF1-155 |  |  | 1
205923 | AF2-272 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00115 |  |  |  | 0 |  | 1 | NEW | AF2-272 |  |  | 1
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4 |  |  | 0.00115 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
959813 | AF2-272 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00115 |  |  |  | 0 |  | 1 | MTX | AF2-272 |  |  | 1
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 42.3 |  |  | 0.00115 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237041 | AE2-055 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00114 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
940682 | AE2-055 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00114 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
200722 | 26SHAWVL 2 | 18 | 226 | 30 | 62 | 125 | 117.94 |  |  | 0.00115 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200715 | 26SHAWVL 1 | 18 | 226 | 30 | 62 | 123 | 116.05 |  |  | 0.00115 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 102.41 |  |  | 0.00114 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 102.41 |  |  | 0.00114 |  |  |  | 0.036 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 93.75 |  |  | 0.00114 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
237083 | AE1-147_GEN | 0.6 | 201 | 75 | 0 | 19.98 | 1.46 |  |  | 0.00114 |  |  |  | 0 |  | 1 | CAPACITY | AE1-147 |  |  | 1
200666 | 26SHAWVL 4 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.00114 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200665 | 26SHAWVL 3 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.00114 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
939171 | AE1-147_E | 0.6 | 201 | 75 | 0 | 7.98 | 0.58 |  |  | 0.00114 |  |  |  | 0 |  | 1 | NEW | AE1-147 |  |  | 1
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 75.48 |  |  | 0.00114 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
236828 | 01GRAYMONT | 46 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.00114 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
205926 | AF2-429 E | 34.5 | 227 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00114 |  |  |  | 0 |  | 1 | NEW | AF2-429 |  |  | 1
205925 | AF2-428 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00114 |  |  |  | 0 |  | 1 | NEW | AF2-428 |  |  | 1
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | 0.00114 |  |  |  | 0 |  | 1 | MTX | AC1-025 |  |  | 1
961373 | AF2-428 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00114 |  |  |  | 0 |  | 1 | MTX | AF2-428 |  |  | 1
961383 | AF2-429 BAT | 34.5 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00114 |  |  |  | 0 |  | 1 | MTX | AF2-429 |  |  | 1
205924 | AF2-281 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00112 |  |  |  | 0 |  | 1 | NEW | AF2-281 |  |  | 1
205927 | AF2-430 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00112 |  |  |  | 0 |  | 1 | NEW | AF2-430 |  |  | 1
959903 | AF2-281 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00112 |  |  |  | 0 |  | 1 | MTX | AF2-281 |  |  | 1
961393 | AF2-430 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00112 |  |  |  | 0 |  | 1 | MTX | AF2-430 |  |  | 1
205928 | AF2-431 E | 69 | 227 | 75 | 0 | 1.17 | 0.11 |  |  | 0.00111 |  |  |  | 0 |  | 1 | NEW | AF2-431 |  |  | 1
961403 | AF2-431 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00111 |  |  |  | 0 |  | 1 | MTX | AF2-431 |  |  | 1
209972 | AF2-288 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00111 |  |  |  | 0 |  | 1 | NEW | AF2-288 |  |  | 1
209937 | AF2-287 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00111 |  |  |  | 0 |  | 1 | NEW | AF2-287 |  |  | 1
209971 | AF2-288 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00111 |  |  |  | 0 |  | 1 | MTX | AF2-288 |  |  | 1
209936 | AF2-287 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00111 |  |  |  | 0 |  | 1 | MTX | AF2-287 |  |  | 1
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 34.62 |  |  | 0.00108 |  |  |  | 0 |  | 1 | NEW | Z1-069 |  |  | 1
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 17.1 | 10.44 |  |  | 0.00108 |  |  |  | 0 |  | 1 | CAPACITY | Z1-069 |  |  | 1
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 21.5 | 11.56 |  |  | 0.00101 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 49.15 |  |  | 0.001 |  |  |  | 0 |  | 1 | NEW | P47 |  |  | 1
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.001 |  |  |  | 0 |  | 1 | NEW | K02 |  |  | 1
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.2 | 9.28 |  |  | 0.001 |  |  |  | 0 |  | 1 | CAPACITY | P47 |  |  | 1
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.00099 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 11.3 |  |  | 0.00099 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 11.3 |  |  | 0.00098 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203938 | 26AA2-132 | 34.5 | 226 | 29 | 0 | 19.9 | 0 |  |  | 0.00095 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.00093 |  |  |  | 0.036 |  | 1 | CAPACITY | X1-109 |  |  | 1
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.00093 |  |  |  | 0 |  | 1 | CAPACITY | X1-109 |  |  | 1
203937 | 26AA1-144 G2 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.00094 |  |  |  | 0 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203936 | 26AA1-144 G1 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.00094 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.11 |  |  | 0.00093 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00089 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00089 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203926 | AA2-133 GEN | 13.8 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.00089 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1307 |  |  | 0.00089 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 213 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 205.47 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 130.16 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00087 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00087 |  |  |  | 0.036 |  | 1 | CAPACITY | Hummel |  |  | 1
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 103.81 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00087 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA |  |  | 1
211089 | AF2-277 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00088 |  |  |  | 0 |  | 1 | NEW | AF2-277 |  |  | 1
211088 | AF2-277 BAT | 69 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00088 |  |  |  | 0 |  | 1 | MTX | AF2-277 |  |  | 1
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1288.2 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | 0.00085 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200044 | BETH CT1 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00086 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200048 | BETH CT5 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 73.26 |  |  | 0.00085 |  |  |  | 0 |  | 1 | NEW | P28 |  |  | 1
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 31.73 |  |  | 0.00085 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 11.51 |  |  | 0.00085 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 13.37 |  |  | 0.00085 |  |  |  | 0 |  | 1 | CAPACITY | P28 |  |  | 1
209018 | SUNBIPCT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00082 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212345 | PENS | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00082 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 0.26 |  |  | 0.0008 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208948 | WILL CT | 12.5 | 229 | 55 | 23.1 | 26.6 | 14.31 |  |  | 0.0008 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212455 | AF2-290 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00081 |  |  |  | 0 |  | 1 | NEW | AF2-290 |  |  | 1
212005 | ALWD | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.0008 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212435 | SMIL | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00081 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212454 | AF2-290 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00081 |  |  |  | 0 |  | 1 | MTX | AF2-290 |  |  | 1
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.0008 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.0008 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
921653 | AA2-008 E | 230 | 229 | 58 | 0 | 57 | 0 |  |  | 0.0008 |  |  |  | 0.036 |  | 1 | ENERGY | MOXIE PATRIOT |  |  | 1
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 21.4 | 11.51 |  |  | 0.0008 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212451 | AF2-427 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.0008 |  |  |  | 0 |  | 1 | NEW | AF2-427 |  |  | 1
212464 | AF2-289 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.0008 |  |  |  | 0 |  | 1 | NEW | AF2-289 |  |  | 1
212495 | AF2-284 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.0008 |  |  |  | 0 |  | 1 | NEW | AF2-284 |  |  | 1
212461 | AF2-289 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.0008 |  |  |  | 0 |  | 1 | MTX | AF2-289 |  |  | 1
212450 | AF2-427 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.0008 |  |  |  | 0 |  | 1 | MTX | AF2-427 |  |  | 1
212494 | AF2-284 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.0008 |  |  |  | 0 |  | 1 | MTX | AF2-284 |  |  | 1
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 4.3 |  |  | 0.00079 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 40.29 |  |  | 0.00079 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 30.66 |  |  | 0.00079 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 5.19 |  |  | 0.00079 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 757.9 |  |  | 0.00079 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 758.5 |  |  | 0.00079 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916009 | LOR2_Q27 E | 0.7 | 229 | 74 | 0 | 88.8 | 54.21 |  |  | 0.00077 |  |  |  | 0 |  | 1 | NEW | Q27 |  |  | 1
208941 | FISH CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00077 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916008 | LOR1 E | 0.7 | 229 | 74 | 0 | 23.8 | 14.53 |  |  | 0.00077 |  |  |  | 0 |  | 1 | NEW | N14 |  |  | 1
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 81.14 |  |  | 0.00077 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 77.37 |  |  | 0.00077 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.2 | 6.84 |  |  | 0.00077 |  |  |  | 0 |  | 1 | CAPACITY | Q27 |  |  | 1
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.14 |  |  | 0.00077 |  |  |  | 0 |  | 1 | CAPACITY | N14 |  |  | 1
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1251.7 |  |  | 0.00076 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00075 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00075 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1253.3 |  |  | 0.00074 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.00072 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH5678 |  |  | 1
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 32 |  |  | 0.00072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 31.63 |  |  | 0.00072 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
211375 | BEAC | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00072 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 15.92 |  |  | 0.00072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
211591 | HARW | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00072 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 26.19 |  |  | 0.00072 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 26.03 |  |  | 0.00072 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 23.83 |  |  | 0.00072 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00071 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 15.71 |  |  | 0.00072 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
208944 | JENK CT | 12.5 | 229 | 55 | 24 | 27.6 | 14.85 |  |  | 0.00071 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
946263 | BECR K09 E | 0.69 | 229 | 74 | 0 | 20.7 | 12.64 |  |  | 0.00071 |  |  |  | 0 |  | 1 | NEW | L18 |  |  | 1
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.02 |  |  | 0.00071 |  |  |  | 0 |  | 1 | CAPACITY | L18 |  |  | 1
208940 | ALLE CT | 12.5 | 229 | 55 | 48.7 | 56 | 30.12 |  |  | 0.0007 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
211374 | AVOC | 12.5 | 229 | 77 | 0 | 17.4 | 10.8 |  |  | 0.0007 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
209007 | NOEN IPP | 13.8 | 229 | 12 | 96.9 | 111.4 | 105.11 |  |  | 0.00069 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 52.08 |  |  | 0.00069 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 7.75 |  |  | 0.00069 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00067 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00067 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00067 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 37.91 |  |  | 0.00067 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
209031 | WAYM IPP E | 34.5 | 229 | 74 | 0 | 55.5 | 33.88 |  |  | 0.00067 |  |  |  | 0 |  | 1 | NEW | K21 |  |  | 1
209009 | PEIP 2 | 13.8 | 229 | 56 | 38 | 43.7 | 23.5 |  |  | 0.00067 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
935072 | AD1-143 E1 | 69 | 229 | 74 | 0 | 34.28 | 20.93 |  |  | 0.00068 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | 0.00067 |  |  |  | 0.0975 |  | 1 | MTX | Z2-107 |  |  | 1
211065 | PASP 1_2 C | 13.8 | 229 | 75 | 0 | 8 | 0.74 |  |  | 0.00068 |  |  |  | 0 |  | 1 | CAPACITY | AC1-087 |  |  | 1
942581 | PASP 2 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.00068 |  |  |  | 0 |  | 1 | NEW | AC1-087 |  |  | 1
926082 | PASP 1 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.00068 |  |  |  | 0 |  | 1 | NEW | U4-014 |  |  | 1
935071 | AD1-143 C1 | 69 | 229 | 75 | 0 | 5.72 | 0.53 |  |  | 0.00068 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
209010 | PEIP 1 | 13.8 | 229 | 64 | 17.4 | 26.5 | 21.42 |  |  | 0.00067 |  |  |  | 0.28996 |  | 1 | CAPACITY |  |  |  | 1
935082 | AD1-143 E2 | 69 | 229 | 75 | 0 | 4.8 | 0.44 |  |  | 0.00068 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 5.49 |  |  | 0.00067 |  |  |  | 0 |  | 1 | CAPACITY | K21 |  |  | 1
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 5.34 |  |  | 0.00067 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
211490 | AF2-282 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00067 |  |  |  | 0 |  | 1 | NEW | AF2-282 |  |  | 1
211554 | AF2-283 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00067 |  |  |  | 0 |  | 1 | NEW | AF2-283 |  |  | 1
935081 | AD1-143 C2 | 69 | 229 | 75 | 0 | 0.2 | 0.02 |  |  | 0.00068 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
211489 | AF2-282 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00067 |  |  |  | 0 |  | 1 | MTX | AF2-282 |  |  | 1
211553 | AF2-283 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00067 |  |  |  | 0 |  | 1 | MTX | AF2-283 |  |  | 1
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.47 |  |  | 0.00066 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208946 | MACR CT | 12.5 | 229 | 55 | 61.4 | 70.6 | 37.97 |  |  | 0.00064 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 153 | 82.29 |  |  | 0.00063 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 91.3 | 105 | 56.48 |  |  | 0.00063 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 89.6 | 103 | 55.4 |  |  | 0.00063 |  |  |  | 0.036 |  | 1 | CAPACITY | GILBERT |  |  | 1
206341 | 28GIL 8 | 13.8 | 228 | 58 | 82.2 | 94.5 | 50.83 |  |  | 0.00063 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
211938 | AF2-285 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00064 |  |  |  | 0 |  | 1 | NEW | AF2-285 |  |  | 1
211937 | AF2-285 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00064 |  |  |  | 0 |  | 1 | MTX | AF2-285 |  |  | 1
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00061 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00061 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 128.98 |  |  | 0.00061 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 107.57 |  |  | 0.00061 |  |  |  | 0.036 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 107.57 |  |  | 0.00061 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
207403 | 28AA2-082 E | 34.5 | 228 | 76 | -18 | 18 | 0 |  |  | 0.00059 |  |  |  | 0.05 |  | 1 | MTX | AA2-082 |  |  | 1
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0.4 |  |  | 0.00059 |  |  |  | 0 |  | 1 | NEW | AD2-070 |  |  | 1
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00059 |  |  |  | 0 |  | 1 | CAPACITY | AD2-070 |  |  | 1
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.0006 |  |  |  | 0 |  | 1 | NEW | W4-097 |  |  | 1
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.0006 |  |  |  | 0 |  | 1 | CAPACITY | W4-097 |  |  | 1
207402 | 28AA2-082 C | 34.5 | 228 | 76 | 0 | 2 | 1.19 |  |  | 0.00059 |  |  |  | 0 |  | 1 | CAPACITY | AA2-082 |  |  | 1
208920 | WLPK | 12.5 | 229 | 60 | 35.5 | 40.8 | 28.68 |  |  | 0.00058 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00059 |  |  |  | 0 |  | 1 | NEW | W4-073 |  |  | 1
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 3.04 | 0.28 |  |  | 0.00059 |  |  |  | 0 |  | 1 | CAPACITY | W4-073 |  |  | 1
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00059 |  |  |  | 0 |  | 1 | NEW | W1-127 |  |  | 1
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0.12 |  |  | 0.00059 |  |  |  | 0 |  | 1 | NEW | U2-059 |  |  | 1
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00059 |  |  |  | 0 |  | 1 | CAPACITY | W1-127 |  |  | 1
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00059 |  |  |  | 0 |  | 1 | CAPACITY | U2-059 |  |  | 1
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 3.8 | 2.04 |  |  | 0.00057 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204651 | 27PORT CT | 13.8 | 227 | 55 | 4 | 37 | 19.9 |  |  | 0.00053 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | W3-077 |  |  | 1
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | W2-091 |  |  | 1
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | W3-077 |  |  | 1
916006 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 4.4 | 2.69 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | W2-091 |  |  | 1
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 140.5 | 75.57 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 21 | 11.3 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00049 |  |  |  | 0 |  | 1 | NEW | W2-016 |  |  | 1
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | W2-016 |  |  | 1
206747 | 28DSM_X3-029 | 34.5 | 228 | 58 | 0 | 11.15 | 0 |  |  | 0.00048 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
207462 | AF1-133 C | 34.5 | 228 | 75 | 0 | 12 | 1.11 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | AF1-133 |  |  | 1
944682 | AF1-133 E | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | AF1-133 |  |  | 1
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | 0.00048 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00047 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00047 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00047 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
916005 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 3.45 | 2.11 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | Y2-018 |  |  | 1
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 0.35 | 0.03 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | Y2-018 |  |  | 1
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00046 |  |  |  | 0 |  | 1 | NEW | W3-044 |  |  | 1
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY | W3-044 |  |  | 1
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00044 |  |  |  | 0 |  | 1 | NEW | W4-046 |  |  | 1
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 0.22 |  |  | 0.00044 |  |  |  | 0 |  | 1 | CAPACITY | W4-046 |  |  | 1
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00042 |  |  |  | 0 |  | 1 | NEW | V4-001 |  |  | 1
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00042 |  |  |  | 0 |  | 1 | CAPACITY | V4-001 |  |  | 1
207468 | AF1-326 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.0004 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207455 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | 0.0004 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
207470 | AF1-327 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00038 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00031 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | W4-064 |  |  | 1
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | T20 |  |  | 1
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | W4-064 |  |  | 1
916010 | T20SOLAR E | 0.5 | 230 | 75 | 0 | 2 | 1.22 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | T20 |  |  | 1
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 247.42 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00031 |  |  |  | 0.036 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200054 | ROCKSP 3 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200055 | ROCKSP 4 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200052 | ROCKSP 1 | 18 | 235 | 57 | 145.7 | 167.5 | 90.09 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200053 | ROCKSP 2 | 18 | 235 | 57 | 144.9 | 166.5 | 89.56 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | 0.00031 |  |  |  | 0.0975 |  | 1 | MTX | AA2-061 |  |  | 1
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | 0.00031 |  |  |  | 0.0975 |  | 1 | MTX | AA2-060 |  |  | 1
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | X1-012 |  |  | 1
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0.57 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | BeaverRun |  |  | 1
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0.43 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | W3-110 |  |  | 1
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | X1-012 |  |  | 1
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 0.26 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | W3-110 |  |  | 1
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY | BeaverRun |  |  | 1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AC2-175 |  |  | 1
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0.12 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AE1-081 |  |  | 1
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.09 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY | AE1-081 |  |  | 1
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | W2-050 |  |  | 1
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 256.8 | 138.13 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 137.8 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W2-080 |  |  | 1
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W2-080 |  |  | 1
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0.46 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V3-070 |  |  | 1
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | V3-070 |  |  | 1
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | W3-029 |  |  | 1
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0.93 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | W3-003 |  |  | 1
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0.38 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | X2-075 |  |  | 1
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | W3-029 |  |  | 1
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 0.21 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | X2-075 |  |  | 1
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | W1-132 |  |  | 1
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | V4-069 |  |  | 1
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | W2-061 |  |  | 1
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | V4-070 |  |  | 1
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | V4-070 |  |  | 1
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | V4-069 |  |  | 1
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | W2-061 |  |  | 1
219913 | AD2-042 E | 26.4 | 231 | 75 | 0 | 8.2 | 0.76 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | AD2-042 |  |  | 1
219915 | AD2-027 E | 26.4 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | AD2-027 |  |  | 1
219912 | AD2-042 C | 26.4 | 231 | 75 | 0 | 5 | 0.46 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | AD2-042 |  |  | 1
219914 | AD2-027 C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | AD2-027 |  |  | 1
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.65 | 3.95 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
207456 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | 0.00019 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.43 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
207466 | AF1-324 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00018 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00018 |  |  |  | 0 |  | 1 | NEW | X1-095 |  |  | 1
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00018 |  |  |  | 0 |  | 1 | CAPACITY | X1-095 |  |  | 1
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 25.82 |  |  | 0.00016 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.55 | 0.14 |  |  | 0.00013 |  |  |  | 0 |  | 1 | NEW | AC1-030 |  |  | 1
219907 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | 0.00013 |  |  |  | 0 |  | 1 | CAPACITY | AC1-030 |  |  | 1
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0.05 |  |  | 0.00013 |  |  |  | 0 |  | 1 | NEW | X1-071 |  |  | 1
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.03 |  |  | 0.00013 |  |  |  | 0 |  | 1 | CAPACITY | X1-071 |  |  | 1
207458 | AD2-210_C | 34.5 | 228 | 76 | 0 | 8 | 0 |  |  | 0.00012 |  |  |  | 0.05 |  | 1 | NEW |  |  |  | 1
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0.21 |  |  | 6e-05 |  |  |  | 0 |  | 1 | NEW | AC1-017 |  |  | 1
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0.2 |  |  | 6e-05 |  |  |  | 0 |  | 1 | NEW | X1-070 |  |  | 1
219906 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | 6e-05 |  |  |  | 0 |  | 1 | CAPACITY | AC1-017 |  |  | 1
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.11 |  |  | 6e-05 |  |  |  | 0 |  | 1 | CAPACITY | X1-070 |  |  | 1
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0.06 |  |  | 6e-05 |  |  |  | 0 |  | 1 | NEW | AB1-021 |  |  | 1
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 6e-05 |  |  |  | 0 |  | 1 | CAPACITY | AB1-021 |  |  | 1
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 43.08 |  |  | 5e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 35.07 |  |  | 5e-05 |  |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 16.18 |  |  | 5e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.2 | 7.55 |  |  | 5e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 5e-05 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
219765 | PARADISE E | 13 | 231 | 75 | 0 | 3.2 | 0.3 |  |  | 5e-05 |  |  |  | 0 |  | 1 | NEW | U4-036 |  |  | 1
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | 5e-05 |  |  |  | 0 |  | 1 | MTX | X2-013 |  |  | 1
219904 | AC1-010 C | 26.4 | 231 | 75 | 0 | 2.2 | 0.2 |  |  | 5e-05 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 5e-05 |  |  |  | 0 |  | 1 | CAPACITY | U4-036 |  |  | 1
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 139.31 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 50.99 |  |  | 3e-05 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 3e-05 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 3e-05 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 3e-05 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 3e-05 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 43.57 |  |  | 3e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 18.4 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217831 | PB_NUTCLIF | 26 | 231 | 77 | 0 | 10.7 | 7.21 |  |  | 3e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 4e-05 |  |  |  | 0 |  | 1 | NEW | V2-025 |  |  | 1
217194 | REDH C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 4e-05 |  |  |  | 0 |  | 1 | CAPACITY | V2-025 |  |  | 1
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.24 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0.03 |  |  | 3e-05 |  |  |  | 0 |  | 1 | NEW | V3-065 |  |  | 1
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | 3e-05 |  |  |  | 0 |  | 1 | NEW | V3-066 |  |  | 1
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.02 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | V3-065 |  |  | 1
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | V3-066 |  |  | 1
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 135.65 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 96.22 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 96.22 |  |  | 3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217850 | MONTCLAIR_U | 26 | 231 | 77 | 0 | 10.6 | 7.15 |  |  | 3e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.15 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0.15 |  |  | 3e-05 |  |  |  | 0 |  | 1 | NEW | W4-059 |  |  | 1
219910 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0.14 |  |  | 3e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | 3e-05 |  |  |  | 0 |  | 1 | NEW | X1-072 |  |  | 1
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | X1-072 |  |  | 1
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.02 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | W4-059 |  |  | 1
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 113.38 |  |  | 2e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 2e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 1e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 1e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 1e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 1e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 22.59 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 16.14 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 1.15 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW | W3-080 |  |  | 1
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW | W2-102 |  |  | 1
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW | W4-103 |  |  | 1
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y3-026 |  |  | 1
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW | Y3-026 |  |  | 1
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 0.34 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY | W3-080 |  |  | 1
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 3.56 | 0.33 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY | W4-103 |  |  | 1
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW | Y2-081 |  |  | 1
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY | W2-102 |  |  | 1
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y2-081 |  |  | 1
219685 | NATIONAL_GYP | 26 | 231 | 77 | 0 | 2.8 | 1.89 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219922 | AF1-261 | 26.4 | 231 | 75 | 0 | 0.9 | 0.61 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217825 | UMD_NJ | 26 | 231 | 77 | 0 | 10.5 | 7.08 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
930243 | AB1-063_E | 69 | 231 | 0 | 0 | 0 | -0.7 |  |  | 0 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0.06 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW | X2-087 |  |  | 1
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0.05 |  |  | 0 |  |  |  | 0 |  | 1 | NEW | V3-067 |  |  | 1
219917 | AB1-063 E | 69 | 231 | 75 | 0 | 0.4 | 0.04 |  |  | 0 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY | X2-087 |  |  | 1
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.03 |  |  | 0 |  |  |  | 0 |  | 1 | CAPACITY | V3-067 |  |  | 1
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0.03 |  |  | 0 |  |  |  | 0 |  | 1 | NEW | V3-068 |  |  | 1
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 0 |  |  |  | 0 |  | 1 | CAPACITY | V3-068 |  |  | 1
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218672 | KENILWRTH E | 26.4 | 231 | 65 | 0 | 8 | 0 |  |  | -2e-05 |  |  |  | 0.1097 |  | 1 | NEW |  |  |  | 1
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 3.55 |  |  | -2e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | -1e-05 |  |  |  | 0 |  | 1 | NEW | W1-101 |  |  | 1
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.05 |  |  | -1e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-101 |  |  | 1
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | 0
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 302.3 | 162.6 |  |  | -3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | -3e-05 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 45.24 |  |  | -3e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 72.1 | 82.9 | 44.59 |  |  | -3e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 25.21 |  |  | -3e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
936193 | AD2-025_E | 13.2 | 231 | 76 | 0 | 2 | 0 |  |  | -3e-05 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
219916 | AD2-025 E | 13.2 | 231 | 76 | -2 | 2 | 0 |  |  | -3e-05 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
218450 | LINSOLAR E | 26.4 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | -3e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219138 | THOSOLAR E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | -3e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218449 | LINSOLAR C | 26.4 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | -3e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219137 | THOSOLAR C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -3e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0.04 |  |  | -4e-05 |  |  |  | 0 |  | 1 | NEW | W2-036 |  |  | 1
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | W2-036 |  |  | 1
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | 0
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0.23 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | W1-121 Z |  |  | 1
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Y |  |  | 1
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Z |  |  | 1
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | W1-121 Y |  |  | 1
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 302.1 | 162.49 |  |  | -6e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
990902 | TOSCO_E | 18 | 231 | 2 | 0 | 137.5 | 0 |  |  | -5e-05 |  |  |  | 0.1042 |  | 1 | ENERGY | Tosco |  |  | 1
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | -6e-05 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | -6e-05 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | -6e-05 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | -6e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | -6e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218344 | TOSCO_G6 | 18 | 231 | 2 | 37 | 42.5 | 22.86 |  |  | -5e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY | Tosco |  |  | 1
219728 | YARDVSOLFA E | 13.2 | 231 | 75 | 0 | 2.42 | 0.22 |  |  | -6e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219727 | YARDVSOLFA C | 13.2 | 231 | 75 | 0 | 1.48 | 0.14 |  |  | -6e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 181.64 |  |  | -7e-05 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | -7e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Q90 |  |  | 1
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | -7e-05 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
218780 | PRINCENTON_U | 26 | 231 | 77 | 0 | 31.56 | 21.27 |  |  | -8e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0.45 |  |  | -8e-05 |  |  |  | 0 |  | 1 | NEW | Z1-096 |  |  | 1
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 0.28 |  |  | -8e-05 |  |  |  | 0 |  | 1 | CAPACITY | Z1-096 |  |  | 1
219622 | TRENT_BIOGAS | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | -8e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219001 | SEWAREN7GT | 25 | 231 | 58 | 0 | 324.6 | 174.59 |  |  | -9e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
219002 | SEWAREN7ST | 18 | 231 | 58 | 0 | 216.4 | 116.4 |  |  | -9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -9e-05 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -9e-05 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
217212 | AMBOY SO E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.0001 |  |  |  | 0 |  | 1 | NEW | V3-069 |  |  | 1
217213 | AMBOY SO C | 13.2 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.0001 |  |  |  | 0 |  | 1 | CAPACITY | V3-069 |  |  | 1
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 43.9 |  |  | -0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 0 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | NEW |  |  |  | 1
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0.38 |  |  | -0.0001 |  |  |  | 0 |  | 1 | NEW | AB1-139 |  |  | 1
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0.36 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | V2-009 3 |  |  | 1
219908 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 0.23 |  |  | -0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AB1-139 |  |  | 1
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 0.22 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 3 |  |  | 1
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0.22 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | V2-009 4 |  |  | 1
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 4 |  |  | 1
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.0001 |  |  |  | 0 |  | 1 | NEW | AE1-041 |  |  | 1
219920 | AE1-041 EBAT | 26.4 | 231 | 76 | -0.5 | 0.5 | 0 |  |  | -0.0001 |  |  |  | 0 |  | 1 | MTX | AE1-041 |  |  | 1
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0.03 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | W2-052 |  |  | 1
219919 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | -0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AE1-041 |  |  | 1
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | W2-052 |  |  | 1
218527 | CNTRALGAS2 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218526 | CNTRALGAS2 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0.07 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0.06 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
932032 | AC2-009 E | 69 | 231 | 75 | -0.5 | 0.49 | 0.05 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AC2-009 |  |  | 1
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AA2-058 |  |  | 1
219918 | AC2-009 C | 69 | 231 | 75 | -0.1 | 0.1 | 0.01 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AC2-009 |  |  | 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | V3-024 |  |  | 1
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0.28 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | V2-009 2 |  |  | 1
219679 | NRGCENTER E | 13.2 | 231 | 55 | 0 | 2 | 0 |  |  | -0.00012 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V3-024 |  |  | 1
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 0.17 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 2 |  |  | 1
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0.16 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | W3-124 |  |  | 1
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0.14 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | V2-009 1 |  |  | 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | X2-088 |  |  | 1
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.00012 |  |  |  | 0 |  | 1 | MTX | Z1-082 |  |  | 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.1 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W3-124 |  |  | 1
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 1 |  |  | 1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | X2-088 |  |  | 1
924132 | AB2-057 E | 26 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | -0.00014 |  |  |  | 0 |  | 1 | NEW | AB2-057 |  |  | 1
219903 | AB2-057 C | 26 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.00014 |  |  |  | 0 |  | 1 | CAPACITY | AB2-057 |  |  | 1
217199 | V3-059 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | -0.00014 |  |  |  | 0 |  | 1 | NEW | V3-059 |  |  | 1
217198 | V3-058 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | -0.00014 |  |  |  | 0 |  | 1 | NEW | V3-058 |  |  | 1
218455 | CINNBAY_CGEN | 26.4 | 231 | 64 | 0 | 9 | 7.66 |  |  | -0.00014 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218781 | BRIS_MYERS | 26 | 231 | 77 | 0 | 3 | 2.02 |  |  | -0.00014 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218525 | CNTRALGAS1 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.00015 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0.12 |  |  | -0.00015 |  |  |  | 0 |  | 1 | NEW | X2-089 |  |  | 1
218524 | CNTRALGAS1 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | -0.00015 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.07 |  |  | -0.00015 |  |  |  | 0 |  | 1 | CAPACITY | X2-089 |  |  | 1
219650 | TRENT_COLLEG | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | -0.00019 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219818 | TRENTONSOL E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | -0.00019 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219817 | TRENTONSOL C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -0.00019 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0.04 |  |  | -0.00019 |  |  |  | 0 |  | 1 | NEW | W4-058 |  |  | 1
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | -0.00019 |  |  |  | 0 |  | 1 | CAPACITY | W4-058 |  |  | 1
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0.28 |  |  | -0.00021 |  |  |  | 0 |  | 1 | NEW | X3-075 |  |  | 1
219921 | AF1-264 | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.00021 |  |  |  | 0 |  | 1 | CAPACITY | X3-075 |  |  | 1
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0003
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 164.59 |  |  | -0.0003 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | -0.0003 |  |  |  | 0.036 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | -0.0003 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 99.6 | 114.5 | 61.59 |  |  | -0.0003 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 93.2 | 107.1 | 57.61 |  |  | -0.0003 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0.22 |  |  | -0.00031 |  |  |  | 0 |  | 1 | NEW | Y3-087 |  |  | 1
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 0.21 |  |  | -0.00031 |  |  |  | 0 |  | 1 | CAPACITY | Y3-087 |  |  | 1
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 133.39 |  |  | -0.00033 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | -0.00033 |  |  |  | 0.036 |  | 1 | CAPACITY | RED OAK |  |  | 1
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | -0.00034 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 94.67 |  |  | -0.00034 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206327 | 28S RIV G1 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | -0.00035 |  |  |  | 0.036 |  | 1 | CAPACITY | S RIV |  |  | 1
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | -0.00035 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 85.3 | 98 | 52.71 |  |  | -0.00035 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 29.23 |  |  | -0.00035 |  |  |  | 0.036 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 29.23 |  |  | -0.00035 |  |  |  | 0 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  |  |  | -0.0004
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEW | W4-060 |  |  | 1
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | -0.00046 |  |  |  | 0 |  | 1 | CAPACITY | W4-060 |  |  | 1
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0.23 |  |  | -0.00054 |  |  |  | 0 |  | 1 | NEW | W1-112 |  |  | 1
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.17 | 0.11 |  |  | -0.00054 |  |  |  | 0 |  | 1 | CAPACITY | W1-112 |  |  | 1
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 34.26 |  |  | -0.00058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -0.00062 |  |  |  | 0 |  | 1 | NEW | AC1-207 |  |  | 1
207420 | AC1-207 TAP | 34.5 | 228 | 75 | 0 | 4.9 | 0.45 |  |  | -0.00062 |  |  |  | 0 |  | 1 | CAPACITY | AC1-207 |  |  | 1
207454 | AA2-184 E | 34.5 | 228 | 75 | 0 | 11.6 | 1.07 |  |  | -0.00062 |  |  |  | 0 |  | 1 | NEW | BenMoreell |  |  | 1
207464 | AF1-023 | 34.5 | 228 | 75 | 0 | 8.4 | 0.78 |  |  | -0.00062 |  |  |  | 0 |  | 1 | CAPACITY | BenMoreell |  |  | 1
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0.52 |  |  | -0.00063 |  |  |  | 0 |  | 1 | NEW | W2-078 |  |  | 1
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -0.00063 |  |  |  | 0 |  | 1 | NEW | W1-113 |  |  | 1
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00063 |  |  |  | 0 |  | 1 | CAPACITY | W2-078 |  |  | 1
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 0.26 |  |  | -0.00063 |  |  |  | 0 |  | 1 | CAPACITY | W1-113 |  |  | 1
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.00063 |  |  |  | 0 |  | 1 | NEW | W1-124 |  |  | 1
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 3.8 | 0.35 |  |  | -0.00063 |  |  |  | 0 |  | 1 | CAPACITY | W1-124 |  |  | 1
207419 | AB2-139 E | 34.5 | 228 | 76 | -0.2 | 0.21 | 0 |  |  | -0.00063 |  |  |  | 0 |  | 1 | MTX | AB2-139 |  |  | 1
207461 | AE2-057 C | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -0.00066 |  |  |  | 0 |  | 1 | CAPACITY | AE2-057 |  |  | 1
940702 | AE2-057 E | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -0.00066 |  |  |  | 0 |  | 1 | NEW | AE2-057 |  |  | 1
228471 | VALERO1 | 13.8 | 234 | 58 | 19.1 | 22 | 11.83 |  |  | -0.00067 |  |  |  | 0.036 |  | 1 | CAPACITY | Valero |  |  | 1
228484 | VALERO4 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.00067 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228473 | VALERO3 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.00067 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228472 | VALERO2 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.00067 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
901032 | W1-024E OP1 | 34.5 | 228 | 75 | 0 | 2.5 | 0.23 |  |  | -0.00066 |  |  |  | 0 |  | 1 | NEW | W1-024 |  |  | 1
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 0.14 |  |  | -0.00066 |  |  |  | 0 |  | 1 | CAPACITY | W1-024 |  |  | 1
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0.98 |  |  | -0.00068 |  |  |  | 0 |  | 1 | NEW | X1-037 |  |  | 1
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 0.39 |  |  | -0.00068 |  |  |  | 0 |  | 1 | CAPACITY | X1-037 |  |  | 1
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -0.00067 |  |  |  | 0 |  | 1 | NEW | X4-031 |  |  | 1
940922 | AE2-081 E | 34.5 | 228 | 75 | 0 | 1.75 | 0.16 |  |  | -0.00068 |  |  |  | 0 |  | 1 | NEW | AE2-081 |  |  | 1
207460 | AE2-056 C | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | -0.00068 |  |  |  | 0 |  | 1 | CAPACITY | AE2-056 |  |  | 1
207463 | AE2-081 C | 34.5 | 228 | 75 | 0 | 1.57 | 0.14 |  |  | -0.00068 |  |  |  | 0 |  | 1 | CAPACITY | AE2-081 |  |  | 1
940692 | AE2-056 E | 34.5 | 228 | 75 | 0 | 1.4 | 0.13 |  |  | -0.00068 |  |  |  | 0 |  | 1 | NEW | AE2-056 |  |  | 1
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | -0.00068 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.0007 |  |  |  | 0 |  | 1 | NEW | W1-032 |  |  | 1
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.0007 |  |  |  | 0 |  | 1 | CAPACITY | W1-032 |  |  | 1
207451 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -0.00078 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -0.00078 |  |  |  | 0 |  | 1 | NEW | W3-079 |  |  | 1
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.00078 |  |  |  | 0 |  | 1 | CAPACITY | W3-079 |  |  | 1
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00079 |  |  |  | 0 |  | 1 | NEW | Y2-051 |  |  | 1
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.00079 |  |  |  | 0 |  | 1 | CAPACITY | Y2-051 |  |  | 1
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 206.63 |  |  | -0.00083 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00083 |  |  |  | 0 |  | 1 | NEW | X1-085 |  |  | 1
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.00083 |  |  |  | 0 |  | 1 | CAPACITY | X1-085 |  |  | 1
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.00086 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.00086 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 76.9 | 88.4 | 47.55 |  |  | -0.00086 |  |  |  | 0.036 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.00086 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.00086 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
207179 | 28SIXFLAGS | 34.5 | 228 | 77 | 0 | 17 | 0 |  |  | -0.00086 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
207450 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -0.00087 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.00086 |  |  |  | 0 |  | 1 | MTX | AA1-060 |  |  | 1
923293 | AB1-138 E | 0.36 | 228 | 75 | 0 | 6 | 0.56 |  |  | -0.00091 |  |  |  | 0 |  | 1 | NEW | AB1-138 |  |  | 1
206280 | 28LAKEHURS | 34.5 | 228 | 55 | 0 | 13.7 | 10.22 |  |  | -0.00091 |  |  |  | 0.17131 |  | 1 | CAPACITY |  |  |  | 1
207445 | AB1-138 C | 0.38 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.00091 |  |  |  | 0 |  | 1 | CAPACITY | AB1-138 |  |  | 1
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.0009 |  |  |  | 0 |  | 1 | NEW | AB1-025 S |  |  | 1
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.0009 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 S |  |  | 1
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.00092 |  |  |  | 0 |  | 1 | NEW | W2-082 |  |  | 1
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -0.00092 |  |  |  | 0 |  | 1 | NEW | W4-025 |  |  | 1
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | -0.00092 |  |  |  | 0 |  | 1 | NEW | W2-019 |  |  | 1
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00092 |  |  |  | 0 |  | 1 | NEW | W1-129 |  |  | 1
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY | W2-082 |  |  | 1
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00092 |  |  |  | 0 |  | 1 | NEW | X4-015 |  |  | 1
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 0.24 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY | W4-025 |  |  | 1
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 0.21 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY | W2-019 |  |  | 1
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY | W1-129 |  |  | 1
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY | X4-015 |  |  | 1
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0.75 |  |  | -0.00093 |  |  |  | 0 |  | 1 | NEW | Z2-102 |  |  | 1
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.00093 |  |  |  | 0 |  | 1 | NEW | W1-120 |  |  | 1
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.00093 |  |  |  | 0 |  | 1 | NEW | W1-119 |  |  | 1
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 0.46 |  |  | -0.00093 |  |  |  | 0 |  | 1 | CAPACITY | Z2-102 |  |  | 1
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.00093 |  |  |  | 0 |  | 1 | CAPACITY | W1-119 |  |  | 1
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.00093 |  |  |  | 0 |  | 1 | CAPACITY | W1-120 |  |  | 1
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0.16 |  |  | -0.00096 |  |  |  | 0 |  | 1 | NEW | W2-071 |  |  | 1
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.1 |  |  | -0.00096 |  |  |  | 0 |  | 1 | CAPACITY | W2-071 |  |  | 1
939122 | AE1-142 E O1 | 34.5 | 228 | 75 | 0 | 11.8 | 1.09 |  |  | -0.00098 |  |  |  | 0 |  | 1 | NEW | AE1-142 |  |  | 1
207459 | AE1-142 C O1 | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -0.00098 |  |  |  | 0 |  | 1 | CAPACITY | AE1-142 |  |  | 1
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0.17 |  |  | -0.00105 |  |  |  | 0 |  | 1 | NEW | V4-005 |  |  | 1
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.1 |  |  | -0.00105 |  |  |  | 0 |  | 1 | CAPACITY | V4-005 |  |  | 1
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 57.7 | 31.03 |  |  | -0.00105 |  |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 57.6 | 30.98 |  |  | -0.00105 |  |  |  | 0.036 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0.63 |  |  | -0.00108 |  |  |  | 0 |  | 1 | NEW | W2-056 |  |  | 1
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 0.39 |  |  | -0.00108 |  |  |  | 0 |  | 1 | CAPACITY | W2-056 |  |  | 1
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.00108 |  |  |  | 0 |  | 1 | NEW | AB1-025 N |  |  | 1
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.00108 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 N |  |  | 1
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | -0.00109 |  |  |  | 0 |  | 1 | NEW | Y1-075 |  |  | 1
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.00109 |  |  |  | 0 |  | 1 | CAPACITY | Y1-075 |  |  | 1
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 18.29 |  |  | -0.00116 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 16.67 |  |  | -0.00116 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.3 |  |  |  | -0.0013
TILTON | PJM->LTFIMP_TILTON |  |  | LTF |  | 63 |  |  |  | -0.0013
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  |  |  | -0.0013
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  |  |  | -0.0013
MDU | PJM->LTFIMP_MDU |  |  | LTF |  | 10.1 |  |  |  | -0.0013
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  |  |  | -0.0014
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  |  |  | -0.0014
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  |  |  | -0.0014
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  |  |  | -0.0014
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  |  |  | -0.0014
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  |  |  | -0.0014
228357 | V2-046E | 12.9 | 234 | 75 | 0 | 12.9 | 1.19 |  |  | -0.00165 |  |  |  | 0 |  | 1 | NEW | V2-046 |  |  | 1
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 0.72 |  |  | -0.00165 |  |  |  | 0 |  | 1 | CAPACITY | V2-046 |  |  | 1
230410 | AE1-218 E O1 | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.00168 |  |  |  | 0 |  | 1 | NEW | AE1-218 |  |  | 1
230409 | AE1-218 C O1 | 12.9 | 234 | 75 | 0 | 0.8 | 0.07 |  |  | -0.00168 |  |  |  | 0 |  | 1 | CAPACITY | AE1-218 |  |  | 1
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 226.44 |  |  | -0.00171 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
230403 | AB1-116 E | 12.9 | 234 | 28 | 0 | 0.78 | 0 |  |  | -0.00177 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228721 | V2-035E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.00184 |  |  |  | 0 |  | 1 | NEW | V2-035 |  |  | 1
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.07 |  |  | -0.00184 |  |  |  | 0 |  | 1 | CAPACITY | V2-035 |  |  | 1
230408 | AD2-065 E | 12.9 | 234 | 75 | 0 | 3.03 | 0.28 |  |  | -0.00191 |  |  |  | 0 |  | 1 | NEW | AD2-065 |  |  | 1
230407 | AD2-065_C | 12.9 | 234 | 75 | 0 | 1.08 | 0.1 |  |  | -0.00191 |  |  |  | 0 |  | 1 | CAPACITY | AD2-065 |  |  | 1
924052 | AB2-049 E | 69 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.00193 |  |  |  | 0 |  | 1 | NEW | AB2-049 |  |  | 1
230415 | AB2-049 C | 69 | 234 | 75 | 0 | 1.14 | 0.1 |  |  | -0.00193 |  |  |  | 0 |  | 1 | CAPACITY | AB2-049 |  |  | 1
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0.53 |  |  | -0.00194 |  |  |  | 0 |  | 1 | NEW | W1-130 |  |  | 1
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 0.3 |  |  | -0.00194 |  |  |  | 0 |  | 1 | CAPACITY | W1-130 |  |  | 1
228733 | AB1-119 E | 12.9 | 234 | 28 | 0 | 0.73 | 0 |  |  | -0.00198 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.1 | 39.2 | 21.08 |  |  | -0.00218 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 20.22 |  |  | -0.00218 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.00219 |  |  |  | 0 |  | 1 | NEW | V4-054 |  |  | 1
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 0.35 |  |  | -0.00219 |  |  |  | 0 |  | 1 | CAPACITY | V4-054 |  |  | 1
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 3 | 2.55 |  |  | -0.00218 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
230414 | AF1-041 E | 69 | 234 | 75 | 0 | 2.4 | 0.22 |  |  | -0.00236 |  |  |  | 0 |  | 1 | NEW | AF1-041 |  |  | 1
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0.13 |  |  | -0.00235 |  |  |  | 0 |  | 1 | NEW | AB1-001 |  |  | 1
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.08 |  |  | -0.00235 |  |  |  | 0 |  | 1 | CAPACITY | AB1-001 |  |  | 1
228014 | PVILLEG | 0.48 | 234 | 65 | 0 | 1.3 | 0.77 |  |  | -0.00235 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
227801 | ONTC&DCT | 13.8 | 234 | 75 | 33.6 | 38.6 | 3.57 |  |  | -0.00237 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | -0.00237 |  |  |  | 0.30476 |  | 1 | ENERGY |  |  |  | 1
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | -0.00237 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 30.66 |  |  | -0.00239 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0.56 |  |  | -0.0024 |  |  |  | 0 |  | 1 | NEW | W2-030 |  |  | 1
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 0.34 |  |  | -0.0024 |  |  |  | 0 |  | 1 | CAPACITY | W2-030 |  |  | 1
227928 | V4-067E | 12.9 | 234 | 75 | 0 | 1.6 | 0.15 |  |  | -0.0024 |  |  |  | 0 |  | 1 | NEW | V4-067 |  |  | 1
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.0024 |  |  |  | 0 |  | 1 | NEW | AB2-122 |  |  | 1
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.09 |  |  | -0.0024 |  |  |  | 0 |  | 1 | CAPACITY | V4-067 |  |  | 1
230413 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.06 |  |  | -0.0024 |  |  |  | 0 |  | 1 | CAPACITY | AB2-122 |  |  | 1
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.1 | 12.43 |  |  | -0.00242 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 29.85 |  |  | -0.00246 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 45.13 |  |  | -0.00264 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.7 |  |  | -0.00266 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
228712 | V2-041E | 13.2 | 234 | 75 | 0 | 2.48 | 0.23 |  |  | -0.00269 |  |  |  | 0 |  | 1 | NEW | V2-041 |  |  | 1
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 0.14 |  |  | -0.00269 |  |  |  | 0 |  | 1 | CAPACITY | V2-041 |  |  | 1
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 45.99 |  |  | -0.00276 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228203 | P06 | 13.8 | 234 | 57 | 78 | 89.7 | 48.25 |  |  | -0.00289 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | -0.00655 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 1138.9 |  |  | -0.00655 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 1145.8 |  |  | -0.00655 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1178.3 |  |  | -0.0066 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 102.2 |  |  | -0.00711 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.00711 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.00711 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.00711 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | -0.10541 |  |  |  | 0.036 |  | 1 | NEW | Garrison |  |  | 1
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 103.81 |  |  | -0.10541 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 62.5 |  |  | -0.10541 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
232901 | NORTHST | 69 | 235 | 56 | 5 | 45 | 24.2 |  |  | -0.10541 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 14.34 |  |  | -0.10541 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 26.36 |  |  | -0.13427 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 25.82 |  |  | -0.13427 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 111.97 |  |  | -0.1845 |  |  |  | 0 |  | 1 | NEW | AB1-056 |  |  | 1
233906 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 39.32 |  |  | -0.1845 |  |  |  | 0 |  | 1 | CAPACITY | AB1-056 |  |  | 1
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 388.63 |  |  | -0.1845 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232920 | IR10 | 13.2 | 235 | 55 | 14 | 16.1 | 8.66 |  |  | -0.18694 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 0.39 |  |  | -0.18744 |  |  |  | 0 |  | 1 | CAPACITY | AB1-137 |  |  | 1
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0.17 |  |  | -0.18744 |  |  |  | 0 |  | 1 | NEW | AB1-137 |  |  | 1
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.19057 |  |  |  | 0 |  | 1 | CAPACITY | Z2-076 |  |  | 1
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.19057 |  |  |  | 0 |  | 1 | CAPACITY | Z2-077 |  |  | 1
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.19057 |  |  |  | 0 |  | 1 | NEW | Z2-077 |  |  | 1
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.19057 |  |  |  | 0 |  | 1 | NEW | Z2-076 |  |  | 1
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.23 |  |  | -0.19881 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.20533 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.20533 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.20533 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 0.83 |  |  | -0.20533 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.20533 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232915 | OH NUG4 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.20533 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 0.82 |  |  | -0.20533 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 16.08 |  |  | -0.20542 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232905 | CHERITON_25 | 24.9 | 235 | 65 | 0 | 12.5 | 0.23 |  |  | -0.20542 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
917082 | Z2-012 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.20542 |  |  |  | 0 |  | 1 | NEW | Z2-012 |  |  | 1
233901 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.20542 |  |  |  | 0 |  | 1 | CAPACITY | Z2-012 |  |  | 1
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.20554 |  |  |  | 0 |  | 1 | CAPACITY | W1-005 |  |  | 1
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.20554 |  |  |  | 0 |  | 1 | CAPACITY | W1-004 |  |  | 1
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.20554 |  |  |  | 0 |  | 1 | CAPACITY | W1-003 |  |  | 1
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.20554 |  |  |  | 0 |  | 1 | CAPACITY | W1-006 |  |  | 1
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.20554 |  |  |  | 0 |  | 1 | NEW | W1-003 |  |  | 1
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.20554 |  |  |  | 0 |  | 1 | NEW | W1-005 |  |  | 1
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.20554 |  |  |  | 0 |  | 1 | NEW | W1-006 |  |  | 1
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.20554 |  |  |  | 0 |  | 1 | NEW | W1-004 |  |  | 1
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0.37 |  |  | -0.20794 |  |  |  | 0 |  | 1 | NEW | X1-032 |  |  | 1
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 8.6 |  |  | -0.20853 |  |  |  | 0 |  | 1 | NEW | AA1-102 |  |  | 1
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 5.27 |  |  | -0.20853 |  |  |  | 0 |  | 1 | CAPACITY | AA1-102 |  |  | 1
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 6.23 |  |  | -0.20853 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
233900 | O-025 C | 25 | 235 | 64 | 0 | 6 | 5.11 |  |  | -0.20864 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
960882 | AF2-379 E | 69 | 235 | 75 | 0 | 2.26 | 0.21 |  |  | -0.20958 |  |  |  | 0 |  | 1 | NEW | AF2-379 |  |  | 1
233940 | AF2-379 C | 69 | 235 | 75 | 0 | 1.64 | 0.15 |  |  | -0.20958 |  |  |  | 0 |  | 1 | CAPACITY | AF2-379 |  |  | 1
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0.86 |  |  | -0.21346 |  |  |  | 0 |  | 1 | NEW | Y3-058 |  |  | 1
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 8.9 | 0.82 |  |  | -0.21346 |  |  |  | 0 |  | 1 | CAPACITY | Y3-058 |  |  | 1
925262 | AB2-180 E | 0.38 | 235 | 75 | 0 | 6 | 0.56 |  |  | -0.21346 |  |  |  | 0 |  | 1 | NEW | AB2-180 |  |  | 1
233942 | AB2-180 C | 0.38 | 235 | 75 | 0 | 14 | 8.72 |  |  | -0.21346 |  |  |  | 0 |  | 1 | CAPACITY | AB2-180 |  |  | 1
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.55 |  |  | -0.22179 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 2.83 |  |  | -0.22814 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232919 | VN10 | 13.2 | 235 | 55 | 0 | 14.3 | 7.69 |  |  | -0.22993 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0.19 |  |  | -0.23584 |  |  |  | 0 |  | 1 | NEW | Y1-080 |  |  | 1
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 0.12 |  |  | -0.23584 |  |  |  | 0 |  | 1 | CAPACITY | Y1-080 |  |  | 1
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.238 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.238 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.25488 |  |  |  | 0 |  | 1 | NEW | X3-008 |  |  | 1
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.25488 |  |  |  | 0 |  | 1 | CAPACITY | X3-008 |  |  | 1
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 1.28 |  |  | -0.31712 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0.57 |  |  | -0.38076 |  |  |  | 0 |  | 1 | NEW | Y1-079 |  |  | 1
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 0.35 |  |  | -0.38076 |  |  |  | 0 |  | 1 | CAPACITY | Y1-079 |  |  | 1
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0.34 |  |  | -0.4256 |  |  |  | 0 |  | 1 | NEW | X3-066 |  |  | 1
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 3.08 | 0.28 |  |  | -0.4256 |  |  |  | 0 |  | 1 | CAPACITY | X3-066 |  |  | 1
233930 | AB2-032 GEN | 0.6 | 235 | 75 | 0 | 13.6 | 1.26 |  |  | -0.45143 |  |  |  | 0 |  | 1 | CAPACITY | AB2-032 |  |  | 1
923925 | AB2-153 E | 0.6 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.45143 |  |  |  | 0 |  | 1 | NEW | AB2-153 |  |  | 1
233933 | AB2-153 GEN | 0.6 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.45143 |  |  |  | 0 |  | 1 | CAPACITY | AB2-153 |  |  | 1
923928 | AB2-032 E | 0.6 | 235 | 75 | 0 | 6.4 | 0.59 |  |  | -0.45143 |  |  |  | 0 |  | 1 | NEW | AB2-032 |  |  | 1
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | -0.45158 |  |  |  | 0 |  | 1 | CAPACITY | AB1-141 |  |  | 1
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | -0.45158 |  |  |  | 0 |  | 1 | CAPACITY | AB1-142 |  |  | 1
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | -0.45158 |  |  |  | 0 |  | 1 | NEW | AB1-142 |  |  | 1
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | -0.45158 |  |  |  | 0 |  | 1 | NEW | AB1-141 |  |  | 1
924802 | AB2-133 E | 69 | 235 | 75 | 0 | 31.2 | 2.89 |  |  | -0.46609 |  |  |  | 0 |  | 1 | NEW | AB2-133 |  |  | 1
233939 | AB2-133 C | 69 | 235 | 75 | 0 | 24.6 | 2.28 |  |  | -0.46609 |  |  |  | 0 |  | 1 | CAPACITY | AB2-133 |  |  | 1

## GD-W30
****** PJM Winter Generator Deliverability Detailed Report ****** PJM [TARA Ver 2101.1.0.0 64-bit - Fri Jun 25 13:09:20 2021]
FG Index [All Queue] | 168 | FG ID | 49 | Monitored Facility:232233 PRESTON 69.0 232234 TODD 69.0 1 / Contingency:DPL_P4-2_DP11_SRT-A[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
105 | 96.8 | 100.66 | AC | 88.76 | 11.57 | -0.83 | 2.14 | 0.01 | 101.64 | 105.7 | 2e-06 | 0 | 12712.4 | 0 | 12644.7 | 0.05 | 76.22 | 67.72 | 8.5 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | FRMP | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited? | Ramping Limit
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 1.28 | 69 | FiftyFifty | 0.17091 | 11.5747 | 11.7928 |  | 0.1097 | 0.8903 | 1 | CAPACITY |  |  |  | 1
AF2-085 | BATEXP_AF2-085->PJM |  |  | LTF |  | 20 |  | 20 | LTF/CMTX | 0.00053 | 0.0107 | 0.0107 | 0
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 682 |  | 682 | LTF/CBM | 0.00052 | 0.3562 | 0.3562 | 0.0011
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 94.5 |  | 94.5 | CLTF | 0.00052 | 0.0496 | 0.0496 | 0.0001
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 1348 |  | 1348 | LTF/CBM | 0.00052 | 0.6951 | 0.6951 | 0.0021
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1063 |  | 1063 | LTF/CBM | 0.00051 | 0.5453 | 0.5453 | 0.0016
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  | 175 | CLTF | 0.00052 | 0.0905 | 0.0905 | 0.0003
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  | 158.9 | CLTF | 0.00051 | 0.0817 | 0.0817 | 0.0002
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  | 140 | CLTF | 0.00052 | 0.0724 | 0.0724 | 0.0002
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 59.6 |  | 59.6 | CLTF | 0.00051 | 0.0306 | 0.0306 | 0.0001
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 32.9 |  | 32.9 | CLTF | 0.00051 | 0.0169 | 0.0169 | 0.0001
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 18 |  | 18 | LTF/CBM | 0.00052 | 0.0093 | 0.0093 | 0
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  | 10.5 | CLTF | 0.00051 | 0.0054 | 0.0054 | 0
AC1-212 | BATEXP_AC1-212->PJM |  |  | LTF |  | 1.9 |  | 1.9 | LTF/CMTX | 0.00051 | 0.001 | 0.001 | 0
AA2-082 | BATEXP_AA2-082->PJM |  |  | LTF |  | 2 |  | 2 | LTF/CMTX | 0.00027 | 0.0005 | 0.0005 | 0
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 389 |  | 389 | LTF/CBM | 0.00024 | 0.0935 | 0.0935 | 0.0006
AD2-210 | BATEXP_AD2-210->PJM |  |  | LTF |  | 8 |  | 8 | LTF/CMTX | 0.00015 | 0.0012 | 0.0012 | 0
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  | 645 | LTF/CMTX | 0.0001 | 0.0665 | 0.0665 | 0.001
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  | 239.8 | LTF/CMTX | 4e-05 | 0.0096 | 0.0096 | 0.0004
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 | 8.5 | Adder/OL | -0.09768 | -0.8302 | -0.9768 | 0 | 0.1042 |  | 1 | ENERGY |  |  |  | 1
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0.57 |  |  | 0.06685 |  |  |  | 0 |  | 1 | NEW | Y1-079 |  |  | 1
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 0.35 |  |  | 0.06685 |  |  |  | 0 |  | 1 | CAPACITY | Y1-079 |  |  | 1
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0.34 |  |  | 0.04796 |  |  |  | 0 |  | 1 | NEW | X3-066 |  |  | 1
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 3.08 | 0.28 |  |  | 0.04796 |  |  |  | 0 |  | 1 | CAPACITY | X3-066 |  |  | 1
233930 | AB2-032 GEN | 0.6 | 235 | 75 | 0 | 13.6 | 1.26 |  |  | 0.04314 |  |  |  | 0 |  | 1 | CAPACITY | AB2-032 |  |  | 1
923925 | AB2-153 E | 0.6 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.04314 |  |  |  | 0 |  | 1 | NEW | AB2-153 |  |  | 1
233933 | AB2-153 GEN | 0.6 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | 0.04314 |  |  |  | 0 |  | 1 | CAPACITY | AB2-153 |  |  | 1
923928 | AB2-032 E | 0.6 | 235 | 75 | 0 | 6.4 | 0.59 |  |  | 0.04314 |  |  |  | 0 |  | 1 | NEW | AB2-032 |  |  | 1
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | 0.04311 |  |  |  | 0 |  | 1 | CAPACITY | AB1-141 |  |  | 1
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | 0.04311 |  |  |  | 0 |  | 1 | CAPACITY | AB1-142 |  |  | 1
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | 0.04311 |  |  |  | 0 |  | 1 | NEW | AB1-142 |  |  | 1
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | 0.04311 |  |  |  | 0 |  | 1 | NEW | AB1-141 |  |  | 1
924802 | AB2-133 E | 69 | 235 | 75 | 0 | 31.2 | 2.89 |  |  | 0.03089 |  |  |  | 0 |  | 1 | NEW | AB2-133 |  |  | 1
233939 | AB2-133 C | 69 | 235 | 75 | 0 | 24.6 | 2.28 |  |  | 0.03089 |  |  |  | 0 |  | 1 | CAPACITY | AB2-133 |  |  | 1
233935 | AB2-179 C | 0.38 | 235 | 75 | 0 | 37.6 | 3.48 |  |  | 0.02007 |  |  |  | 0 |  | 1 | CAPACITY | AB2-179 |  |  | 1
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.02007 |  |  |  | 0 |  | 1 | NEW | AB2-179 |  |  | 1
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.21 |  |  | 0.00383 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 9.25 |  |  | 0.0033 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00298 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 7.64 |  |  | 0.00298 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 81.14 |  |  | 0.00298 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 12.37 |  |  | 0.00296 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 12.32 |  |  | 0.00296 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00291 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00291 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 164.17 |  |  | 0.00291 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 8.32 |  |  | 0.00228 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 99.67 |  |  | 0.00228 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 67.49 |  |  | 0.00215 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.00215 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.00215 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 33.74 |  |  | 0.00215 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.00215 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.00215 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213893 | PHLISST1 | 20 | 230 | 58 | 232.3 | 267 | 143.61 |  |  | 0.00169 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.0017 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.0017 |  |  |  | 0.036 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00169 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 38.35 |  |  | 0.00164 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 30.66 |  |  | 0.00164 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 29.58 |  |  | 0.00164 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 9.57 |  |  | 0.00164 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 0.00155 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 20.25 |  |  | 0.00148 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 20.98 |  |  | 0.0012 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.0012 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.0012 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00117 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00117 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00116 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00116 |  |  |  | 0.036 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 18.29 |  |  | 0.00117 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.00117 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 222.4 | 119.62 |  |  | 0.00116 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.00107 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 87.67 |  |  | 0.00088 |  |  |  | 0.036 |  | 1 | CAPACITY | GRAYS FERRY |  |  | 1
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.00086 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00084 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00084 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00068 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00068 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00068 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00068 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 28 |  |  | 0.00067 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00064 |  |  |  | 0 |  | 1 | NEW | AA2-072 |  |  | 1
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 139.8 | 75.19 |  |  | 0.00063 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 61.1 |  |  | 0.00063 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 55.94 |  |  | 0.00063 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 27.97 |  |  | 0.00063 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223401 | AF1-299 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.00063 |  |  |  | 0 |  | 1 | CAPACITY | AF1-299 |  |  | 1
223402 | AF1-300 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.00063 |  |  |  | 0 |  | 1 | CAPACITY | AF1-300 |  |  | 1
946352 | AF1-299 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.00063 |  |  |  | 0 |  | 1 | NEW | AF1-299 |  |  | 1
946362 | AF1-300 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.00063 |  |  |  | 0 |  | 1 | NEW | AF1-300 |  |  | 1
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.4 |  |  | 0.00063 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220904 | CRANE G2 | 20 | 232 | 12 | 0 | 14 | 0 |  |  | 0.00061 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.2 | 16.24 |  |  | 0.0006 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 29.8 | 16.03 |  |  | 0.0006 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 7.34 |  |  | 0.0006 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 68.9 |  |  | 0.0006 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 289.09 |  |  | 0.0006 |  |  |  | 0.1042 |  | 1 | CAPACITY | Wagner3 |  |  | 1
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.0006 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 7.15 |  |  | 0.0006 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00059 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 57 |  |  | 0.0006 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 642.7 |  |  | 0.0006 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 638.9 |  |  | 0.0006 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 93.64 |  |  | 0.00058 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208904 | HOLT 696 | 13.2 | 229 | 60 | 16 | 58.4 | 41.06 |  |  | 0.00058 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208903 | HOLT 695 | 13.2 | 229 | 60 | 19 | 53.2 | 37.4 |  |  | 0.00058 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 0.45 |  |  | 0.00058 |  |  |  | 0 |  | 1 | CAPACITY | V4-027 |  |  | 1
208254 | AF2-280 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00058 |  |  |  | 0 |  | 1 | NEW | AF2-280 |  |  | 1
208474 | KINZ 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00058 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.64 |  |  | 0.00057 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208253 | AF2-280 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00058 |  |  |  | 0 |  | 1 | MTX | AF2-280 |  |  | 1
916007 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 0.1 | 0.06 |  |  | 0.00058 |  |  |  | 0 |  | 1 | NEW | V4-027 |  |  | 1
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 80.49 |  |  | 0.00056 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 68.19 |  |  | 0.00056 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 53.78 |  |  | 0.00056 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
223967 | METZ E69 | 69 | 233 | 56 | 0 | 20 | 0 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 45.34 |  |  | 0.00056 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 44.99 |  |  | 0.00056 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
226895 | WOAKV2-037 E | 69 | 233 | 29 | 0 | 4.5 | 0 |  |  | 0.00056 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
208769 | SISO | 12.5 | 229 | 2 | 2.5 | 1.6 | 0 |  |  | 0.00056 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
208876 | WLAN | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
226920 | AE1-012 E | 115 | 233 | 75 | 0 | 0.34 | 0.03 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW | AE1-012 |  |  | 1
226919 | AE1-012 C | 115 | 233 | 75 | 0 | 0.22 | 0.02 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | AE1-012 |  |  | 1
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 11.01 |  |  | 0.00056 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 10.83 |  |  | 0.00056 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 247.42 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 205.47 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 182.23 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 327.3 | 176.05 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00056 |  |  |  | 0.036 |  | 1 | CAPACITY | Y1-065 |  |  | 1
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.00056 |  |  |  | 0.036 |  | 1 | CAPACITY | WALDORF |  |  | 1
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00055 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.00055 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-035 |  |  | 1
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 103.81 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200054 | ROCKSP 3 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200055 | ROCKSP 4 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200052 | ROCKSP 1 | 18 | 235 | 57 | 145.7 | 167.5 | 90.09 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200053 | ROCKSP 2 | 18 | 235 | 57 | 144.9 | 166.5 | 89.56 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00055 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA |  |  | 1
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227024 | SMECOCT | 13.8 | 238 | 57 | 0 | 80.2 | 43.14 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 43.03 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.00055 |  |  |  | 0.036 |  | 1 | CAPACITY | PANDA |  |  | 1
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00055 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
226704 | AOCX4-046 E | 13.8 | 233 | 58 | 0 | 19.5 | 0 |  |  | 0.00055 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 1.86 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW | AC2-101 |  |  | 1
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 1.58 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW | AC2-120 |  |  | 1
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.00056 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00056 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 13.12 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227282 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 1.14 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | AC2-101 |  |  | 1
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.00055 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
227280 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 0.97 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | AC2-120 |  |  | 1
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 9.68 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.00056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209030 | FRFA O01 | 12.5 | 229 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208527 | AF2-279 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW | AF2-279 |  |  | 1
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0.16 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW | AB2-157 |  |  | 1
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 2 | 1.22 |  |  | 0.00056 |  |  |  | 0 |  | 1 | NEW | V3-051 |  |  | 1
226910 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY | AB2-157 |  |  | 1
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.91 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226924 | AE1-015 E | 69 | 233 | 75 | 0 | 0.75 | 0.07 |  |  | 0.00055 |  |  |  | 0 |  | 1 | NEW | AE1-015 |  |  | 1
226923 | AE1-015 C | 69 | 233 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | AE1-015 |  |  | 1
226922 | AE1-013 E | 69 | 233 | 75 | 0 | 0.5 | 0.05 |  |  | 0.00055 |  |  |  | 0 |  | 1 | NEW | AE1-013 |  |  | 1
226921 | AE1-013 C | 69 | 233 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | AE1-013 |  |  | 1
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.87 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208526 | AF2-279 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00056 |  |  |  | 0 |  | 1 | MTX | AF2-279 |  |  | 1
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 619.4 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 613.3 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 866 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 841.8 |  |  | 0.00056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1288.2 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1307 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 229.53 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.00055 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.00055 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 188.28 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00054 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-039 |  |  | 1
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 3.62 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00054 |  |  |  | 0.036 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 1.07 |  |  | 0.00054 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 1.07 |  |  | 0.00054 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
237026 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 2.22 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 0.33 |  |  | 0.00055 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
314088 | 6VANDORN | 230 | 345 | 1 | 7 | 21 | 14.08 |  |  | 0.00054 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 52 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 75 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 787.1 | 23.61 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | NEW | AC1-107 |  |  | 1
316169 | AC1-164 GEN | 0.44 | 345 | 75 | 192.1 | 220.8 | 33.12 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-164 |  |  | 1
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 448.57 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
316044 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 1 |  |  | 1
316045 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 2 |  |  | 1
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 171.69 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
316294 | AC1-161 C | 0.44 | 345 | 75 | 0 | 168.2 | 25.23 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-161 |  |  | 1
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 422.31 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 395.08 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 301.17 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 16.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-190 |  |  | 1
926785 | AC1-164_E | 0.44 | 345 | 75 | 91 | 104.6 | 15.69 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-164 |  |  | 1
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 89.82 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.00054 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
926755 | AC1-161 E | 0.44 | 345 | 75 | 0 | 71.8 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-161 |  |  | 1
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 11.81 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-139 |  |  | 1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-158 2 |  |  | 1
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-158 1 |  |  | 1
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 185.28 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 10.77 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-134 |  |  | 1
316192 | AB2-158 C | 230 | 345 | 75 | 0 | 71 | 10.65 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AB2-158 |  |  | 1
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 10.59 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-134 |  |  | 1
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 67 | 10.05 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-065 |  |  | 1
925672 | AC1-043 E | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA2-088 |  |  | 1
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 8.4 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA2-178 |  |  | 1
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
932596 | AC2-079 E | 0.64 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-079 |  |  | 1
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 7.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-015 |  |  | 1
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 170 | 127.52 |  |  | 0.00054 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 127.52 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
316201 | AC1-065 C | 0.39 | 345 | 75 | 0 | 49.4 | 7.41 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-065 |  |  | 1
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 165.2 | 123.92 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 165.1 | 123.84 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 7.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-190 |  |  | 1
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 120.47 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 120.39 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 120.09 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 119.87 |  |  | 0.00054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 118.52 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 113.79 |  |  | 0.00054 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.1 | 113.34 |  |  | 0.00054 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 112.29 |  |  | 0.00054 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
313053 | 6PAPERMILL | 230 | 345 | 77 | 12 | 37 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
316185 | AD1-033 C | 0.6 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD1-033 |  |  | 1
316267 | AC1-143 C | 0.38 | 345 | 75 | 0 | 41.2 | 6.18 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC1-143 |  |  | 1
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 6.15 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-015 |  |  | 1
316254 | AC1-120 C | 0.6 | 345 | 75 | 0 | 39.6 | 5.94 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC1-120 |  |  | 1
926004 | AC1-076_E | 0.6 | 345 | 75 | 0 | 39.42 | 5.91 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-076 |  |  | 1
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 98.04 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316257 | AC1-043 C | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA2-088 |  |  | 1
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 96.46 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 126.7 | 95.04 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
932586 | AC2-078 E | 0.64 | 345 | 75 | 0 | 37.2 | 5.58 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-078 |  |  | 1
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 94.51 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 124.8 | 93.61 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-139 |  |  | 1
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 0.89 |  |  | 0.00053 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 1 |  |  | 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 2 |  |  | 1
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 83.11 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316311 | AC2-079 C | 0.64 | 345 | 75 | 0 | 32.3 | 4.84 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-079 |  |  | 1
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 82.06 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 80.64 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-065 |  |  | 1
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 4.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
316280 | AD1-041 C | 0.55 | 345 | 75 | 0 | 30 | 4.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD1-041 |  |  | 1
315099 | 1CHESPKB | 13.8 | 345 | 20 | 0 | 24.7 | 0 |  |  | 0.00053 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 0.75 |  |  | 0.00053 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
934065 | AD1-033 E | 0.6 | 345 | 75 | 0 | 28 | 4.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD1-033 |  |  | 1
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00053 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 0.72 |  |  | 0.00053 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 4.08 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AB2-158 |  |  | 1
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 65.18 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 65.11 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 64.51 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 64.43 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 64.21 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 64.14 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA2-178 |  |  | 1
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-065 |  |  | 1
316164 | AC1-076_C | 0.6 | 345 | 75 | 0 | 23.8 | 3.57 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC1-076 |  |  | 1
316289 | AC2-078 C | 0.64 | 345 | 75 | 0 | 22.8 | 3.42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-078 |  |  | 1
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 57.83 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
926486 | AC1-120 E | 0.6 | 345 | 75 | 0 | 20.4 | 3.06 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-120 |  |  | 1
934146 | AD1-041 E | 0.55 | 345 | 75 | 0 | 20 | 3 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD1-041 |  |  | 1
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 49.66 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 2.85 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
926615 | AC1-143 E | 0.38 | 345 | 75 | 0 | 18.8 | 2.82 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-143 |  |  | 1
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 45.01 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316312 | AB1-027 C | 230 | 345 | 75 | 0 | 17.5 | 2.63 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-027 |  |  | 1
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 0.45 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-100 2 |  |  | 1
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-100 1 |  |  | 1
316304 | AE2-227 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE2-227 |  |  | 1
316301 | AE2-228 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE2-228 |  |  | 1
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 37.51 |  |  | 0.00053 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
316321 | Z2-027 C | 230 | 345 | 75 | 0 | 13.8 | 2.07 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z2-027 |  |  | 1
316315 | AB2-025 C | 230 | 345 | 75 | 0 | 13.65 | 2.05 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-025 |  |  | 1
316170 | AC1-121 C | 0.6 | 345 | 75 | 0 | 13.6 | 2.04 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC1-121 |  |  | 1
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | W4-102 |  |  | 1
316052 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC2-072 |  |  | 1
316234 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AE1-124 |  |  | 1
316233 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-074 |  |  | 1
316159 | AE1-175 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-175 |  |  | 1
316051 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-071 |  |  | 1
316223 | AC1-118 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AC1-118 |  |  | 1
316241 | AE2-078 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE2-078 |  |  | 1
316247 | AF1-033 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AF1-033 |  |  | 1
316242 | AE2-079 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE2-079 |  |  | 1
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 1.97 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD2-030 |  |  | 1
316313 | AB2-026 C | 230 | 345 | 75 | 0 | 13.07 | 1.96 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-026 |  |  | 1
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 1.95 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-022 |  |  | 1
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 12.7 | 1.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-137 |  |  | 1
316036 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-147 |  |  | 1
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 1.86 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Y1-086 |  |  | 1
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 1.83 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AB2-029 |  |  | 1
316240 | AF1-291 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AF1-291 |  |  | 1
316236 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-162 |  |  | 1
316258 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-075 |  |  | 1
316244 | AE2-225 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE2-225 |  |  | 1
316305 | AF2-043 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AF2-043 |  |  | 1
316322 | AB2-045 C | 230 | 345 | 75 | 0 | 11.43 | 1.72 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-045 |  |  | 1
237003 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0.76 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
316316 | AC1-027 C | 115 | 345 | 75 | 0 | 11.2 | 1.68 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-027 |  |  | 1
316314 | AB2-024 C | 230 | 345 | 75 | 0 | 11.13 | 1.67 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-024 |  |  | 1
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0.73 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-097 |  |  | 1
316004 | AC1-112 C | 230 | 345 | 75 | 0 | 10.9 | 1.63 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-112 |  |  | 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
923213 | AB1-125_E | 0.6 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AB1-125 |  |  | 1
942152 | AE2-227 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-227 |  |  | 1
942162 | AE2-228 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-228 |  |  | 1
316057 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-196 |  |  | 1
316150 | AD2-215 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD2-215 |  |  | 1
316246 | AF1-032 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AF1-032 |  |  | 1
315085 | 1SPRUNCC | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315086 | 1SPRUNCD | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316072 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 1.46 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD1-144 |  |  | 1
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0.63 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | W1-116 |  |  | 1
316050 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 1.38 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-070 |  |  | 1
316059 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD1-063 |  |  | 1
316245 | AE2-229 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE2-229 |  |  | 1
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-092 |  |  | 1
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-138 |  |  | 1
237025 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | W4-102 |  |  | 1
946262 | AF1-291 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AF1-291 |  |  | 1
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE1-162 |  |  | 1
957492 | AF2-043 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AF2-043 |  |  | 1
942132 | AE2-225 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-225 |  |  | 1
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 1.17 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-116 |  |  | 1
316303 | AF2-085 | 230 | 345 | 76 | 0 | 20 | 13.41 |  |  | 0.00053 |  |  |  | 0.05 |  | 1 | CAPACITY |  |  |  | 1
237024 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0.51 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
316006 | AB2-029 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AB2-029 |  |  | 1
316320 | Y1-086 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Y1-086 |  |  | 1
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 7.5 | 1.13 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-027 |  |  | 1
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-137 |  |  | 1
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-147 |  |  | 1
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 1.05 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-022 |  |  | 1
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0.46 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-136 |  |  | 1
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-118 |  |  | 1
940902 | AE2-079 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-079 |  |  | 1
943622 | AF1-033 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AF1-033 |  |  | 1
940892 | AE2-078 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-078 |  |  | 1
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z2-030 |  |  | 1
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC2-072 |  |  | 1
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AE1-124 |  |  | 1
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD2-030 |  |  | 1
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE1-074 |  |  | 1
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-071 |  |  | 1
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 1 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-196 |  |  | 1
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0.44 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-096 |  |  | 1
316160 | AE1-175 E | 230 | 345 | 75 | 0 | 6.6 | 0.99 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE1-175 |  |  | 1
926502 | AC1-121 E | 0.6 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AC1-121 |  |  | 1
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-027 |  |  | 1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-045 |  |  | 1
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.1 | 10.8 |  |  | 0.00053 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHARLES CITY_LF |  |  | 1
237006 | AB1-125_C | 0.6 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AB1-125 |  |  | 1
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-024 |  |  | 1
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-026 |  |  | 1
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-025 |  |  | 1
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0.92 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-112 |  |  | 1
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-138 |  |  | 1
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD1-063 |  |  | 1
942172 | AE2-229 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-229 |  |  | 1
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z2-027 |  |  | 1
237034 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 0.4 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-136 |  |  | 1
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0.88 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE1-075 |  |  | 1
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 10.06 |  |  | 0.00053 |  |  |  | 0.44065 |  | 1 | CAPACITY |  |  |  | 1
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 0.39 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | W1-116 |  |  | 1
961102 | AF2-401 E | 115 | 345 | 75 | 0 | 5.8 | 0.87 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW | AF2-401 |  |  | 1
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 9.99 |  |  | 0.00053 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHESTERFIELD LF_A |  |  | 1
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD1-144 |  |  | 1
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD2-215 |  |  | 1
943612 | AF1-032 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AF1-032 |  |  | 1
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-109 |  |  | 1
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-109 |  |  | 1
316035 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 0.7 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-116 |  |  | 1
961092 | AF2-400 E | 115 | 345 | 75 | 0 | 4.43 | 0.66 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | af2-400 |  |  | 1
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 7.56 |  |  | 0.00053 |  |  |  | 0.1097 |  | 1 | CAPACITY | VIRGINIA BEACH LF_A |  |  | 1
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-092 |  |  | 1
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 7.38 |  |  | 0.00053 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
237077 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z2-030 |  |  | 1
314541 | 3WATKINS | 115 | 345 | 75 | 0 | 4 | 0.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 6.71 |  |  | 0.00053 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0.57 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-070 |  |  | 1
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0.24 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-095 |  |  | 1
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 1.87 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316302 | AF2-401 C | 115 | 345 | 75 | 0 | 3.52 | 0.53 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY | AF2-401 |  |  | 1
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
237030 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 0.23 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-096 |  |  | 1
316318 | V4-068 C | 115 | 345 | 75 | 0 | 3.2 | 0.48 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | V4-068 |  |  | 1
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 0.21 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-095 |  |  | 1
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 258.69 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
316300 | AF2-400 C | 115 | 345 | 75 | 0 | 2.71 | 0.41 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AF2-400 |  |  | 1
901082 | W1-029 E | 230 | 345 | 74 | 0 | 169 | 167.31 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | W1-029 |  |  | 1
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0.27 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | V4-068 |  |  | 1
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0.22 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 0.76 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 1.44 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 1.07 | 0.16 |  |  | 0.00054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.61 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | W1-029 |  |  | 1
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.39 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 10.4 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z1-068 |  |  | 1
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.49 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z1-068 |  |  | 1
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 2 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 8.7 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 948.5 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 948.9 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 4 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 6.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 20 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 52.8 | 52.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 4.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 843.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 844.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 11.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 15.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 12.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53 | 53 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 108.79 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | K11 |  |  | 1
316299 | AC2-112 C | 0.6 | 345 | 75 | 0 | 103.1 | 15.47 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-112 |  |  | 1
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 107.08 |  |  | 0.00052 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 105.41 |  |  | 0.00052 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
316011 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 12.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 1
923994 | AB2-040_E | 0.6 | 345 | 75 | 0 | 69.51 | 10.43 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-040 |  |  | 1
315131 | 1EDGECMA | 13.8 | 345 | 11 | 7.5 | 58 | 0 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 9.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-059 |  |  | 1
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 67.13 |  |  | 0.00052 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
270173 | AC1-122_C | 0.6 | 205 | 75 | 0 | 54.4 | 3.97 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | AC1-122 |  |  | 1
314860 | 4E MILL | 138 | 345 | 77 | 0 | 50 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEWENERGY | Covington |  |  | 1
316049 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 8.4 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-081 |  |  | 1
316274 | AC1-208 C | 0.38 | 345 | 75 | 0 | 55.4 | 8.31 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-208 |  |  | 1
932855 | AC2-112 E | 0.6 | 345 | 75 | 0 | 46.9 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-112 |  |  | 1
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 8.22 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA2-053 |  |  | 1
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 8.16 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-060 |  |  | 1
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z2-088 |  |  | 1
316222 | AC1-221 C | 0.6 | 345 | 75 | 0 | 51.2 | 7.68 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-221 |  |  | 1
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 7.64 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-063A |  |  | 1
316327 | AA2-057 C | 0.63 | 345 | 75 | 0 | 50 | 7.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA2-057 |  |  | 1
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z2-088 |  |  | 1
314859 | 4WSTVACO | 138 | 345 | 2 | 0 | 40.5 | 0 |  |  | 0.00053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316283 | AC2-100 C | 0.57 | 345 | 75 | 0 | 45.6 | 6.84 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-100 |  |  | 1
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 6.68 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-054 |  |  | 1
316263 | AC1-034 C | 0.55 | 345 | 75 | 0 | 42.75 | 6.41 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-034 |  |  | 1
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-174 |  |  | 1
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 6.06 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-173 |  |  | 1
316174 | AB2-169_C | 0.63 | 345 | 75 | 0 | 39 | 5.85 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-169 |  |  | 1
316003 | AC1-222 C | 0.6 | 345 | 75 | 0 | 38.8 | 5.82 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-222 |  |  | 1
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 41.06 |  |  | 0.00052 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 5.74 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-075 |  |  | 1
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-174 |  |  | 1
316210 | AC1-098 C | 0.6 | 345 | 75 | 0 | 37.6 | 5.64 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-098 |  |  | 1
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 39.39 |  |  | 0.00052 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 1
909222 | X2-060 E | 138 | 345 | 64 | 0 | 30 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | ENERGY | Covington |  |  | 1
925122 | AB2-169 E | 0.63 | 345 | 75 | 0 | 35 | 5.25 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-169 |  |  | 1
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 5.18 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 5.1 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-059 |  |  | 1
925595 | AC1-034 E | 0.55 | 345 | 75 | 0 | 32.25 | 4.84 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-034 |  |  | 1
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-043 |  |  | 1
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AC1-145 |  |  | 1
927146 | AC1-208 E | 0.38 | 345 | 75 | 0 | 24.5 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-208 |  |  | 1
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 0.76 |  |  | 0.00053 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 0.75 |  |  | 0.00053 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
925665 | AC1-042 E | 0.4 | 345 | 75 | 0 | 26.04 | 3.91 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AC1-042 |  |  | 1
927264 | AC1-222 E | 0.6 | 345 | 75 | 0 | 25.9 | 3.88 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-222 |  |  | 1
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.2 | 27.3 |  |  | 0.00052 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 3.84 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-060 |  |  | 1
919710 | AA2-057 E | 0.63 | 345 | 75 | 0 | 24.9 | 3.73 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA2-057 |  |  | 1
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-063A |  |  | 1
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-081 |  |  | 1
926516 | AC1-122_E | 0.6 | 205 | 75 | 0 | 21.5 | 1.57 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AC1-122 |  |  | 1
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 18.41 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | K11 |  |  | 1
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 3.38 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA2-053 |  |  | 1
926206 | AC1-098 E | 0.6 | 345 | 75 | 0 | 22.4 | 3.36 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-098 |  |  | 1
237037 | AE1-188 C | 34.5 | 201 | 75 | 0 | 20.5 | 1.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-188 |  |  | 1
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 1.46 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD1-085 |  |  | 1
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 74.1 | 55.58 |  |  | 0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 3.26 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-075 |  |  | 1
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 3.08 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-054 |  |  | 1
316217 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 2.85 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | AC1-145 |  |  | 1
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 2.84 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-043 |  |  | 1
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 2.54 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
932763 | AC2-100 E | 0.57 | 345 | 75 | 0 | 16.4 | 2.46 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-100 |  |  | 1
316197 | AC1-042 C | 0.4 | 345 | 75 | 0 | 15.96 | 2.39 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | AC1-042 |  |  | 1
927255 | AC1-221 E | 0.6 | 345 | 75 | 0 | 14.6 | 2.19 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-221 |  |  | 1
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 0.36 |  |  | 0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-127 |  |  | 1
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-128 |  |  | 1
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 45.9 | 34.43 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD1-085 |  |  | 1
316317 | KELFORD C | 115 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z2-043 |  |  | 1
237038 | AE2-054 C | 34.5 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
316205 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 1.92 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-080 |  |  | 1
316212 | AC1-099 C | 0.6 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-099 |  |  | 1
939592 | AE1-188 E | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE1-188 |  |  | 1
316181 | AB2-040 GEN | 0.6 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB2-040 |  |  | 1
316238 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
316239 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
316237 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
316248 | AF1-058 C | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AF1-058 |  |  | 1
244012 | 05PINNACLE | 4 | 205 | 75 | 0 | 11 | 0.8 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 19.81 |  |  | 0.00052 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
316005 | AA1-067 C | 230 | 345 | 75 | 0 | 10.5 | 1.58 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-067 |  |  | 1
235043 | AF1-166 C | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AF1-166 |  |  | 1
316054 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC2-074 |  |  | 1
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-098 |  |  | 1
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-099 |  |  | 1
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 34.7 | 26.03 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD1-060 |  |  | 1
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 1.39 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-036 |  |  | 1
316074 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD1-157 |  |  | 1
940672 | AE2-054 E | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
316034 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 1.29 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-036 |  |  | 1
316319 | Z2-044 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | Z2-044 |  |  | 1
237001 | AB1-127 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-127 |  |  | 1
237002 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-128 |  |  | 1
270130 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
943902 | AF1-058 E | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AF1-058 |  |  | 1
926214 | AC1-099 E | 0.6 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-099 |  |  | 1
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 1.08 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-080 |  |  | 1
917332 | KELFORD E | 115 | 345 | 75 | 0 | 7 | 1.05 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z2-043 |  |  | 1
945012 | AF1-166 E | 34.5 | 201 | 75 | 0 | 6.4 | 0.47 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AF1-166 |  |  | 1
316243 | AE2-151 C | 115 | 345 | 75 | 0 | 6.5 | 0.98 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE2-151 |  |  | 1
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AB1-173 |  |  | 1
237080 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AD1-060 |  |  | 1
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 15.7 | 10.53 |  |  | 0.00053 |  |  |  | 0.1097 |  | 1 | CAPACITY | AMELIA LF_1-A |  |  | 1
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AD1-157 |  |  | 1
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 10.07 |  |  | 0.00053 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE1-098 |  |  | 1
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE1-099 |  |  | 1
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0.79 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC2-074 |  |  | 1
313853 | 3PONTONDP | 115 | 345 | 65 | 0 | 4 | 0 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0.68 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-067 |  |  | 1
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 4.44 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0.54 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | Z2-044 |  |  | 1
941542 | AE2-151 E | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AE2-151 |  |  | 1
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 2.22 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270205 | AE1-176 | 138 | 205 | 60 | 0 | 2.4 | 1.33 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 81.18 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | T157 |  |  | 1
918234 | AA1-038_E | 0.69 | 345 | 74 | 0 | 66.7 | 66.03 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AA1-038 |  |  | 1
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 0.72 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.44 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 20.3 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | T157 |  |  | 1
315616 | AA1-038_C | 0.69 | 345 | 74 | 0 | 9.9 | 9.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AA1-038 |  |  | 1
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 11 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.2 | 441.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 437.1 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 50.3 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 48 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 15 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 45.6 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 5.5 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 503.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 502.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 502.8 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 502.3 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 553 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM2 |  |  | 1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 522.9 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 548.2 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM1 |  |  | 1
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 52.4 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235591 | 01PLEAS2 | 26 | 201 | 16 | 350 | 639 | 0 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235590 | 01PLEAS1 | 26 | 201 | 16 | 300 | 639 | 0 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
237068 | AA2-119 GEN | 20.5 | 201 | 58 | 0 | 600 | 0 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | NEW | Harrison |  |  | 1
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 253.85 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Guernsey |  |  | 1
276658 | AB1-122 CT1 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-122 |  |  | 1
276660 | AB1-122 CT2 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-122 |  |  | 1
276640 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | AC1-204 |  |  | 1
276642 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-204 |  |  | 1
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 194.77 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | AA2-116 |  |  | 1
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 289.95 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet8 |  |  | 1
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 139.32 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 293.58 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet7 |  |  | 1
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 127.94 |  |  | 0.00051 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 127.17 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 317.2 | 121.14 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 113.58 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.1 | 113.46 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 113.43 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 272.1 | 103.92 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-079 |  |  | 1
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 95.86 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 243 | 92.8 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 92.04 |  |  | 0.00051 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | X2-052 |  |  | 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 85.93 |  |  | 0.00052 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247529 | 05COVRT2 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 2 |  |  | 1
247530 | 05COVRT3 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247528 | 05COVRT1 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 125.75 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U2-072 |  |  | 1
276174 | W4-005 E | 0.69 | 222 | 74 | 0 | 260.4 | 125.46 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | W4-005 |  |  | 1
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 77.49 |  |  | 0.00051 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 202.7 | 77.41 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Z1-079 |  |  | 1
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 160.3 | 184.3 | 70.39 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 69.62 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 69.62 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 158.6 | 182.3 | 69.62 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | DRESDEN |  |  | 1
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 68.74 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 156.6 | 180 | 68.74 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251832 | 08HLCRTG | 0.38 | 212 | 75 | 0 | 120 | 8.76 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-014 |  |  | 1
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 155.8 | 179.1 | 68.4 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 154.7 | 177.8 | 67.9 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | RONCO |  |  | 1
247225 | 05FTHLG2 | 18 | 205 | 57 | 151.2 | 173.8 | 66.38 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247224 | 05FTHLG1 | 18 | 205 | 57 | 151.1 | 173.7 | 66.34 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247232 | 05RIVRG3 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247231 | 05RIVRG2 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 170.9 | 65.27 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 170.8 | 65.23 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 64.77 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 64.28 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | NELSON |  |  | 1
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 63.89 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 63.82 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 197.5 | 95.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Q57 |  |  | 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 63.01 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 62.67 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 61.87 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 1.46 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 89.13 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | X2-022 |  |  | 1
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 57.21 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 57.17 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149 | 56.9 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 263.89 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK8 |  |  | 1
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 174.1 | 83.88 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | S06 |  |  | 1
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 83.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Z2-087 |  |  | 1
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U3-002 |  |  | 1
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U2-090 |  |  | 1
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | V3-007 |  |  | 1
293516 | O-009 E | 0.69 | 222 | 74 | 0 | 169.6 | 81.71 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O09 |  |  | 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 6.79 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 163.2 | 78.63 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | S27 |  |  | 1
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 162.2 | 78.15 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | S28 |  |  | 1
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 244.23 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK7 |  |  | 1
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 77.09 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O50 |  |  | 1
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 76.89 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Q01 3 |  |  | 1
247531 | 05COVRT4 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 114.1 | 131.2 | 50.11 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Covert 2 |  |  | 1
925135 | AB2-170 E | 0.55 | 205 | 75 | 0 | 80.6 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 73.43 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P10 |  |  | 1
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 227.1 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 223.38 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 47.32 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 46.9 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 46.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 46.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 46.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 46.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 45.87 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.2 | 45.52 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293519 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | S36 |  |  | 1
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | S37 |  |  | 1
930062 | AB1-014 E | 0.38 | 212 | 75 | 0 | 77.5 | 5.66 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-014 |  |  | 1
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 209.23 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet9 |  |  | 1
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 44.3 |  |  | 0.00052 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 137 | 66.01 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | L05_CE22 |  |  | 1
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 113.7 | 43.42 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 1.03 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 131.6 | 63.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O22 2 |  |  | 1
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 42.01 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 62.88 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AA1-018 |  |  | 1
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 108.1 | 41.28 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O51 2 |  |  | 1
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O51 1 |  |  | 1
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 106.7 | 40.75 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 60.22 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Q01 4 |  |  | 1
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 90.5 | 104 | 39.72 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253317 | AC1-085 B_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253314 | AC1-085 A_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
936570 | AD2-072_C | 0.6 | 320 | 75 | 0 | 63.75 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AD2-072 |  |  | 1
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 88.4 | 101.6 | 38.8 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 38.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 57.82 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | N15 |  |  | 1
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 57.82 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | T131 |  |  | 1
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 87.5 | 100.6 | 38.42 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 55.94 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | U2-073 A |  |  | 1
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 114.9 | 55.36 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O22 1 |  |  | 1
939134 | AE1-143 C | 0.64 | 320 | 75 | 0 | 64.14 | 4.68 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | AE1-143 |  |  | 1
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 54.49 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC2-176 |  |  | 1
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 41.94 |  |  | 0.00051 |  |  |  | 0.39467 |  | 1 | CAPACITY |  |  |  | 1
924049 | AB2-047 E2 | 0.69 | 222 | 74 | 0 | 109.6 | 52.81 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
924048 | AB2-047 E1 | 0.69 | 222 | 74 | 0 | 107.9 | 51.99 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P36 1 |  |  | 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P36 2 |  |  | 1
270186 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 4.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
247549 | V3-028 C | 345 | 205 | 75 | 0 | 57 | 4.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | V3-028 |  |  | 1
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 32.12 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 31.16 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
930042 | AB1-006 E2 | 0.69 | 205 | 74 | 0 | 96.75 | 46.61 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 30.93 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.5 | 30.74 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 46.25 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | S71 |  |  | 1
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 80.3 | 30.67 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 30.59 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 30.55 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925133 | AB2-170 C | 0.55 | 205 | 75 | 0 | 49.4 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205916 | AD1-020_C | 0.6 | 227 | 75 | 0 | 54 | 4.99 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 30.17 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 29.56 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 29.06 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76 | 29.02 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 28.99 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 28.91 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 28.87 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 28.8 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 134.03 |  |  | 0.00052 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 88.2 | 42.49 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | T127 4 |  |  | 1
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 42.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O29 1 |  |  | 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 42.21 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P26 |  |  | 1
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 27.95 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 27.88 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 41.92 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | V1-011 |  |  | 1
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 41.39 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P59 |  |  | 1
251959 | 08MADSN8 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251955 | 08MADSN4 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251958 | 08MADSN7 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251953 | 08MADSN2 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251957 | 08MADSN6 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251956 | 08MADSN5 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251954 | 08MADSN3 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251952 | 08MADSN1 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 41.19 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | M24 |  |  | 1
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | R60 1 |  |  | 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | R60 2 |  |  | 1
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 84.83 | 40.87 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | R60 3 |  |  | 1
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 84.8 | 40.86 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | T126 2 |  |  | 1
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 84.7 | 40.81 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | T126 3 |  |  | 1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 70.9 | 27.08 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243415 | 05WWVSTA | 69 | 205 | 61 | 69.8 | 96 | 53.26 |  |  | 0.00051 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 26.35 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 39.65 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Q01 21 |  |  | 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80.6 | 38.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P46 |  |  | 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P11 2 |  |  | 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | P11 1 |  |  | 1
247943 | T-127 E | 0.69 | 205 | 74 | 0 | 79.8 | 38.45 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | T127 5 |  |  | 1
247903 | 05FR-22G E | 0.69 | 205 | 74 | 0 | 78.8 | 37.97 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Q01 22 |  |  | 1
247900 | 05FR-11G E | 0.6 | 205 | 74 | 0 | 78.3 | 37.72 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Q01 11 |  |  | 1
930041 | AB1-006 E1 | 0.69 | 205 | 74 | 0 | 77.25 | 37.22 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 37.1 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Q01 12 |  |  | 1
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 76.1 | 36.67 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | R49 |  |  | 1
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 22.88 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 22.8 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 22.19 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 22.07 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 44.38 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
252507 | AC2-088 C | 0.57 | 212 | 75 | 0 | 38.4 | 2.8 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
253197 | 09PIQUA3 | 69 | 209 | 77 | 0 | 38.3 | 2.77 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 31.8 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-173 |  |  | 1
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 31.32 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | NEW | W2-048 |  |  | 1
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 20.47 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | 0.00052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | 0.00052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 30.18 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 93.75 |  |  | 0.00052 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG2 |  |  | 1
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX | M24 BAT |  |  | 1
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 125.1 | 93.15 |  |  | 0.00052 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG1 |  |  | 1
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-068 |  |  | 1
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-069 |  |  | 1
936576 | AD2-072_E | 0.6 | 320 | 75 | 0 | 31.25 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AD2-072 |  |  | 1
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 19.29 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 38.84 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-166 |  |  | 1
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-165 |  |  | 1
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 28.52 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O35 |  |  | 1
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 28.23 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 18.71 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 18.67 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 18.64 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916000 | 01BACKB E | 34.5 | 201 | 74 | 0 | 57.9 | 27.9 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | K19 |  |  | 1
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 64 | 34.42 |  |  | 0.00051 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
939135 | AE1-143 E | 0.64 | 320 | 75 | 0 | 31.86 | 2.33 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AE1-143 |  |  | 1
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 36.56 |  |  | 0.00051 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
932665 | AC2-088 E | 0.57 | 212 | 75 | 0 | 31.6 | 2.31 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 26.98 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | S14 |  |  | 1
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 56 | 26.98 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Z1-073 |  |  | 1
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 2.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC2-067 |  |  | 1
927209 | AC1-214 E2 | 0.69 | 222 | 74 | 0 | 55.15 | 26.57 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-214 2 |  |  | 1
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 25.15 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | U2-030 |  |  | 1
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 78.63 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | CRG2 |  |  | 1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 104.7 | 77.96 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | CRG1 |  |  | 1
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 0.39 |  |  | 0.00051 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 24.52 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | U2-073 B |  |  | 1
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 23.17 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O29 2 |  |  | 1
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 0.37 |  |  | 0.00051 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 1.93 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC2-067 |  |  | 1
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 22.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | WestBrooklyn |  |  | 1
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 21.97 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | W4-005 |  |  | 1
242587 | 05CELAN | 138 | 205 | 77 | 0 | 81.6 | 58.39 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
916212 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 44.75 | 21.56 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Z1-072 |  |  | 1
916001 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 44.5 | 21.44 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | N47 |  |  | 1
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 21.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | O29 3 |  |  | 1
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 21.15 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-150 |  |  | 1
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 20.96 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U2-061 |  |  | 1
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 20.96 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U1-059 |  |  | 1
272363 | ESS H440 ; R | 138 | 222 | 2 | 0 | 22 | 0 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
274881 | WALNUT RG;1U | 0.69 | 222 | 74 | 0 | 42.4 | 20.43 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O09 |  |  | 1
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 25.91 |  |  | 0.00051 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Q57 |  |  | 1
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O50 |  |  | 1
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 25.52 |  |  | 0.00051 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 59.57 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 18.79 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | U2-072 |  |  | 1
237013 | AA2-103 E | 0.48 | 201 | 76 | 0 | 20 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX | AA2-123 |  |  | 1
913222 | Y1-054 E | 138 | 212 | 58 | 0 | 20 | 0 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX | Z1-108 |  |  | 1
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX | Z1-107 |  |  | 1
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 2.01 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
205917 | AD1-020 ES | 0.55 | 227 | 75 | 0 | 21.5 | 1.99 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 41.2 | 22.16 |  |  | 0.00051 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 17.25 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | S28 |  |  | 1
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 11.46 |  |  | 0.00051 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 16.91 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O22 2 |  |  | 1
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | S36 |  |  | 1
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | S37 |  |  | 1
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 16.77 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | S27 |  |  | 1
253363 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | 0.00051 |  |  |  | 0.05 |  | 1 | MTX | AC1-212 |  |  | 1
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 24 | 27.6 | 10.54 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | 0.00052 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | 0.00052 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
243352 | 05NTRDAM | 138 | 205 | 77 | 0 | 57.6 | 41.21 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 10.04 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
247521 | T131 | 0.69 | 205 | 74 | 26.1 | 30 | 14.45 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | T131 |  |  | 1
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-165 |  |  | 1
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-166 |  |  | 1
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 14.02 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Q01 4 |  |  | 1
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-069 |  |  | 1
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-068 |  |  | 1
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 13.2 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | N15 |  |  | 1
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 54.8 | 40.8 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 8.4 |  |  | 0.00051 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
270681 | BRIGHTSTK; R | 345 | 222 | 74 | 0 | 26 | 12.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Z2-087 |  |  | 1
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 12.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | V3-007 |  |  | 1
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 12.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | U2-090 |  |  | 1
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 12.48 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | S06 |  |  | 1
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 12.38 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Q01 11 |  |  | 1
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 11.56 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 11.56 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | S71 |  |  | 1
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 1.23 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 11.03 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | R49 |  |  | 1
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 10.98 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Sublette |  |  | 1
270180 | AB1-006 W1 | 0.65 | 205 | 74 | 0 | 22.75 | 10.96 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O51 1 |  |  | 1
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O51 2 |  |  | 1
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | V3-028 |  |  | 1
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 10.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O29 1 |  |  | 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 10.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P26 |  |  | 1
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | 0.00052 |  |  |  | 0.0975 |  | 1 | MTX | AA1-100 |  |  | 1
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 0.16 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 9.73 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | T127 5 |  |  | 1
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P11 1 |  |  | 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P11 2 |  |  | 1
270839 | OTTER CRK; R | 345 | 222 | 74 | 0 | 19.5 | 9.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AA1-018 |  |  | 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 9.35 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P46 |  |  | 1
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX | Z1-106 |  |  | 1
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.00051 |  |  |  | 0.05 |  | 1 | MTX | Z1-106 |  |  | 1
251828 | CLNTESP1 | 0 | 212 | 76 | 0 | 10 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 0.15 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 8.86 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O22 1 |  |  | 1
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 20.5 | 11.03 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270183 | AB2-010_C | 138 | 205 | 75 | 0 | 10 | 0.73 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
251364 | 08LEBANO | 69 | 212 | 77 | 0 | 30.6 | 21.57 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.3 | 8.34 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | K28 |  |  | 1
270201 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 8.14 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC2-176 |  |  | 1
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 7.95 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | R60 3 |  |  | 1
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | R60 2 |  |  | 1
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | R60 1 |  |  | 1
276655 | AB2-047 C1 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
276656 | AB2-047 C2 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 7.71 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | W1-056 |  |  | 1
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 4.93 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 7.37 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | T126 3 |  |  | 1
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P36 1 |  |  | 1
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P36 2 |  |  | 1
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 7.32 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | T126 2 |  |  | 1
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 7.23 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | M24 |  |  | 1
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 14.8 | 7.13 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O35 |  |  | 1
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 14.6 | 7.03 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 A |  |  | 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 14.4 | 6.94 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Z1-073 |  |  | 1
270182 | AB2-011_C | 138 | 205 | 75 | 0 | 8 | 0.58 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 6.74 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | S14 |  |  | 1
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 6.36 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 13 | 6.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | L05_CE22 |  |  | 1
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Q01 21 |  |  | 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Q01 22 |  |  | 1
247607 | V1-011 GEN | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | V1-011 |  |  | 1
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 6.17 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 8.21 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Q01 12 |  |  | 1
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Q01 3 |  |  | 1
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 5.78 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O29 2 |  |  | 1
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 5.68 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | T127 4 |  |  | 1
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 5.64 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P59 |  |  | 1
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | 0.00051 |  |  |  | 0.0975 |  | 1 | MTX | Z1-065 |  |  | 1
251387 | 08MDDLTW | 69 | 212 | 77 | 0 | 22.5 | 16.62 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 5.35 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | O29 3 |  |  | 1
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 5.16 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | N47 |  |  | 1
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 12.2 | 6.77 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
253178 | 09MINSTR | 69 | 209 | 77 | 0 | 10 | 4.61 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
276618 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 6.71 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 4.91 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P10 |  |  | 1
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | ENERGY |  |  |  | 1
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0.41 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | X3-005 |  |  | 1
270191 | AC1-173 C | 0.65 | 205 | 74 | 0 | 9.9 | 4.77 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-173 |  |  | 1
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 9.7 | 4.67 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Z1-072 |  |  | 1
252509 | AD1-136 C | 0.57 | 212 | 75 | 0 | 5.4 | 0.39 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 4.63 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | U1-059 |  |  | 1
270111 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 4.51 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
276617 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 5.88 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
204555 | 27QUEEN ST | 115 | 227 | 75 | 0 | 5 | 0.46 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
276646 | AC1-214 C2 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 2 |  |  | 1
276645 | AC1-214 C1 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 1 |  |  | 1
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 8.4 | 4.05 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 B |  |  | 1
935033 | AD1-136 E | 0.57 | 212 | 75 | 0 | 4.6 | 0.34 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 3.9 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | K19 |  |  | 1
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.1 | 5.05 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 3.76 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY | U2-030 |  |  | 1
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | 0.00052 |  |  |  | 0 |  | 1 | MTX | AD2-205 |  |  | 1
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
237033 | AB1-150 C | 138 | 201 | 74 | 0 | 7.3 | 3.52 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-150 |  |  | 1
251346 | 08IVYDL1 | 69 | 212 | 77 | 0 | 12.5 | 8.81 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
276602 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 3.42 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | WestBrooklyn |  |  | 1
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 3.13 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | U2-061 |  |  | 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 10.1 | 6.78 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
244357 | 05GRANGER EL | 34.5 | 205 | 2 | 0 | 3.2 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247622 | Y3-025 | 69 | 205 | 64 | 0 | 3.18 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 0.25 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | X3-005 |  |  | 1
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.3 | 6.25 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
927208 | AC1-214 E1 | 0.69 | 222 | 74 | 0 | 5.25 | 2.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC1-214 1 |  |  | 1
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 3.33 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 3.05 |  |  | 0.00052 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
923772 | AB2-011_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
923762 | AB2-010_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
244415 | 05OLIV SLR C | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | OLIV SLR |  |  | 1
247967 | 05OLIV SLR E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | OLIV SLR |  |  | 1
270106 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
249991 | 08BUFTN1 | 138 | 212 | 77 | 0 | 2.2 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Z2-113 |  |  | 1
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Z2-113 |  |  | 1
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 4.3 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 4.3 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | MTX | AB1-055 |  |  | 1
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | MTX | Y3-100 |  |  | 1
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | MTX | Y3-099 |  |  | 1
250091 | 08RCHLE3 | 138 | 212 | 77 | 0 | 6.7 | 4.72 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 3.89 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
205922 | AF2-268 E | 115 | 227 | 75 | 0 | 2 | 0.19 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 2.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270181 | AB1-006 W2 | 0.69 | 205 | 74 | 0 | 3.25 | 1.57 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
276603 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 1.54 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Sublette |  |  | 1
342550 | 4BAVARIAN LF | 138 | 320 | 77 | 0 | 4.8 | 3.24 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253234 | 09VERSAL | 69 | 209 | 77 | 0 | 5.4 | 3.91 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.5 | 3.02 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.02 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0.11 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | V4-073 |  |  | 1
243353 | 05OLIVE | 138 | 205 | 77 | 0 | 5 | 3.58 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 2.75 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243017 | 05HAVILAND1 | 138 | 205 | 77 | 0 | 4.5 | 3.22 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247604 | X1-042 | 12 | 205 | 64 | 0 | 3.8 | 2.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253029 | 09GRNVIL | 138 | 209 | 77 | 0 | 4.5 | 3.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | W1-056 |  |  | 1
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Z2-116 |  |  | 1
247969 | Z2-116 E | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Z2-116 |  |  | 1
247968 | Z2-115 E | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | Z2-115 |  |  | 1
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Z2-115 |  |  | 1
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.6 | 1.44 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253128 | 09CELINA | 69 | 209 | 77 | 0 | 4 | 2.89 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.14 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342070 | 2PINE GROVE | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
341584 | 2GRIFFIN | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253160 | 09JCKCEN | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
243362 | 05RANDOLPH1 | 138 | 205 | 77 | 0 | 4 | 3.06 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253158 | 09INDI L | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253303 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.07 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | V4-073 |  |  | 1
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 1.75 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251298 | 08CRITDN | 69 | 212 | 77 | 0 | 2.7 | 1.9 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 2.4 | 1.61 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
341329 | 2COLESBURG | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
342031 | 2PACTOLUS | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.48 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
341200 | 2BROMLEYEK | 69 | 320 | 77 | 0 | 2 | 1.35 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
250041 | 08HAMLTN | 138 | 212 | 77 | 0 | 2.2 | 1.55 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253362 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.28 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-212 |  |  | 1
251542 | 08VERONA | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251269 | 08BEAVR2 | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.3 | 0.72 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246235 | 05BLUFFTON | 69 | 205 | 77 | 0 | 2 | 1.43 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253127 | 09CEDRVL | 69 | 209 | 77 | 0 | 1.8 | 1.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246477 | 05NILES | 69 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246476 | 05NILES | 34.5 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
342442 | 2W GLASGOW | 69 | 320 | 77 | 0 | 1 | 0.67 |  |  | 0.00052 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 610.3 |  |  | 0.00052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 800 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 800 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1330 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AMG3 |  |  | 1
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1300 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | RKG2 |  |  | 1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1356 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | RKG1 |  |  | 1
274662 | QUAD CITI;1U | 18 | 222 | 48 | 132 | 909.5 | 909.5 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274663 | QUAD CITI;2U | 18 | 222 | 48 | 132 | 911.2 | 911.2 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1407 | 1407 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | GVG2 |  |  | 1
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1389 | 1389 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | GVG1 |  |  | 1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1308.8 | 1308.8 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | MTG1 |  |  | 1
274657 | BYRON ;2U | 25 | 222 | 45 | 658.5 | 1141.5 | 1141.5 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274656 | BYRON ;1U | 25 | 222 | 45 | 648.1 | 1168.5 | 1168.5 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 72.8 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 124.2 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 734 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 586 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 600 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274687 | WILL CNTY;4U | 20 | 222 | 15 | 49.4 | 510 | 510 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | WILL4 |  |  | 1
274660 | LASCO STA;1U | 25 | 222 | 49 | 135 | 1131.2 | 1131.2 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274661 | LASCO STA;2U | 25 | 222 | 49 | 132 | 1134.8 | 1134.8 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 1183 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 1154 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 710 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235585 | 01HARRN1 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235587 | 01HARRN3 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235586 | 01HARRN2 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 552 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 545.5 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1186 | 1186 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 1014.5 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 770.1 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241951 | AB1-105 OP | 345 | 202 | 58 | 0 | 850 | 0 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
270122 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 185.22 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | NEW | AB1-107 |  |  | 1
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | NEW | AB1-069 |  |  | 1
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 156.58 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 345.1 | 131.79 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 124.58 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-123 |  |  | 1
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 307.6 | 117.47 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | CAPACITY | Z2-028 |  |  | 1
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 280 | 106.93 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | OREGON |  |  | 1
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | Y2-050 |  |  | 1
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 162.6 | 62.1 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY | FREMONT |  |  | 1
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 159.1 | 60.76 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
253924 | 15SHELL | 138 | 215 | 58 | 0 | 98 | 0 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | ENERGY | Y3-103 |  |  | 1
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 83.83 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | V4-010 |  |  | 1
239024 | 02NWCAG5 | 16.5 | 202 | 57 | 23 | 145 | 55.38 |  |  | 0.0005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 216.9 |  |  | 0.0005 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
907201 | AC2-103 E1 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
907202 | AC2-103 E2 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 38.8 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253970 | 15BI2 | 13.8 | 215 | 58 | 83.2 | 95.6 | 36.51 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
239023 | 02NWCAG4 | 14.4 | 202 | 57 | 20 | 93 | 35.52 |  |  | 0.0005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239022 | 02NWCAG3 | 14.4 | 202 | 57 | 20 | 92.3 | 35.25 |  |  | 0.0005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 29.6 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 28.95 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 28.68 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
918421 | AA1-056 | 345 | 202 | 58 | 0 | 46 | 0 |  |  | 0.00051 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
254026 | 15USSILL | 138 | 215 | 77 | 0 | 66 | 27.72 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 101.27 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 19.51 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 18.94 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.5 | 18.52 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 25 | 0.37 |  |  | 0.0005 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
916002 | 01ELLIOTTS E | 34.5 | 201 | 74 | 0 | 44.9 | 21.63 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | N32 |  |  | 1
254024 | 15CLAIRT | 138 | 215 | 77 | 0 | 35 | 14.7 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 40.5 | 21.78 |  |  | 0.00051 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 1.46 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | 0.0005 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 12.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | V4-010 |  |  | 1
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 0.19 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 0.19 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
237036 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 7.64 |  |  | 0.00051 |  |  |  | 0.1042 |  | 1 | CAPACITY | AD2-002 |  |  | 1
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 6.91 |  |  | 0.0005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
241885 | AC2-103 C1 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
241886 | AC2-103 C2 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 26.1 | 16.36 |  |  | 0.0005 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 20.6 | 11.08 |  |  | 0.00051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
254304 | AE2-114 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AE2-114 |  |  | 1
254305 | AE2-115 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AE2-115 |  |  | 1
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 15.2 | 5.8 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | CAPACITY | Y3-103 |  |  | 1
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 10.54 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 7.55 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | Z1-035 |  |  | 1
237048 | AF1-022 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AF1-022 |  |  | 1
237046 | AF1-021 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AF1-021 |  |  | 1
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0.77 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | W1-045 |  |  | 1
916003 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 13.3 | 6.41 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | K20 |  |  | 1
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0.53 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
270174 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 13.77 |  |  | 0.0005 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
943302 | AF1-001 E | 34.5 | 201 | 75 | 0 | 7.25 | 0.53 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AF1-001 |  |  | 1
941212 | AE2-115 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AE2-115 |  |  | 1
941202 | AE2-114 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AE2-114 |  |  | 1
237039 | AF1-001 C | 34.5 | 201 | 75 | 0 | 6.5 | 0.47 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AF1-001 |  |  | 1
943512 | AF1-022 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AF1-022 |  |  | 1
943502 | AF1-021 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AF1-021 |  |  | 1
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.1 | 0.47 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | W1-045 |  |  | 1
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 9.4 |  |  | 0.00051 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
254303 | AC2-168 C | 138 | 215 | 75 | 0 | 4.4 | 0.32 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 7.03 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 6.96 |  |  | 0.00051 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 2.65 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | N32 |  |  | 1
247454 | 05OGG STREET | 69 | 205 | 77 | 0 | 10 | 7.16 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 0.04 |  |  | 0.0005 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 33.02 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | P.H. GLATFELTER_IPP |  |  | 1
205930 | AF2-099 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AF2-099 |  |  | 1
205931 | AF2-100 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY | AF2-100 |  |  | 1
205920 | AF2-101 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AF2-101 |  |  | 1
205921 | AF2-151 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | AF2-151 |  |  | 1
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 0.88 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 2.69 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 2.69 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 1.13 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | Z1-035 |  |  | 1
958062 | AF2-100 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AF2-100 |  |  | 1
958052 | AF2-099 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEW | AF2-099 |  |  | 1
958072 | AF2-101 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AF2-101 |  |  | 1
958602 | AF2-151 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AF2-151 |  |  | 1
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 0.82 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | K20 |  |  | 1
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.77 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254037 | 15UNIVRS | 138 | 215 | 77 | 0 | 1.1 | 0.46 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243158 | 05WOOSTE | 138 | 205 | 77 | 0 | 1 | 0.72 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245304 | 05WOOSTER | 23 | 205 | 77 | 0 | 1 | 0.72 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245305 | 05WOOSTER | 69 | 205 | 77 | 0 | 1 | 0.72 |  |  | 0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 790.2 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 896 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 30 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 620.4 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 627.1 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 567.5 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253900 | 15BVRVL1 | 22 | 215 | 44 | 781.7 | 898.5 | 898.5 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 899.3 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237054 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 195.92 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 124.5 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | 0.0005 |  |  |  | 0.036 |  | 1 | CAPACITY | T-174 |  |  | 1
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 173.6 | 199.5 | 76.19 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 167 | 191.9 | 73.29 |  |  | 0.00049 |  |  |  | 0.036 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 164.1 | 188.6 | 72.03 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | 0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | 0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
913142 | Y1-033 E OP1 | 0.7 | 226 | 74 | 0 | 34.02 | 20.77 |  |  | 0.00049 |  |  |  | 0 |  | 1 | NEW | Y1-033 |  |  | 1
237043 | AE2-125 C | 25 | 201 | 75 | 0 | 8.28 | 0.6 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 13.36 |  |  | 0.0005 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
941312 | AE2-125 E | 25 | 201 | 75 | 0 | 5.52 | 0.4 |  |  | 0.0005 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 3.05 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | Y1-033 |  |  | 1
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.22 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 2.55 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1247 |  |  | 0.0005 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 410 | 156.58 |  |  | 0.00049 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 236.66 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00049 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-076 |  |  | 1
235621 | 01SBEND3 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00049 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235619 | 01SBEND1 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00049 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235620 | 01SBEND2 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00049 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235622 | 01SBEND4 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00049 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 28.78 |  |  | 0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 28.78 |  |  | 0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 345.42 |  |  | 0.00049 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris2 |  |  | 1
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | 0.00049 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 291.92 |  |  | 0.00049 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris1 |  |  | 1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 44 | 26.86 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | P60 |  |  | 1
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 25.64 |  |  | 0.00049 |  |  |  | 0 |  | 1 | NEW | K23 |  |  | 1
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 19.54 |  |  | 0.00049 |  |  |  | 0 |  | 1 | NEW | L13 |  |  | 1
203939 | AE1-160 C | 34.5 | 226 | 75 | 0 | 12.7 | 1.17 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | AE1-160 |  |  | 1
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 17.58 |  |  | 0.00049 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
237052 | AF1-210 C | 25 | 201 | 75 | 0 | 9.54 | 0.7 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | AF1-210 |  |  | 1
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | 0.00049 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
939292 | AE1-160 E | 34.5 | 226 | 75 | 0 | 7.3 | 0.68 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | AE1-160 |  |  | 1
945452 | AF1-210 E | 25 | 201 | 75 | 0 | 6.36 | 0.46 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | AF1-210 |  |  | 1
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 80.2 |  |  | 0.00048 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 4.22 |  |  | 0.00049 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 5.19 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | P60 |  |  | 1
916004 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | K22 |  |  | 1
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 3.83 |  |  | 0.00049 |  |  |  | 0.0789 |  | 1 | CAPACITY | ALLEG LD_5 |  |  | 1
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 3.77 |  |  | 0.00048 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 3.85 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | Lookout Wind |  |  | 1
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 3.6 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | L13 |  |  | 1
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 4.8 | 2.93 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY | K23 |  |  | 1
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.26 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 1.1 |  |  | 0.00049 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.55 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | K22 |  |  | 1
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.53 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 1119.7 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 749 |  |  | 0.00049 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 851.6 | 851.6 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | Keys2 |  |  | 1
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 852.3 | 852.3 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | Keys1 |  |  | 1
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 850.6 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | Cone1 |  |  | 1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 850 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | Cone2 |  |  | 1
200805 | 26COLVER13 | 13.2 | 226 | 12 | 95.7 | 110 | 0 |  |  | 0.00048 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200503 | 26C.SLOPE | 115 | 226 | 11 | 17 | 50 | 0 |  |  | 0.00048 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208947 | WSHO CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 39.07 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | N39 |  |  | 1
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 62.3 | 38.03 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | R32 |  |  | 1
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | O38 |  |  | 1
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 54.4 | 33.21 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | O18 |  |  | 1
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 31.6 | 19.29 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | Q53 |  |  | 1
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | 0.00047 |  |  |  | 0.1097 |  | 1 | ENERGY |  |  |  | 1
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 17.22 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | V3-030 |  |  | 1
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.00048 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.00048 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200809 | 26SITHE | 138 | 226 | 60 | 0 | 36 | 25.31 |  |  | 0.00047 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 26.2 | 15.99 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | K13 |  |  | 1
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 21.23 |  |  | 0.00048 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
203940 | AF1-140 C | 23 | 226 | 75 | 0 | 9.78 | 0.9 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | AF1-140 |  |  | 1
203932 | AE1-123 | 34.5 | 226 | 55 | 0 | 18 | 9.68 |  |  | 0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
944752 | AF1-140 E | 23 | 226 | 75 | 0 | 6.52 | 0.6 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | AF1-140 |  |  | 1
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 7.75 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | R32 |  |  | 1
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 8.66 |  |  | 0.00048 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 11.1 | 6.78 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | N39 |  |  | 1
957932 | AF2-087 E | 46 | 226 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | AF2-087 |  |  | 1
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.1 | 5.56 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | O38 |  |  | 1
203942 | AF2-270 E | 23 | 226 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | O18 |  |  | 1
203941 | AF2-087 C | 46 | 226 | 75 | 0 | 3.05 | 0.28 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | AF2-087 |  |  | 1
210323 | AF2-286 E | 13.8 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | AF2-286 |  |  | 1
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 3.91 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | Q53 |  |  | 1
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 3.24 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | V3-030 |  |  | 1
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 1.95 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | K13 |  |  | 1
208697 | PRIN B34 | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208885 | WNHO | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208348 | EELI | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
210322 | AF2-286 BAT | 13.8 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00047 |  |  |  | 0 |  | 1 | MTX | AF2-286 |  |  | 1
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 525.7 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 620 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 650 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 614 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 164.5 |  |  | 0.00046 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 155.36 |  |  | 0.00046 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 62 | 33.35 |  |  | 0.00047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213798 | MERCK 3 | 13.8 | 230 | 29 | 13 | 42 | 22.59 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
208942 | HARR CT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 41.7 | 25.46 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | Q36 |  |  | 1
213797 | MERCK 2 | 13.8 | 230 | 29 | 4 | 32 | 17.21 |  |  | 0.00047 |  |  |  | 0.1042 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
237050 | AF1-155 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY | AF1-155 |  |  | 1
203946 | AE2-131 C | 34.5 | 226 | 75 | 0 | 12 | 1.11 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY | AE2-131 |  |  | 1
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 21.09 |  |  | 0.00046 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
944902 | AF1-155 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00046 |  |  |  | 0 |  | 1 | NEW | AF1-155 |  |  | 1
941352 | AE2-131 E | 34.5 | 226 | 75 | 0 | 8 | 0.74 |  |  | 0.00046 |  |  |  | 0 |  | 1 | NEW | AE2-131 |  |  | 1
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 14.76 |  |  | 0.00046 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 7.45 |  |  | 0.00047 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 5.07 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | Q36 |  |  | 1
203944 | AF2-271 E | 46 | 226 | 75 | 0 | 3 | 0.28 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
209945 | AF2-278 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00046 |  |  |  | 0 |  | 1 | NEW | AF2-278 |  |  | 1
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | 0.00047 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 2.75 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
210319 | WCAR 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00046 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210022 | LING 2 | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
209944 | AF2-278 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00046 |  |  |  | 0 |  | 1 | MTX | AF2-278 |  |  | 1
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 30 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 10.2 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204664 | 27AES GEN3 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204662 | 27AES GEN1 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00046 |  |  |  | 0.036 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204663 | 27AES GEN2 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
237083 | AE1-147_GEN | 0.6 | 201 | 75 | 0 | 19.98 | 1.46 |  |  | 0.00045 |  |  |  | 0 |  | 1 | CAPACITY | AE1-147 |  |  | 1
237041 | AE2-055 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
200666 | 26SHAWVL 4 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.00046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200665 | 26SHAWVL 3 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.00045 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
940682 | AE2-055 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
939171 | AE1-147_E | 0.6 | 201 | 75 | 0 | 7.98 | 0.58 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW | AE1-147 |  |  | 1
200722 | 26SHAWVL 2 | 18 | 226 | 30 | 62 | 125 | 117.94 |  |  | 0.00046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200715 | 26SHAWVL 1 | 18 | 226 | 30 | 62 | 123 | 116.05 |  |  | 0.00046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
236828 | 01GRAYMONT | 46 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4 |  |  | 0.00046 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | 0.00045 |  |  |  | 0 |  | 1 | MTX | AC1-025 |  |  | 1
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | 0.00046 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.7 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 42.3 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | 0.00045 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
209937 | AF2-287 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00044 |  |  |  | 0 |  | 1 | NEW | AF2-287 |  |  | 1
209972 | AF2-288 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00044 |  |  |  | 0 |  | 1 | NEW | AF2-288 |  |  | 1
208580 | MGTN 2 | 12.5 | 229 | 77 | 0 | 4.8 | 2.98 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
209971 | AF2-288 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00044 |  |  |  | 0 |  | 1 | MTX | AF2-288 |  |  | 1
209936 | AF2-287 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00044 |  |  |  | 0 |  | 1 | MTX | AF2-287 |  |  | 1
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 1122.1 |  |  | 0.00045 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 34.62 |  |  | 0.00044 |  |  |  | 0 |  | 1 | NEW | Z1-069 |  |  | 1
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 17.1 | 10.44 |  |  | 0.00044 |  |  |  | 0 |  | 1 | CAPACITY | Z1-069 |  |  | 1
214030 | WAYNEJCT | 13.8 | 230 | 29 | 0 | 8.8 | 4.73 |  |  | 0.00044 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 260.87 |  |  | 0.00043 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 32.1 | 17.27 |  |  | 0.00042 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 3.23 |  |  | 0.00042 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205923 | AF2-272 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00042 |  |  |  | 0 |  | 1 | NEW | AF2-272 |  |  | 1
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 5 | 4.26 |  |  | 0.00042 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
959813 | AF2-272 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00042 |  |  |  | 0 |  | 1 | MTX | AF2-272 |  |  | 1
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 102.41 |  |  | 0.00041 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 102.41 |  |  | 0.00041 |  |  |  | 0.036 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 93.75 |  |  | 0.00041 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 49.15 |  |  | 0.00041 |  |  |  | 0 |  | 1 | NEW | P47 |  |  | 1
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.00041 |  |  |  | 0 |  | 1 | NEW | K02 |  |  | 1
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 21.5 | 11.56 |  |  | 0.00042 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.2 | 9.28 |  |  | 0.00041 |  |  |  | 0 |  | 1 | CAPACITY | P47 |  |  | 1
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 75.48 |  |  | 0.00041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
205926 | AF2-429 E | 34.5 | 227 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00041 |  |  |  | 0 |  | 1 | NEW | AF2-429 |  |  | 1
205925 | AF2-428 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00041 |  |  |  | 0 |  | 1 | NEW | AF2-428 |  |  | 1
961383 | AF2-429 BAT | 34.5 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00041 |  |  |  | 0 |  | 1 | MTX | AF2-429 |  |  | 1
961373 | AF2-428 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00041 |  |  |  | 0 |  | 1 | MTX | AF2-428 |  |  | 1
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.00041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 11.3 |  |  | 0.00041 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 11.3 |  |  | 0.00041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205924 | AF2-281 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00041 |  |  |  | 0 |  | 1 | NEW | AF2-281 |  |  | 1
205927 | AF2-430 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00041 |  |  |  | 0 |  | 1 | NEW | AF2-430 |  |  | 1
205928 | AF2-431 E | 69 | 227 | 75 | 0 | 1.17 | 0.11 |  |  | 0.0004 |  |  |  | 0 |  | 1 | NEW | AF2-431 |  |  | 1
959903 | AF2-281 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00041 |  |  |  | 0 |  | 1 | MTX | AF2-281 |  |  | 1
961393 | AF2-430 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00041 |  |  |  | 0 |  | 1 | MTX | AF2-430 |  |  | 1
961403 | AF2-431 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.0004 |  |  |  | 0 |  | 1 | MTX | AF2-431 |  |  | 1
203937 | 26AA1-144 G2 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.00039 |  |  |  | 0 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203936 | 26AA1-144 G1 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.00039 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203938 | 26AA2-132 | 34.5 | 226 | 29 | 0 | 19.9 | 0 |  |  | 0.0004 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.00039 |  |  |  | 0.036 |  | 1 | CAPACITY | X1-109 |  |  | 1
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.00039 |  |  |  | 0 |  | 1 | CAPACITY | X1-109 |  |  | 1
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.11 |  |  | 0.00039 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 213 |  |  | 0.00037 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 130.16 |  |  | 0.00037 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00037 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00037 |  |  |  | 0.036 |  | 1 | CAPACITY | Hummel |  |  | 1
203926 | AA2-133 GEN | 13.8 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.00038 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | 0.00036 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 73.26 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | P28 |  |  | 1
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 31.73 |  |  | 0.00036 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 11.51 |  |  | 0.00036 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 13.37 |  |  | 0.00036 |  |  |  | 0 |  | 1 | CAPACITY | P28 |  |  | 1
209018 | SUNBIPCT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212345 | PENS | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
921653 | AA2-008 E | 230 | 229 | 58 | 0 | 57 | 0 |  |  | 0.00034 |  |  |  | 0.036 |  | 1 | ENERGY | MOXIE PATRIOT |  |  | 1
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 0.26 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208948 | WILL CT | 12.5 | 229 | 55 | 23.1 | 26.6 | 14.31 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 21.4 | 11.51 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 4.3 |  |  | 0.00034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212464 | AF2-289 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AF2-289 |  |  | 1
212451 | AF2-427 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AF2-427 |  |  | 1
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 40.29 |  |  | 0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 30.66 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212455 | AF2-290 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AF2-290 |  |  | 1
212495 | AF2-284 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AF2-284 |  |  | 1
212005 | ALWD | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 5.19 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212435 | SMIL | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212454 | AF2-290 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00035 |  |  |  | 0 |  | 1 | MTX | AF2-290 |  |  | 1
212461 | AF2-289 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00035 |  |  |  | 0 |  | 1 | MTX | AF2-289 |  |  | 1
212450 | AF2-427 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00035 |  |  |  | 0 |  | 1 | MTX | AF2-427 |  |  | 1
212494 | AF2-284 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00035 |  |  |  | 0 |  | 1 | MTX | AF2-284 |  |  | 1
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 758.5 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 757.9 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200048 | BETH CT5 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200044 | BETH CT1 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00034 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH1234 |  |  | 1
916009 | LOR2_Q27 E | 0.7 | 229 | 74 | 0 | 88.8 | 54.21 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | Q27 |  |  | 1
208941 | FISH CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00033 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916008 | LOR1 E | 0.7 | 229 | 74 | 0 | 23.8 | 14.53 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | N14 |  |  | 1
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 81.14 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 77.37 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.2 | 6.84 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | Q27 |  |  | 1
211089 | AF2-277 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AF2-277 |  |  | 1
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.14 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | N14 |  |  | 1
211088 | AF2-277 BAT | 69 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00033 |  |  |  | 0 |  | 1 | MTX | AF2-277 |  |  | 1
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1251.7 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00033 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00033 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1253.3 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 32 |  |  | 0.00032 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 31.63 |  |  | 0.00032 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 26.19 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 26.03 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 23.83 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
211375 | BEAC | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00032 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00032 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 15.92 |  |  | 0.00032 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 15.71 |  |  | 0.00032 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
208944 | JENK CT | 12.5 | 229 | 55 | 24 | 27.6 | 14.85 |  |  | 0.00032 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
946263 | BECR K09 E | 0.69 | 229 | 74 | 0 | 20.7 | 12.64 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | L18 |  |  | 1
211374 | AVOC | 12.5 | 229 | 77 | 0 | 17.4 | 10.8 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.02 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | L18 |  |  | 1
211591 | HARW | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00031 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00031 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00031 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.0003 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH5678 |  |  | 1
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 52.08 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
208940 | ALLE CT | 12.5 | 229 | 55 | 48.7 | 56 | 30.12 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 37.91 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
209031 | WAYM IPP E | 34.5 | 229 | 74 | 0 | 55.5 | 33.88 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | K21 |  |  | 1
209009 | PEIP 2 | 13.8 | 229 | 56 | 38 | 43.7 | 23.5 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | 0.00031 |  |  |  | 0.0975 |  | 1 | MTX | Z2-107 |  |  | 1
209007 | NOEN IPP | 13.8 | 229 | 12 | 96.9 | 111.4 | 105.11 |  |  | 0.0003 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209010 | PEIP 1 | 13.8 | 229 | 64 | 17.4 | 26.5 | 21.42 |  |  | 0.00031 |  |  |  | 0.28996 |  | 1 | CAPACITY |  |  |  | 1
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 7.75 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 5.49 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | K21 |  |  | 1
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 5.34 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
211490 | AF2-282 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AF2-282 |  |  | 1
211554 | AF2-283 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AF2-283 |  |  | 1
211553 | AF2-283 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00031 |  |  |  | 0 |  | 1 | MTX | AF2-283 |  |  | 1
211489 | AF2-282 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00031 |  |  |  | 0 |  | 1 | MTX | AF2-282 |  |  | 1
935072 | AD1-143 E1 | 69 | 229 | 74 | 0 | 34.28 | 20.93 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
211065 | PASP 1_2 C | 13.8 | 229 | 75 | 0 | 8 | 0.74 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AC1-087 |  |  | 1
942581 | PASP 2 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AC1-087 |  |  | 1
926082 | PASP 1 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | U4-014 |  |  | 1
935071 | AD1-143 C1 | 69 | 229 | 75 | 0 | 5.72 | 0.53 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
935082 | AD1-143 E2 | 69 | 229 | 75 | 0 | 4.8 | 0.44 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
211938 | AF2-285 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AF2-285 |  |  | 1
935081 | AD1-143 C2 | 69 | 229 | 75 | 0 | 0.2 | 0.02 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
211937 | AF2-285 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00029 |  |  |  | 0 |  | 1 | MTX | AF2-285 |  |  | 1
208946 | MACR CT | 12.5 | 229 | 55 | 61.4 | 70.6 | 37.97 |  |  | 0.00029 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.47 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00028 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00028 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 128.98 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 107.57 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 107.57 |  |  | 0.00028 |  |  |  | 0.036 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 153 | 82.29 |  |  | 0.00028 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 91.3 | 105 | 56.48 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 89.6 | 103 | 55.4 |  |  | 0.00028 |  |  |  | 0.036 |  | 1 | CAPACITY | GILBERT |  |  | 1
206341 | 28GIL 8 | 13.8 | 228 | 58 | 82.2 | 94.5 | 50.83 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
208920 | WLPK | 12.5 | 229 | 60 | 35.5 | 40.8 | 28.68 |  |  | 0.00028 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
207403 | 28AA2-082 E | 34.5 | 228 | 76 | -18 | 18 | 0 |  |  | 0.00027 |  |  |  | 0.05 |  | 1 | MTX | AA2-082 |  |  | 1
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | W4-073 |  |  | 1
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0.4 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AD2-070 |  |  | 1
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AD2-070 |  |  | 1
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 3.04 | 0.28 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | W4-073 |  |  | 1
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 3.8 | 2.04 |  |  | 0.00026 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | W4-097 |  |  | 1
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | W1-127 |  |  | 1
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0.12 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | U2-059 |  |  | 1
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | W1-127 |  |  | 1
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | W4-097 |  |  | 1
207402 | 28AA2-082 C | 34.5 | 228 | 76 | 0 | 2 | 1.19 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AA2-082 |  |  | 1
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | U2-059 |  |  | 1
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 140.5 | 75.57 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00026 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00026 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204651 | 27PORT CT | 13.8 | 227 | 55 | 4 | 37 | 19.9 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 21 | 11.3 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W3-077 |  |  | 1
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W2-091 |  |  | 1
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W3-077 |  |  | 1
916006 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 4.4 | 2.69 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W2-091 |  |  | 1
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00024 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00024 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00024 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206747 | 28DSM_X3-029 | 34.5 | 228 | 58 | 0 | 11.15 | 0 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
207462 | AF1-133 C | 34.5 | 228 | 75 | 0 | 12 | 1.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AF1-133 |  |  | 1
944682 | AF1-133 E | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF1-133 |  |  | 1
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | W3-044 |  |  | 1
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | W3-044 |  |  | 1
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | W4-046 |  |  | 1
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 0.22 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | W4-046 |  |  | 1
916005 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 3.45 | 2.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | Y2-018 |  |  | 1
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 0.35 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Y2-018 |  |  | 1
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | W2-016 |  |  | 1
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | W2-016 |  |  | 1
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | V4-001 |  |  | 1
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | V4-001 |  |  | 1
207468 | AF1-326 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00022 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207470 | AF1-327 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00021 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207455 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | 0.00022 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | W4-064 |  |  | 1
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | W4-064 |  |  | 1
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | 0.0002 |  |  |  | 0.0975 |  | 1 | MTX | AA2-061 |  |  | 1
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | 0.0002 |  |  |  | 0.0975 |  | 1 | MTX | AA2-060 |  |  | 1
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | X1-012 |  |  | 1
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0.57 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | BeaverRun |  |  | 1
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0.43 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | W3-110 |  |  | 1
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | BeaverRun |  |  | 1
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | X1-012 |  |  | 1
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 0.26 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | W3-110 |  |  | 1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AC2-175 |  |  | 1
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0.12 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AE1-081 |  |  | 1
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.09 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | AE1-081 |  |  | 1
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00017 |  |  |  | 0 |  | 1 | NEW | W2-080 |  |  | 1
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY | W2-080 |  |  | 1
207466 | AF1-324 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00016 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | W3-029 |  |  | 1
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0.93 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | W3-003 |  |  | 1
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00017 |  |  |  | 0 |  | 1 | NEW | W2-050 |  |  | 1
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0.46 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | V3-070 |  |  | 1
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0.38 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | X2-075 |  |  | 1
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | W3-029 |  |  | 1
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | V3-070 |  |  | 1
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 0.21 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | X2-075 |  |  | 1
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | W1-132 |  |  | 1
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | V4-070 |  |  | 1
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | W2-061 |  |  | 1
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | V4-069 |  |  | 1
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | X1-095 |  |  | 1
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | V4-069 |  |  | 1
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | V4-070 |  |  | 1
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | X1-095 |  |  | 1
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | W2-061 |  |  | 1
207456 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | 0.00017 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00014 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
207458 | AD2-210_C | 34.5 | 228 | 76 | 0 | 8 | 0 |  |  | 0.00015 |  |  |  | 0.05 |  | 1 | NEW |  |  |  | 1
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00014 |  |  |  | 0 |  | 1 | CAPACITY | T20 |  |  | 1
916010 | T20SOLAR E | 0.5 | 230 | 75 | 0 | 2 | 1.22 |  |  | 0.00014 |  |  |  | 0 |  | 1 | NEW | T20 |  |  | 1
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0.06 |  |  | 0.00013 |  |  |  | 0 |  | 1 | NEW | AB1-021 |  |  | 1
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.00013 |  |  |  | 0 |  | 1 | CAPACITY | AB1-021 |  |  | 1
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 139.31 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 256.8 | 138.13 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 137.8 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 135.65 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 0.00012 |  |  |  | 0.036 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 113.38 |  |  | 0.00012 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00012 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00012 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 96.22 |  |  | 0.00012 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 96.22 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 50.99 |  |  | 0.00012 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 0.00012 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 0.00012 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 0.00012 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 0.00012 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 43.57 |  |  | 0.00012 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 0.00012 |  |  |  | 0.036 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 18.4 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217831 | PB_NUTCLIF | 26 | 231 | 77 | 0 | 10.7 | 7.21 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217850 | MONTCLAIR_U | 26 | 231 | 77 | 0 | 10.6 | 7.15 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | V2-025 |  |  | 1
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.15 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217194 | REDH C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V2-025 |  |  | 1
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0.15 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | W4-059 |  |  | 1
219910 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0.14 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.24 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | X1-072 |  |  | 1
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | X1-072 |  |  | 1
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0.03 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | V3-065 |  |  | 1
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | V3-066 |  |  | 1
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.02 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W4-059 |  |  | 1
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.02 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V3-065 |  |  | 1
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V3-066 |  |  | 1
218672 | KENILWRTH E | 26.4 | 231 | 65 | 0 | 8 | 0 |  |  | 0.00011 |  |  |  | 0.1097 |  | 1 | NEW |  |  |  | 1
217825 | UMD_NJ | 26 | 231 | 77 | 0 | 10.5 | 7.08 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 3.55 |  |  | 0.00011 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | 0.00011 |  |  |  | 0 |  | 1 | NEW | W1-101 |  |  | 1
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0.06 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | X2-087 |  |  | 1
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.05 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY | W1-101 |  |  | 1
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0.05 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | V3-067 |  |  | 1
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | X2-087 |  |  | 1
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.03 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V3-067 |  |  | 1
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0.03 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEW | V3-068 |  |  | 1
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY | V3-068 |  |  | 1
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 302.3 | 162.6 |  |  | 0.00011 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 302.1 | 162.49 |  |  | 0.0001 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
990902 | TOSCO_E | 18 | 231 | 2 | 0 | 137.5 | 0 |  |  | 0.0001 |  |  |  | 0.1042 |  | 1 | ENERGY | Tosco |  |  | 1
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 45.24 |  |  | 0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 72.1 | 82.9 | 44.59 |  |  | 0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 25.82 |  |  | 0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218344 | TOSCO_G6 | 18 | 231 | 2 | 37 | 42.5 | 22.86 |  |  | 0.0001 |  |  |  | 0.1042 |  | 1 | CAPACITY | Tosco |  |  | 1
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 25.21 |  |  | 0.00011 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
219913 | AD2-042 E | 26.4 | 231 | 75 | 0 | 8.2 | 0.76 |  |  | 0.00011 |  |  |  | 0 |  | 1 | NEW | AD2-042 |  |  | 1
219915 | AD2-027 E | 26.4 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00011 |  |  |  | 0 |  | 1 | NEW | AD2-027 |  |  | 1
219912 | AD2-042 C | 26.4 | 231 | 75 | 0 | 5 | 0.46 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AD2-042 |  |  | 1
219914 | AD2-027 C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AD2-027 |  |  | 1
936193 | AD2-025_E | 13.2 | 231 | 76 | 0 | 2 | 0 |  |  | 0.0001 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
219916 | AD2-025 E | 13.2 | 231 | 76 | -2 | 2 | 0 |  |  | 0.0001 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
218450 | LINSOLAR E | 26.4 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | 0.00011 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218449 | LINSOLAR C | 26.4 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.65 | 3.95 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0.04 |  |  | 0.0001 |  |  |  | 0 |  | 1 | NEW | W2-036 |  |  | 1
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | W2-036 |  |  | 1
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.43 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219001 | SEWAREN7GT | 25 | 231 | 58 | 0 | 324.6 | 174.59 |  |  | 9e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
219002 | SEWAREN7ST | 18 | 231 | 58 | 0 | 216.4 | 116.4 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | 9e-05 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | 9e-05 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.55 | 0.14 |  |  | 9e-05 |  |  |  | 0 |  | 1 | NEW | AC1-030 |  |  | 1
219907 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | AC1-030 |  |  | 1
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0.05 |  |  | 9e-05 |  |  |  | 0 |  | 1 | NEW | X1-071 |  |  | 1
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.03 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | X1-071 |  |  | 1
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 0 |  |  | 9e-05 |  |  |  | 0.0692 |  | 1 | NEW |  |  |  | 1
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0.38 |  |  | 9e-05 |  |  |  | 0 |  | 1 | NEW | AB1-139 |  |  | 1
219908 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 0.23 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | AB1-139 |  |  | 1
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0.21 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | AC1-017 |  |  | 1
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0.2 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | X1-070 |  |  | 1
217212 | AMBOY SO E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 9e-05 |  |  |  | 0 |  | 1 | NEW | V3-069 |  |  | 1
218527 | CNTRALGAS2 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219906 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY | AC1-017 |  |  | 1
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.11 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY | X1-070 |  |  | 1
218526 | CNTRALGAS2 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
217213 | AMBOY SO C | 13.2 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | V3-069 |  |  | 1
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 9e-05 |  |  |  | 0 |  | 1 | NEW | AE1-041 |  |  | 1
219920 | AE1-041 EBAT | 26.4 | 231 | 76 | -0.5 | 0.5 | 0 |  |  | 9e-05 |  |  |  | 0 |  | 1 | MTX | AE1-041 |  |  | 1
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0.03 |  |  | 9e-05 |  |  |  | 0 |  | 1 | NEW | W2-052 |  |  | 1
219919 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | AE1-041 |  |  | 1
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | W2-052 |  |  | 1
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 43.08 |  |  | 7e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 35.07 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 7e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 7e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 7e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 7e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 1.15 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | W3-080 |  |  | 1
218780 | PRINCENTON_U | 26 | 231 | 77 | 0 | 31.56 | 21.27 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 16.18 |  |  | 7e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
924132 | AB2-057 E | 26 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | AB2-057 |  |  | 1
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0.45 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | Z1-096 |  |  | 1
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | W2-102 |  |  | 1
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | W4-103 |  |  | 1
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.2 | 7.55 |  |  | 7e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0.36 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | V2-009 3 |  |  | 1
219903 | AB2-057 C | 26 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY | AB2-057 |  |  | 1
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | Y3-026 |  |  | 1
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y3-026 |  |  | 1
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 0.34 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | W3-080 |  |  | 1
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 3.56 | 0.33 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | W4-103 |  |  | 1
219765 | PARADISE E | 13 | 231 | 75 | 0 | 3.2 | 0.3 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | U4-036 |  |  | 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | V3-024 |  |  | 1
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0.28 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | V2-009 2 |  |  | 1
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 0.28 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | Z1-096 |  |  | 1
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | W2-102 |  |  | 1
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0.23 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | W1-121 Z |  |  | 1
219728 | YARDVSOLFA E | 13.2 | 231 | 75 | 0 | 2.42 | 0.22 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 0.22 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 3 |  |  | 1
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0.22 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | V2-009 4 |  |  | 1
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | 7e-05 |  |  |  | 0 |  | 1 | MTX | X2-013 |  |  | 1
219679 | NRGCENTER E | 13.2 | 231 | 55 | 0 | 2 | 0 |  |  | 7e-05 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
219904 | AC1-010 C | 26.4 | 231 | 75 | 0 | 2.2 | 0.2 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
217199 | V3-059 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | V3-059 |  |  | 1
217198 | V3-058 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | V3-058 |  |  | 1
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | V3-024 |  |  | 1
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | U4-036 |  |  | 1
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 0.17 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 2 |  |  | 1
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0.16 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | W3-124 |  |  | 1
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0.14 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | V2-009 1 |  |  | 1
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Z |  |  | 1
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Y |  |  | 1
219727 | YARDVSOLFA C | 13.2 | 231 | 75 | 0 | 1.48 | 0.14 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
218455 | CINNBAY_CGEN | 26.4 | 231 | 64 | 0 | 9 | 7.66 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 4 |  |  | 1
218525 | CNTRALGAS1 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | X2-088 |  |  | 1
219622 | TRENT_BIOGAS | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0.12 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW | X2-089 |  |  | 1
218524 | CNTRALGAS1 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.1 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | W3-124 |  |  | 1
218781 | BRIS_MYERS | 26 | 231 | 77 | 0 | 3 | 2.02 |  |  | 8e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219685 | NATIONAL_GYP | 26 | 231 | 77 | 0 | 2.8 | 1.89 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 1 |  |  | 1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | X2-088 |  |  | 1
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.07 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY | X2-089 |  |  | 1
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | W1-121 Y |  |  | 1
219922 | AF1-261 | 26.4 | 231 | 75 | 0 | 0.9 | 0.61 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 7e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 22.59 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 16.14 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | Y2-081 |  |  | 1
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y2-081 |  |  | 1
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0.07 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
930243 | AB1-063_E | 69 | 231 | 0 | 0 | 0 | -0.7 |  |  | 6e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0.06 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
932032 | AC2-009 E | 69 | 231 | 75 | -0.5 | 0.49 | 0.05 |  |  | 7e-05 |  |  |  | 0 |  | 1 | NEW | AC2-009 |  |  | 1
219917 | AB1-063 E | 69 | 231 | 75 | 0 | 0.4 | 0.04 |  |  | 6e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | AA2-058 |  |  | 1
219918 | AC2-009 C | 69 | 231 | 75 | -0.1 | 0.1 | 0.01 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY | AC2-009 |  |  | 1
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 43.9 |  |  | 7e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219650 | TRENT_COLLEG | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | 5e-05 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219138 | THOSOLAR E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | 6e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219818 | TRENTONSOL E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | 5e-05 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219137 | THOSOLAR C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 6e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219817 | TRENTONSOL C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 5e-05 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0.04 |  |  | 5e-05 |  |  |  | 0 |  | 1 | NEW | W4-058 |  |  | 1
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | 5e-05 |  |  |  | 0 |  | 1 | CAPACITY | W4-058 |  |  | 1
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 181.64 |  |  | 5e-05 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 164.59 |  |  | 4e-05 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | 4e-05 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | 4e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | 5e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Q90 |  |  | 1
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | 5e-05 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 99.6 | 114.5 | 61.59 |  |  | 4e-05 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 93.2 | 107.1 | 57.61 |  |  | 4e-05 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 133.39 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | 3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | RED OAK |  |  | 1
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 94.67 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | 3e-05 |  |  |  | 0 |  | 1 | MTX | Z1-082 |  |  | 1
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206327 | 28S RIV G1 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | 3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | S RIV |  |  | 1
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 85.3 | 98 | 52.71 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 29.23 |  |  | 3e-05 |  |  |  | 0 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 29.23 |  |  | 3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0.28 |  |  | 1e-05 |  |  |  | 0 |  | 1 | NEW | X3-075 |  |  | 1
219921 | AF1-264 | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | 1e-05 |  |  |  | 0 |  | 1 | CAPACITY | X3-075 |  |  | 1
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0 |  |  |  | 0 |  | 1 | NEW | W4-060 |  |  | 1
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0 |  |  |  | 0 |  | 1 | CAPACITY | W4-060 |  |  | 1
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0.22 |  |  | -1e-05 |  |  |  | 0 |  | 1 | NEW | Y3-087 |  |  | 1
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 0.21 |  |  | -1e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y3-087 |  |  | 1
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0.23 |  |  | -2e-05 |  |  |  | 0 |  | 1 | NEW | W1-112 |  |  | 1
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.17 | 0.11 |  |  | -2e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-112 |  |  | 1
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -4e-05 |  |  |  | 0 |  | 1 | NEW | AC1-207 |  |  | 1
207420 | AC1-207 TAP | 34.5 | 228 | 75 | 0 | 4.9 | 0.45 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | AC1-207 |  |  | 1
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | 0
207454 | AA2-184 E | 34.5 | 228 | 75 | 0 | 11.6 | 1.07 |  |  | -4e-05 |  |  |  | 0 |  | 1 | NEW | BenMoreell |  |  | 1
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -4e-05 |  |  |  | 0 |  | 1 | NEW | W1-124 |  |  | 1
207464 | AF1-023 | 34.5 | 228 | 75 | 0 | 8.4 | 0.78 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | BenMoreell |  |  | 1
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0.52 |  |  | -4e-05 |  |  |  | 0 |  | 1 | NEW | W2-078 |  |  | 1
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -4e-05 |  |  |  | 0 |  | 1 | NEW | W1-113 |  |  | 1
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 3.8 | 0.35 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-124 |  |  | 1
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | W2-078 |  |  | 1
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 0.26 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-113 |  |  | 1
940702 | AE2-057 E | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | AE2-057 |  |  | 1
207461 | AE2-057 C | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | AE2-057 |  |  | 1
207419 | AB2-139 E | 34.5 | 228 | 76 | -0.2 | 0.21 | 0 |  |  | -4e-05 |  |  |  | 0 |  | 1 | MTX | AB2-139 |  |  | 1
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0.98 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | X1-037 |  |  | 1
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 0.39 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | X1-037 |  |  | 1
901032 | W1-024E OP1 | 34.5 | 228 | 75 | 0 | 2.5 | 0.23 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | W1-024 |  |  | 1
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | X4-031 |  |  | 1
940922 | AE2-081 E | 34.5 | 228 | 75 | 0 | 1.75 | 0.16 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | AE2-081 |  |  | 1
207460 | AE2-056 C | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | AE2-056 |  |  | 1
207463 | AE2-081 C | 34.5 | 228 | 75 | 0 | 1.57 | 0.14 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | AE2-081 |  |  | 1
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 0.14 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-024 |  |  | 1
940692 | AE2-056 E | 34.5 | 228 | 75 | 0 | 1.4 | 0.13 |  |  | -5e-05 |  |  |  | 0 |  | 1 | NEW | AE2-056 |  |  | 1
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 34.26 |  |  | -7e-05 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -6e-05 |  |  |  | 0 |  | 1 | NEW | W1-032 |  |  | 1
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -6e-05 |  |  |  | 0 |  | 1 | CAPACITY | W1-032 |  |  | 1
228471 | VALERO1 | 13.8 | 234 | 58 | 19.1 | 22 | 11.83 |  |  | -9e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Valero |  |  | 1
207451 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -8e-05 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
228484 | VALERO4 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228473 | VALERO3 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228472 | VALERO2 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -8e-05 |  |  |  | 0 |  | 1 | NEW | W3-079 |  |  | 1
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -8e-05 |  |  |  | 0 |  | 1 | CAPACITY | W3-079 |  |  | 1
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -8e-05 |  |  |  | 0 |  | 1 | NEW | Y2-051 |  |  | 1
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -8e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y2-051 |  |  | 1
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | -9e-05 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.0001 |  |  |  | 0 |  | 1 | NEW | X1-085 |  |  | 1
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.0001 |  |  |  | 0 |  | 1 | CAPACITY | X1-085 |  |  | 1
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 76.9 | 88.4 | 47.55 |  |  | -0.0001 |  |  |  | 0.036 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.0001 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.0001 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
207179 | 28SIXFLAGS | 34.5 | 228 | 77 | 0 | 17 | 0 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
207450 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -0.0001 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.00011 |  |  |  | 0 |  | 1 | MTX | AA1-060 |  |  | 1
923293 | AB1-138 E | 0.36 | 228 | 75 | 0 | 6 | 0.56 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AB1-138 |  |  | 1
206280 | 28LAKEHURS | 34.5 | 228 | 55 | 0 | 13.7 | 10.22 |  |  | -0.00011 |  |  |  | 0.17131 |  | 1 | CAPACITY |  |  |  | 1
207445 | AB1-138 C | 0.38 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AB1-138 |  |  | 1
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | -0.0001
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 206.63 |  |  | -0.00012 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
939122 | AE1-142 E O1 | 34.5 | 228 | 75 | 0 | 11.8 | 1.09 |  |  | -0.00013 |  |  |  | 0 |  | 1 | NEW | AE1-142 |  |  | 1
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | W2-082 |  |  | 1
207459 | AE1-142 C O1 | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -0.00013 |  |  |  | 0 |  | 1 | CAPACITY | AE1-142 |  |  | 1
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0.75 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | Z2-102 |  |  | 1
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | W1-119 |  |  | 1
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | W1-120 |  |  | 1
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 0.46 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | Z2-102 |  |  | 1
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | W4-025 |  |  | 1
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | W2-019 |  |  | 1
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W1-120 |  |  | 1
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W1-119 |  |  | 1
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | W1-129 |  |  | 1
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W2-082 |  |  | 1
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | X4-015 |  |  | 1
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 0.24 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W4-025 |  |  | 1
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 0.21 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W2-019 |  |  | 1
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | W1-129 |  |  | 1
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.00012 |  |  |  | 0 |  | 1 | CAPACITY | X4-015 |  |  | 1
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.00013 |  |  |  | 0 |  | 1 | NEW | AB1-025 S |  |  | 1
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.00013 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 S |  |  | 1
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0.16 |  |  | -0.00015 |  |  |  | 0 |  | 1 | NEW | W2-071 |  |  | 1
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.1 |  |  | -0.00015 |  |  |  | 0 |  | 1 | CAPACITY | W2-071 |  |  | 1
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0.17 |  |  | -0.00017 |  |  |  | 0 |  | 1 | NEW | V4-005 |  |  | 1
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.1 |  |  | -0.00017 |  |  |  | 0 |  | 1 | CAPACITY | V4-005 |  |  | 1
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 57.7 | 31.03 |  |  | -0.00017 |  |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 57.6 | 30.98 |  |  | -0.00017 |  |  |  | 0.036 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 18.29 |  |  | -0.00017 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 16.67 |  |  | -0.00017 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0.63 |  |  | -0.00017 |  |  |  | 0 |  | 1 | NEW | W2-056 |  |  | 1
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 0.39 |  |  | -0.00017 |  |  |  | 0 |  | 1 | CAPACITY | W2-056 |  |  | 1
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.00017 |  |  |  | 0 |  | 1 | NEW | AB1-025 N |  |  | 1
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.00017 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 N |  |  | 1
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | -0.00018 |  |  |  | 0 |  | 1 | NEW | Y1-075 |  |  | 1
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.00018 |  |  |  | 0 |  | 1 | CAPACITY | Y1-075 |  |  | 1
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  |  |  | -0.0002
228357 | V2-046E | 12.9 | 234 | 75 | 0 | 12.9 | 1.19 |  |  | -0.00031 |  |  |  | 0 |  | 1 | NEW | V2-046 |  |  | 1
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 0.72 |  |  | -0.00031 |  |  |  | 0 |  | 1 | CAPACITY | V2-046 |  |  | 1
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 226.44 |  |  | -0.00032 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
230410 | AE1-218 E O1 | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.00031 |  |  |  | 0 |  | 1 | NEW | AE1-218 |  |  | 1
230409 | AE1-218 C O1 | 12.9 | 234 | 75 | 0 | 0.8 | 0.07 |  |  | -0.00031 |  |  |  | 0 |  | 1 | CAPACITY | AE1-218 |  |  | 1
230403 | AB1-116 E | 12.9 | 234 | 28 | 0 | 0.78 | 0 |  |  | -0.00033 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228721 | V2-035E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.00035 |  |  |  | 0 |  | 1 | NEW | V2-035 |  |  | 1
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.07 |  |  | -0.00035 |  |  |  | 0 |  | 1 | CAPACITY | V2-035 |  |  | 1
924052 | AB2-049 E | 69 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.00037 |  |  |  | 0 |  | 1 | NEW | AB2-049 |  |  | 1
230408 | AD2-065 E | 12.9 | 234 | 75 | 0 | 3.03 | 0.28 |  |  | -0.00036 |  |  |  | 0 |  | 1 | NEW | AD2-065 |  |  | 1
230415 | AB2-049 C | 69 | 234 | 75 | 0 | 1.14 | 0.1 |  |  | -0.00037 |  |  |  | 0 |  | 1 | CAPACITY | AB2-049 |  |  | 1
230407 | AD2-065_C | 12.9 | 234 | 75 | 0 | 1.08 | 0.1 |  |  | -0.00036 |  |  |  | 0 |  | 1 | CAPACITY | AD2-065 |  |  | 1
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0.53 |  |  | -0.00037 |  |  |  | 0 |  | 1 | NEW | W1-130 |  |  | 1
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 0.3 |  |  | -0.00037 |  |  |  | 0 |  | 1 | CAPACITY | W1-130 |  |  | 1
228733 | AB1-119 E | 12.9 | 234 | 28 | 0 | 0.73 | 0 |  |  | -0.00038 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.1 | 39.2 | 21.08 |  |  | -0.00043 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 20.22 |  |  | -0.00043 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.00043 |  |  |  | 0 |  | 1 | NEW | V4-054 |  |  | 1
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 0.35 |  |  | -0.00043 |  |  |  | 0 |  | 1 | CAPACITY | V4-054 |  |  | 1
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 3 | 2.55 |  |  | -0.00043 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0.13 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEW | AB1-001 |  |  | 1
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.08 |  |  | -0.00046 |  |  |  | 0 |  | 1 | CAPACITY | AB1-001 |  |  | 1
228014 | PVILLEG | 0.48 | 234 | 65 | 0 | 1.3 | 0.77 |  |  | -0.00046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
227801 | ONTC&DCT | 13.8 | 234 | 75 | 33.6 | 38.6 | 3.57 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | -0.00046 |  |  |  | 0.30476 |  | 1 | ENERGY |  |  |  | 1
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | -0.00046 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
230414 | AF1-041 E | 69 | 234 | 75 | 0 | 2.4 | 0.22 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEW | AF1-041 |  |  | 1
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 30.66 |  |  | -0.00047 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.1 | 12.43 |  |  | -0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0.56 |  |  | -0.00047 |  |  |  | 0 |  | 1 | NEW | W2-030 |  |  | 1
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 0.34 |  |  | -0.00047 |  |  |  | 0 |  | 1 | CAPACITY | W2-030 |  |  | 1
227928 | V4-067E | 12.9 | 234 | 75 | 0 | 1.6 | 0.15 |  |  | -0.00047 |  |  |  | 0 |  | 1 | NEW | V4-067 |  |  | 1
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.00047 |  |  |  | 0 |  | 1 | NEW | AB2-122 |  |  | 1
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.09 |  |  | -0.00047 |  |  |  | 0 |  | 1 | CAPACITY | V4-067 |  |  | 1
230413 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.06 |  |  | -0.00047 |  |  |  | 0 |  | 1 | CAPACITY | AB2-122 |  |  | 1
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 29.85 |  |  | -0.00049 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  |  |  | -0.0005
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  |  |  | -0.0005
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.3 |  |  |  | -0.0005
TILTON | PJM->LTFIMP_TILTON |  |  | LTF |  | 63 |  |  |  | -0.0005
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  |  |  | -0.0005
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  |  |  | -0.0005
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  |  |  | -0.0005
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  |  |  | -0.0005
MDU | PJM->LTFIMP_MDU |  |  | LTF |  | 10.1 |  |  |  | -0.0005
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  |  |  | -0.0005
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 45.13 |  |  | -0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  |  |  | -0.0005
228712 | V2-041E | 13.2 | 234 | 75 | 0 | 2.48 | 0.23 |  |  | -0.00054 |  |  |  | 0 |  | 1 | NEW | V2-041 |  |  | 1
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 0.14 |  |  | -0.00054 |  |  |  | 0 |  | 1 | CAPACITY | V2-041 |  |  | 1
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.7 |  |  | -0.00053 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 45.99 |  |  | -0.00055 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228203 | P06 | 13.8 | 234 | 57 | 78 | 89.7 | 48.25 |  |  | -0.00058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | -0.00142 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 1145.8 |  |  | -0.00142 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 1138.9 |  |  | -0.00142 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1178.3 |  |  | -0.00143 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 102.2 |  |  | -0.00159 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.00159 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.00159 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.00159 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.0219 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.0219 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 26.36 |  |  | -0.02897 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 25.82 |  |  | -0.02897 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | -0.03208 |  |  |  | 0.036 |  | 1 | NEW | Garrison |  |  | 1
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 103.81 |  |  | -0.03208 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 62.5 |  |  | -0.03208 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
232901 | NORTHST | 69 | 235 | 56 | 5 | 45 | 24.2 |  |  | -0.03208 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 14.34 |  |  | -0.03208 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.55 |  |  | -0.03305 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 111.97 |  |  | -0.07694 |  |  |  | 0 |  | 1 | NEW | AB1-056 |  |  | 1
233906 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 39.32 |  |  | -0.07694 |  |  |  | 0 |  | 1 | CAPACITY | AB1-056 |  |  | 1
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 388.63 |  |  | -0.07694 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232920 | IR10 | 13.2 | 235 | 55 | 14 | 16.1 | 8.66 |  |  | -0.08138 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 0.39 |  |  | -0.08222 |  |  |  | 0 |  | 1 | CAPACITY | AB1-137 |  |  | 1
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0.17 |  |  | -0.08222 |  |  |  | 0 |  | 1 | NEW | AB1-137 |  |  | 1
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.08972 |  |  |  | 0 |  | 1 | CAPACITY | Z2-076 |  |  | 1
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.08972 |  |  |  | 0 |  | 1 | CAPACITY | Z2-077 |  |  | 1
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.08972 |  |  |  | 0 |  | 1 | NEW | Z2-077 |  |  | 1
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.08972 |  |  |  | 0 |  | 1 | NEW | Z2-076 |  |  | 1
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.23 |  |  | -0.11128 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.11549 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.11549 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.11549 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 0.83 |  |  | -0.11549 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232915 | OH NUG4 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.11549 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.11549 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 0.82 |  |  | -0.11549 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 16.08 |  |  | -0.11574 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232905 | CHERITON_25 | 24.9 | 235 | 65 | 0 | 12.5 | 0.23 |  |  | -0.11574 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
917082 | Z2-012 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.11574 |  |  |  | 0 |  | 1 | NEW | Z2-012 |  |  | 1
233901 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.11574 |  |  |  | 0 |  | 1 | CAPACITY | Z2-012 |  |  | 1
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.11584 |  |  |  | 0 |  | 1 | CAPACITY | W1-003 |  |  | 1
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.11584 |  |  |  | 0 |  | 1 | CAPACITY | W1-004 |  |  | 1
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.11584 |  |  |  | 0 |  | 1 | CAPACITY | W1-006 |  |  | 1
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.11584 |  |  |  | 0 |  | 1 | CAPACITY | W1-005 |  |  | 1
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.11584 |  |  |  | 0 |  | 1 | NEW | W1-006 |  |  | 1
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.11584 |  |  |  | 0 |  | 1 | NEW | W1-004 |  |  | 1
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.11584 |  |  |  | 0 |  | 1 | NEW | W1-005 |  |  | 1
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.11584 |  |  |  | 0 |  | 1 | NEW | W1-003 |  |  | 1
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0.37 |  |  | -0.11956 |  |  |  | 0 |  | 1 | NEW | X1-032 |  |  | 1
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 8.6 |  |  | -0.12047 |  |  |  | 0 |  | 1 | NEW | AA1-102 |  |  | 1
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 5.27 |  |  | -0.12047 |  |  |  | 0 |  | 1 | CAPACITY | AA1-102 |  |  | 1
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 6.23 |  |  | -0.12047 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
960882 | AF2-379 E | 69 | 235 | 75 | 0 | 2.26 | 0.21 |  |  | -0.12611 |  |  |  | 0 |  | 1 | NEW | AF2-379 |  |  | 1
233940 | AF2-379 C | 69 | 235 | 75 | 0 | 1.64 | 0.15 |  |  | -0.12611 |  |  |  | 0 |  | 1 | CAPACITY | AF2-379 |  |  | 1
233900 | O-025 C | 25 | 235 | 64 | 0 | 6 | 5.11 |  |  | -0.13294 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 2.83 |  |  | -0.14775 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0.86 |  |  | -0.15194 |  |  |  | 0 |  | 1 | NEW | Y3-058 |  |  | 1
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 8.9 | 0.82 |  |  | -0.15194 |  |  |  | 0 |  | 1 | CAPACITY | Y3-058 |  |  | 1
925262 | AB2-180 E | 0.38 | 235 | 75 | 0 | 6 | 0.56 |  |  | -0.15194 |  |  |  | 0 |  | 1 | NEW | AB2-180 |  |  | 1
233942 | AB2-180 C | 0.38 | 235 | 75 | 0 | 14 | 8.72 |  |  | -0.15194 |  |  |  | 0 |  | 1 | CAPACITY | AB2-180 |  |  | 1
232919 | VN10 | 13.2 | 235 | 55 | 0 | 14.3 | 7.69 |  |  | -0.2168 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0.19 |  |  | -0.25825 |  |  |  | 0 |  | 1 | NEW | Y1-080 |  |  | 1
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 0.12 |  |  | -0.25825 |  |  |  | 0 |  | 1 | CAPACITY | Y1-080 |  |  | 1
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.39196 |  |  |  | 0 |  | 1 | NEW | X3-008 |  |  | 1
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.39196 |  |  |  | 0 |  | 1 | CAPACITY | X3-008 |  |  | 1

## GD-W245
****** PJM Winter Generator Deliverability Detailed Report ****** PJM [TARA Ver 2101.1.0.0 64-bit - Mon Jun 21 18:04:02 2021]
FG Index [All Queue] | 245 | FG ID | 83 | Monitored Facility:314554 3BTLEBRO 115 304223 3ROCKYMT115T 115 1 / Contingency:DVP_P7-1: LN 2058-2181_SRT-A[Tower]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
186 | 110.54 | 105.61 | AC | -11.9 | 202.9 | 0.17 | 14.28 | 0.17 | 205.61 | 196.4 | 0.000578 | 0 | 12633.7 | 0 | 11835 | 0.07609 | 800.82 | 798.69 | 2.13 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | FRMP | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited? | Ramping Limit
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 9.9 | 66 | FiftyFifty | 0.42531 | 23.8599 | 28.0704 |  | 0 | 1 | 1 | CAPACITY | AB2-059 |  |  | 1
316049 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 8.4 | 56 | FiftyFifty | 0.42531 | 20.2447 | 23.8173 |  | 0 | 1 | 1 | CAPACITY | AB1-081 |  |  | 1
316263 | AC1-034 C | 0.55 | 345 | 75 | 0 | 42.75 | 6.41 | 42.75 | FiftyFifty | 0.42531 | 15.4545 | 18.182 |  | 0 | 1 | 1 | CAPACITY | AC1-034 |  |  | 1
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 5.1 | 34 | FiftyFifty | 0.42531 | 12.2914 | 14.4605 |  | 0 | 1 | 1 | NEW | AB2-059 |  |  | 1
925595 | AC1-034 E | 0.55 | 345 | 75 | 0 | 32.25 | 4.84 | 32.25 | FiftyFifty | 0.42531 | 11.6586 | 13.7162 |  | 0 | 1 | 1 | NEW | AC1-034 |  |  | 1
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 3.6 | 24 | FiftyFifty | 0.42531 | 8.6763 | 10.2074 |  | 0 | 1 | 1 | NEW | AB1-081 |  |  | 1
316319 | Z2-044 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 | 8.4 | FiftyFifty | 0.3956 | 2.8246 | 3.323 |  | 0 | 1 | 1 | CAPACITY | Z2-044 |  |  | 1
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0.54 | 3.6 | FiftyFifty | 0.3956 | 1.2105 | 1.4242 |  | 0 | 1 | 1 | NEW | Z2-044 |  |  | 1
316327 | AA2-057 C | 0.63 | 345 | 75 | 0 | 50 | 7.5 | 50 | FiftyFifty | 0.30442 | 12.938 | 15.2211 |  | 0 | 1 | 1 | CAPACITY | AA2-057 |  |  | 1
919710 | AA2-057 E | 0.63 | 345 | 75 | 0 | 24.9 | 3.73 | 24.9 | FiftyFifty | 0.30442 | 6.4431 | 7.5801 |  | 0 | 1 | 1 | NEW | AA2-057 |  |  | 1
316210 | AC1-098 C | 0.6 | 345 | 75 | 0 | 37.6 | 5.64 | 37.6 | FiftyFifty | 0.27132 | 8.6713 | 10.2015 |  | 0 | 1 | 1 | CAPACITY | AC1-098 |  |  | 1
926206 | AC1-098 E | 0.6 | 345 | 75 | 0 | 22.4 | 3.36 | 22.4 | FiftyFifty | 0.27132 | 5.1659 | 6.0775 |  | 0 | 1 | 1 | NEW | AC1-098 |  |  | 1
316212 | AC1-099 C | 0.6 | 345 | 75 | 0 | 12.6 | 1.89 | 12.6 | FiftyFifty | 0.27132 | 2.9058 | 3.4186 |  | 0 | 1 | 1 | CAPACITY | AC1-099 |  |  | 1
926214 | AC1-099 E | 0.6 | 345 | 75 | 0 | 7.4 | 1.11 | 7.4 | FiftyFifty | 0.27132 | 1.7066 | 2.0077 |  | 0 | 1 | 1 | NEW | AC1-099 |  |  | 1
316274 | AC1-208 C | 0.38 | 345 | 75 | 0 | 55.4 | 8.31 | 55.4 | FiftyFifty | 0.25359 | 11.9416 | 14.0489 |  | 0 | 1 | 1 | CAPACITY | AC1-208 |  |  | 1
927146 | AC1-208 E | 0.38 | 345 | 75 | 0 | 24.5 | 0 | 24.5 | FiftyFifty | 0.25359 | 6.213 | 6.213 |  | 0 | 1 | 1 | NEW | AC1-208 |  |  | 1
315131 | 1EDGECMA | 13.8 | 345 | 11 | 7.5 | 58 | 0 | 58 | FiftyFifty | 0.21696 | 12.5835 | 12.5835 |  | 0.1042 | 0.8958 | 1 | NEW |  |  |  | 1
316317 | KELFORD C | 115 | 345 | 75 | 0 | 13.2 | 1.98 | 13.2 | FiftyFifty | 0.14511 | 1.6282 | 1.9155 |  | 0 | 0.8958 | 1 | CAPACITY | Z2-043 |  |  | 1
917332 | KELFORD E | 115 | 345 | 75 | 0 | 7 | 1.05 | 7 | FiftyFifty | 0.14511 | 0.8634 | 1.0158 |  | 0 | 0.8958 | 1 | NEW | Z2-043 |  |  | 1
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 52.7 | 7.91 | 52.7 | FiftyFifty | 0.14228 | 6.3734 | 7.4981 |  | 0 | 0.8958 | 1 | CAPACITY | Z2-088 |  |  | 1
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 7.44 | 49.6 | FiftyFifty | 0.14228 | 5.9985 | 7.057 |  | 0 | 0.8958 | 1 | NEW | Z2-088 |  |  | 1
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 74.1 | 55.58 | 74.1 | FiftyFifty | 0.12479 | 2.3108 | 9.2472 |  | 0.036 | 0.8636 | 1 | CAPACITY | ROSEMARY |  |  | 1
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 45.9 | 34.43 | 45.9 | FiftyFifty | 0.12479 | 1.4314 | 5.728 |  | 0 | 0.8636 | 1 | CAPACITY | ROSEMARY |  |  | 1
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 34.7 | 26.03 | 34.7 | FiftyFifty | 0.12479 | 1.0821 | 4.3303 |  | 0 | 0.8636 | 1 | CAPACITY | ROSEMARY |  |  | 1
316011 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 12.6 | 84 | FiftyFifty | 0.11165 | 7.9715 | 9.3782 |  | 0 | 0.8636 | 1 | NEW | AB1-132 |  |  | 1
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 5.4 | 36 | FiftyFifty | 0.11165 | 3.4164 | 4.0192 |  | 0 | 0.8636 | 1 | NEW | AB1-132 |  |  | 1
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 110 | 110 | FiftyFifty | 0.11165 |  |  |  | 0 | 0.8636 | 1 | CAPACITY |  |  |  | 1
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 110 | 110 | FiftyFifty | 0.11165 |  |  |  | 0 | 0.8636 | 1 | CAPACITY |  |  |  | 1
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 50.3 | 50.3 | FiftyFifty | 0.10985 |  |  |  | 0 | 0.8636 | 1 | CAPACITY |  |  |  | 1
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 48 | 48 | FiftyFifty | 0.10985 |  |  |  | 0 | 0.8636 | 1 | CAPACITY |  |  |  | 1
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 8.22 | 54.8 | FiftyFifty | 0.10701 | 4.9843 | 5.8639 |  | 0 | 0.8636 | 1 | CAPACITY | AA2-053 |  |  | 1
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 3.38 | 22.5 | FiftyFifty | 0.10701 | 2.0465 | 2.4076 |  | 0 | 0.8636 | 1 | NEW | AA2-053 |  |  | 1
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 | 2.13 | Adder/OL | 0.08012 | 0.1703 | 0.2003 | 0.0012 | 0 |  | 1 | ENERGY |  |  |  | 1
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.02647 | 1.5284 | 1.5284 | -0.0334
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.02166 | 0.7581 | 0.7581 | -0.0202
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.01436 | 0.7185 | 0.7185 | -0.0289
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.0141 | 0.7009 | 0.7009 | -0.0287
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.01232 | 2.5881 | 2.5881 | -0.1214
AF2-085 | BATEXP_AF2-085->PJM |  |  | LTF |  | 20 |  | 20 | LTF/CMTX | 0.01158 | 0.2317 | 0.2317 | 0.0116
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00923 | 2.3843 | 2.3843 | -0.1494
MDU | PJM->LTFIMP_MDU |  |  | LTF |  | 10.1 |  | 10.1 | CLTF | 0.00854 | 0.0867 | 0.0867 | -0.0059
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00813 | 0.4438 | 0.4438 | -0.0316
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.3 |  | 173.3 | CLTF | 0.00773 | 1.3387 | 1.3387 | -0.1002
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00765 | 0.4257 | 0.4257 | -0.0322
TILTON | PJM->LTFIMP_TILTON |  |  | LTF |  | 63 |  | 63 | CLTF | 0.00759 | 0.4784 | 0.4784 | -0.0364
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  | 239.8 | LTF/CMTX | 0.00223 | 0.5346 | 0.5346 | 0.1386
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  | 645 | LTF/CMTX | 0.00221 | 1.4224 | 1.4224 | 0.373
AD2-210 | BATEXP_AD2-210->PJM |  |  | LTF |  | 8 |  | 8 | LTF/CMTX | 0.00218 | 0.0175 | 0.0175 | 0.0046
AA2-082 | BATEXP_AA2-082->PJM |  |  | LTF |  | 2 |  | 2 | LTF/CMTX | 0.00215 | 0.0043 | 0.0043 | 0.0012
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 389 |  | 389 | LTF/CBM | 0.00159 | 0.6167 | 0.6167 | 0.225
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 7.64 |  |  | 0.09856 |  |  |  | 0 |  | 1 | CAPACITY | AA1-063A |  |  | 1
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.09856 |  |  |  | 0 |  | 1 | NEW | AA1-063A |  |  | 1
316243 | AE2-151 C | 115 | 345 | 75 | 0 | 6.5 | 0.98 |  |  | 0.09394 |  |  |  | 0 |  | 1 | CAPACITY | AE2-151 |  |  | 1
941542 | AE2-151 E | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.09394 |  |  |  | 0 |  | 1 | NEW | AE2-151 |  |  | 1
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.09177 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0.22 |  |  | 0.09177 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
923994 | AB2-040_E | 0.6 | 345 | 75 | 0 | 69.51 | 10.43 |  |  | 0.09169 |  |  |  | 0 |  | 1 | NEW | AB2-040 |  |  | 1
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 6.06 |  |  | 0.09169 |  |  |  | 0 |  | 1 | CAPACITY | AB1-173 |  |  | 1
316181 | AB2-040 GEN | 0.6 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.09169 |  |  |  | 0 |  | 1 | CAPACITY | AB2-040 |  |  | 1
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.09169 |  |  |  | 0 |  | 1 | NEW | AB1-173 |  |  | 1
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.08716 |  |  |  | 0 |  | 1 | CAPACITY | AB2-174 |  |  | 1
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.08716 |  |  |  | 0 |  | 1 | NEW | AB2-174 |  |  | 1
316318 | V4-068 C | 115 | 345 | 75 | 0 | 3.2 | 0.48 |  |  | 0.08518 |  |  |  | 0 |  | 1 | CAPACITY | V4-068 |  |  | 1
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0.27 |  |  | 0.08518 |  |  |  | 0 |  | 1 | NEW | V4-068 |  |  | 1
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.07887 |  |  |  | 0 |  | 1 | NEW | AA2-088 |  |  | 1
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.07887 |  |  |  | 0 |  | 1 | CAPACITY | AA2-088 |  |  | 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.07627 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 2 |  |  | 1
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.07627 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 1 |  |  | 1
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.07627 |  |  |  | 0 |  | 1 | NEW | AB2-100 1 |  |  | 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.07627 |  |  |  | 0 |  | 1 | NEW | AB2-100 2 |  |  | 1
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 67 | 10.05 |  |  | 0.07252 |  |  |  | 0 |  | 1 | CAPACITY | AA1-065 |  |  | 1
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.07252 |  |  |  | 0 |  | 1 | NEW | AA1-065 |  |  | 1
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 6.68 |  |  | 0.0676 |  |  |  | 0 |  | 1 | CAPACITY | AC1-054 |  |  | 1
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 3.08 |  |  | 0.0676 |  |  |  | 0 |  | 1 | NEW | AC1-054 |  |  | 1
316005 | AA1-067 C | 230 | 345 | 75 | 0 | 10.5 | 1.58 |  |  | 0.06652 |  |  |  | 0 |  | 1 | CAPACITY | AA1-067 |  |  | 1
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0.68 |  |  | 0.06652 |  |  |  | 0 |  | 1 | NEW | AA1-067 |  |  | 1
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53 | 53 |  |  | 0.06506 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314541 | 3WATKINS | 115 | 345 | 75 | 0 | 4 | 0.6 |  |  | 0.06404 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
316174 | AB2-169_C | 0.63 | 345 | 75 | 0 | 39 | 5.85 |  |  | 0.06184 |  |  |  | 0 |  | 1 | CAPACITY | AB2-169 |  |  | 1
925122 | AB2-169 E | 0.63 | 345 | 75 | 0 | 35 | 5.25 |  |  | 0.06184 |  |  |  | 0 |  | 1 | NEW | AB2-169 |  |  | 1
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 11 |  |  | 0.06119 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 7.5 |  |  | 0.06115 |  |  |  | 0 |  | 1 | CAPACITY | AB2-015 |  |  | 1
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 6.15 |  |  | 0.06115 |  |  |  | 0 |  | 1 | NEW | AB2-015 |  |  | 1
961092 | AF2-400 E | 115 | 345 | 75 | 0 | 4.43 | 0.66 |  |  | 0.06115 |  |  |  | 0 |  | 1 | NEW | af2-400 |  |  | 1
316300 | AF2-400 C | 115 | 345 | 75 | 0 | 2.71 | 0.41 |  |  | 0.06115 |  |  |  | 0 |  | 1 | CAPACITY | AF2-400 |  |  | 1
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 37.51 |  |  | 0.0591 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | 0.05712 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 8.4 |  |  | 0.05017 |  |  |  | 0 |  | 1 | CAPACITY | AA2-178 |  |  | 1
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.05017 |  |  |  | 0 |  | 1 | NEW | AA2-178 |  |  | 1
316315 | AB2-025 C | 230 | 345 | 75 | 0 | 13.65 | 2.05 |  |  | 0.04561 |  |  |  | 0 |  | 1 | CAPACITY | AB2-025 |  |  | 1
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.04561 |  |  |  | 0 |  | 1 | NEW | AB2-025 |  |  | 1
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 258.69 |  |  | 0.03916 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.03916 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.03399 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 15 |  |  | 0.03399 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.03399 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.03399 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.03399 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.03399 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.03399 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
901082 | W1-029 E | 230 | 345 | 74 | 0 | 169 | 167.31 |  |  | 0.03295 |  |  |  | 0 |  | 1 | NEW | W1-029 |  |  | 1
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.03295 |  |  |  | 0 |  | 1 | CAPACITY | W1-029 |  |  | 1
316321 | Z2-027 C | 230 | 345 | 75 | 0 | 13.8 | 2.07 |  |  | 0.03077 |  |  |  | 0 |  | 1 | CAPACITY | Z2-027 |  |  | 1
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.03077 |  |  |  | 0 |  | 1 | NEW | Z2-027 |  |  | 1
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 1.95 |  |  | 0.02915 |  |  |  | 0 |  | 1 | CAPACITY | AB2-022 |  |  | 1
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 1.86 |  |  | 0.02915 |  |  |  | 0 |  | 1 | NEW | Y1-086 |  |  | 1
316320 | Y1-086 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.02915 |  |  |  | 0 |  | 1 | CAPACITY | Y1-086 |  |  | 1
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 1.05 |  |  | 0.02915 |  |  |  | 0 |  | 1 | NEW | AB2-022 |  |  | 1
932596 | AC2-079 E | 0.64 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | 0.02866 |  |  |  | 0 |  | 1 | NEW | AC2-079 |  |  | 1
316311 | AC2-079 C | 0.64 | 345 | 75 | 0 | 32.3 | 4.84 |  |  | 0.02866 |  |  |  | 0 |  | 1 | CAPACITY | AC2-079 |  |  | 1
316244 | AE2-225 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.02672 |  |  |  | 0 |  | 1 | CAPACITY | AE2-225 |  |  | 1
316305 | AF2-043 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.02672 |  |  |  | 0 |  | 1 | CAPACITY | AF2-043 |  |  | 1
316246 | AF1-032 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.02672 |  |  |  | 0 |  | 1 | CAPACITY | AF1-032 |  |  | 1
316245 | AE2-229 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.02672 |  |  |  | 0 |  | 1 | CAPACITY | AE2-229 |  |  | 1
942132 | AE2-225 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.02672 |  |  |  | 0 |  | 1 | NEW | AE2-225 |  |  | 1
957492 | AF2-043 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.02672 |  |  |  | 0 |  | 1 | NEW | AF2-043 |  |  | 1
942172 | AE2-229 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.02672 |  |  |  | 0 |  | 1 | NEW | AE2-229 |  |  | 1
943612 | AF1-032 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.02672 |  |  |  | 0 |  | 1 | NEW | AF1-032 |  |  | 1
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 10.06 |  |  | 0.02596 |  |  |  | 0.44065 |  | 1 | CAPACITY |  |  |  | 1
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.02592 |  |  |  | 0 |  | 1 | NEW | AB2-043 |  |  | 1
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 2.84 |  |  | 0.02592 |  |  |  | 0 |  | 1 | CAPACITY | AB2-043 |  |  | 1
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 8.16 |  |  | 0.02556 |  |  |  | 0 |  | 1 | CAPACITY | AB2-060 |  |  | 1
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 3.84 |  |  | 0.02556 |  |  |  | 0 |  | 1 | NEW | AB2-060 |  |  | 1
316237 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.02556 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
316238 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.02556 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
316239 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.02556 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.02556 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.02556 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.02556 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.02549 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 2.85 |  |  | 0.02549 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
316150 | AD2-215 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.02492 |  |  |  | 0 |  | 1 | CAPACITY | AD2-215 |  |  | 1
316072 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 1.46 |  |  | 0.02492 |  |  |  | 0 |  | 1 | CAPACITY | AD1-144 |  |  | 1
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.02492 |  |  |  | 0 |  | 1 | NEW | AD1-144 |  |  | 1
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.02492 |  |  |  | 0 |  | 1 | NEW | AD2-215 |  |  | 1
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 11.81 |  |  | 0.02483 |  |  |  | 0 |  | 1 | CAPACITY | AA1-139 |  |  | 1
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | 0.02483 |  |  |  | 0 |  | 1 | NEW | AA1-139 |  |  | 1
932586 | AC2-078 E | 0.64 | 345 | 75 | 0 | 37.2 | 5.58 |  |  | 0.02408 |  |  |  | 0 |  | 1 | NEW | AC2-078 |  |  | 1
316289 | AC2-078 C | 0.64 | 345 | 75 | 0 | 22.8 | 3.42 |  |  | 0.02408 |  |  |  | 0 |  | 1 | CAPACITY | AC2-078 |  |  | 1
316057 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.02209 |  |  |  | 0 |  | 1 | CAPACITY | AC2-196 |  |  | 1
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 1 |  |  | 0.02209 |  |  |  | 0 |  | 1 | NEW | AC2-196 |  |  | 1
316185 | AD1-033 C | 0.6 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.02204 |  |  |  | 0 |  | 1 | CAPACITY | AD1-033 |  |  | 1
934065 | AD1-033 E | 0.6 | 345 | 75 | 0 | 28 | 4.2 |  |  | 0.02204 |  |  |  | 0 |  | 1 | NEW | AD1-033 |  |  | 1
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 10.4 |  |  | 0.02167 |  |  |  | 0 |  | 1 | NEW | Z1-068 |  |  | 1
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.49 |  |  | 0.02167 |  |  |  | 0 |  | 1 | CAPACITY | Z1-068 |  |  | 1
316316 | AC1-027 C | 115 | 345 | 75 | 0 | 11.2 | 1.68 |  |  | 0.02165 |  |  |  | 0 |  | 1 | CAPACITY | AC1-027 |  |  | 1
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.02165 |  |  |  | 0 |  | 1 | NEW | AC1-027 |  |  | 1
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 7.56 |  |  | 0.02117 |  |  |  | 0.1097 |  | 1 | CAPACITY | VIRGINIA BEACH LF_A |  |  | 1
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 12.9 |  |  | 0.02107 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 15.2 |  |  | 0.02107 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 11.9 |  |  | 0.02107 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 1.39 |  |  | 0.02105 |  |  |  | 0 |  | 1 | NEW | AC1-036 |  |  | 1
316034 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 1.29 |  |  | 0.02105 |  |  |  | 0 |  | 1 | CAPACITY | AC1-036 |  |  | 1
315099 | 1CHESPKB | 13.8 | 345 | 20 | 0 | 24.7 | 0 |  |  | 0.02098 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 0.45 |  |  | 0.02098 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316036 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | 0.02098 |  |  |  | 0 |  | 1 | CAPACITY | AC1-147 |  |  | 1
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.02098 |  |  |  | 0 |  | 1 | NEW | AC1-147 |  |  | 1
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 83.11 |  |  | 0.02082 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 82.06 |  |  | 0.02082 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 80.64 |  |  | 0.02082 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | 0.02033 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 4.56 |  |  | 0.02033 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 6.71 |  |  | 0.02033 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
316236 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.02027 |  |  |  | 0 |  | 1 | CAPACITY | AE1-162 |  |  | 1
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.02027 |  |  |  | 0 |  | 1 | NEW | AE1-162 |  |  | 1
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 0.89 |  |  | 0.02002 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 65.18 |  |  | 0.02002 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 65.11 |  |  | 0.02002 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.02002 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.02002 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 844.6 |  |  | 0.02002 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316241 | AE2-078 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.01966 |  |  |  | 0 |  | 1 | CAPACITY | AE2-078 |  |  | 1
316247 | AF1-033 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.01966 |  |  |  | 0 |  | 1 | CAPACITY | AF1-033 |  |  | 1
316242 | AE2-079 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.01966 |  |  |  | 0 |  | 1 | CAPACITY | AE2-079 |  |  | 1
943622 | AF1-033 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.01966 |  |  |  | 0 |  | 1 | NEW | AF1-033 |  |  | 1
940892 | AE2-078 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.01966 |  |  |  | 0 |  | 1 | NEW | AE2-078 |  |  | 1
940902 | AE2-079 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.01966 |  |  |  | 0 |  | 1 | NEW | AE2-079 |  |  | 1
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 10.77 |  |  | 0.01909 |  |  |  | 0 |  | 1 | CAPACITY | AB2-134 |  |  | 1
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 10.59 |  |  | 0.01909 |  |  |  | 0 |  | 1 | NEW | AB2-134 |  |  | 1
316301 | AE2-228 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.01904 |  |  |  | 0 |  | 1 | CAPACITY | AE2-228 |  |  | 1
942162 | AE2-228 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.01904 |  |  |  | 0 |  | 1 | NEW | AE2-228 |  |  | 1
316240 | AF1-291 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.01888 |  |  |  | 0 |  | 1 | CAPACITY | AF1-291 |  |  | 1
946262 | AF1-291 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.01888 |  |  |  | 0 |  | 1 | NEW | AF1-291 |  |  | 1
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 16.8 |  |  | 0.01884 |  |  |  | 0 |  | 1 | CAPACITY | AB2-190 |  |  | 1
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 7.2 |  |  | 0.01884 |  |  |  | 0 |  | 1 | NEW | AB2-190 |  |  | 1
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | 0.01793 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 94.51 |  |  | 0.01793 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.01793 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.01793 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.01793 |  |  |  | 0.036 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 52.8 | 52.8 |  |  | 0.01793 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 4.5 |  |  | 0.01764 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 787.1 | 23.61 |  |  | 0.01733 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 15.7 | 10.53 |  |  | 0.01688 |  |  |  | 0.1097 |  | 1 | CAPACITY | AMELIA LF_1-A |  |  | 1
313853 | 3PONTONDP | 115 | 345 | 65 | 0 | 4 | 0 |  |  | 0.01688 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 843.5 |  |  | 0.01633 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316294 | AC1-161 C | 0.44 | 345 | 75 | 0 | 168.2 | 25.23 |  |  | 0.01611 |  |  |  | 0 |  | 1 | CAPACITY | AC1-161 |  |  | 1
926755 | AC1-161 E | 0.44 | 345 | 75 | 0 | 71.8 | 0 |  |  | 0.01611 |  |  |  | 0 |  | 1 | NEW | AC1-161 |  |  | 1
316159 | AE1-175 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.01586 |  |  |  | 0 |  | 1 | CAPACITY | AE1-175 |  |  | 1
316160 | AE1-175 E | 230 | 345 | 75 | 0 | 6.6 | 0.99 |  |  | 0.01586 |  |  |  | 0 |  | 1 | NEW | AE1-175 |  |  | 1
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 98.04 |  |  | 0.01546 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 96.46 |  |  | 0.01546 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 49.66 |  |  | 0.01546 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 45.01 |  |  | 0.01546 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316074 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.01541 |  |  |  | 0 |  | 1 | CAPACITY | AD1-157 |  |  | 1
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.01541 |  |  |  | 0 |  | 1 | NEW | AD1-157 |  |  | 1
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.1 | 10.8 |  |  | 0.01501 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHARLES CITY_LF |  |  | 1
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 1.97 |  |  | 0.015 |  |  |  | 0 |  | 1 | CAPACITY | AD2-030 |  |  | 1
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.015 |  |  |  | 0 |  | 1 | NEW | AD2-030 |  |  | 1
316280 | AD1-041 C | 0.55 | 345 | 75 | 0 | 30 | 4.5 |  |  | 0.01494 |  |  |  | 0 |  | 1 | CAPACITY | AD1-041 |  |  | 1
934146 | AD1-041 E | 0.55 | 345 | 75 | 0 | 20 | 3 |  |  | 0.01494 |  |  |  | 0 |  | 1 | NEW | AD1-041 |  |  | 1
316201 | AC1-065 C | 0.39 | 345 | 75 | 0 | 49.4 | 7.41 |  |  | 0.0149 |  |  |  | 0 |  | 1 | CAPACITY | AC1-065 |  |  | 1
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.0149 |  |  |  | 0 |  | 1 | NEW | AC1-065 |  |  | 1
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 20 |  |  | 0.0149 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316059 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.01474 |  |  |  | 0 |  | 1 | CAPACITY | AD1-063 |  |  | 1
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.01474 |  |  |  | 0 |  | 1 | NEW | AD1-063 |  |  | 1
313053 | 6PAPERMILL | 230 | 345 | 77 | 12 | 37 | 0 |  |  | 0.01462 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
316314 | AB2-024 C | 230 | 345 | 75 | 0 | 11.13 | 1.67 |  |  | 0.01458 |  |  |  | 0 |  | 1 | CAPACITY | AB2-024 |  |  | 1
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.01458 |  |  |  | 0 |  | 1 | NEW | AB2-024 |  |  | 1
316304 | AE2-227 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.01458 |  |  |  | 0 |  | 1 | CAPACITY | AE2-227 |  |  | 1
942152 | AE2-227 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.01458 |  |  |  | 0 |  | 1 | NEW | AE2-227 |  |  | 1
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 9.99 |  |  | 0.01458 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHESTERFIELD LF_A |  |  | 1
315085 | 1SPRUNCC | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.01443 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315086 | 1SPRUNCD | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.01443 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316169 | AC1-164 GEN | 0.44 | 345 | 75 | 192.1 | 220.8 | 33.12 |  |  | 0.01423 |  |  |  | 0 |  | 1 | CAPACITY | AC1-164 |  |  | 1
926785 | AC1-164_E | 0.44 | 345 | 75 | 91 | 104.6 | 15.69 |  |  | 0.01423 |  |  |  | 0 |  | 1 | NEW | AC1-164 |  |  | 1
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 12.7 | 1.9 |  |  | 0.01416 |  |  |  | 0 |  | 1 | CAPACITY | AC2-137 |  |  | 1
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.01416 |  |  |  | 0 |  | 1 | NEW | AC2-137 |  |  | 1
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 64.51 |  |  | 0.01405 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 64.43 |  |  | 0.01405 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 64.21 |  |  | 0.01405 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 64.14 |  |  | 0.01405 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 6.2 |  |  | 0.01401 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 0.75 |  |  | 0.01367 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 0.72 |  |  | 0.01367 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | 0.01367 |  |  |  | 0 |  | 1 | CAPACITY | AC2-138 |  |  | 1
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.01367 |  |  |  | 0 |  | 1 | NEW | AC2-138 |  |  | 1
316312 | AB1-027 C | 230 | 345 | 75 | 0 | 17.5 | 2.63 |  |  | 0.01335 |  |  |  | 0 |  | 1 | CAPACITY | AB1-027 |  |  | 1
316004 | AC1-112 C | 230 | 345 | 75 | 0 | 10.9 | 1.63 |  |  | 0.01335 |  |  |  | 0 |  | 1 | CAPACITY | AC1-112 |  |  | 1
316050 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 1.38 |  |  | 0.01335 |  |  |  | 0 |  | 1 | CAPACITY | AC2-070 |  |  | 1
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 7.5 | 1.13 |  |  | 0.01335 |  |  |  | 0 |  | 1 | NEW | AB1-027 |  |  | 1
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0.92 |  |  | 0.01335 |  |  |  | 0 |  | 1 | NEW | AC1-112 |  |  | 1
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0.57 |  |  | 0.01335 |  |  |  | 0 |  | 1 | NEW | AC2-070 |  |  | 1
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | 0.0131 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.0131 |  |  |  | 0.036 |  | 1 | NEW | AC1-107 |  |  | 1
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.0131 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 4 |  |  | 0.01279 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316223 | AC1-118 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.0127 |  |  |  | 0 |  | 1 | CAPACITY | AC1-118 |  |  | 1
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.0127 |  |  |  | 0 |  | 1 | NEW | AC1-118 |  |  | 1
316233 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.01237 |  |  |  | 0 |  | 1 | CAPACITY | AE1-074 |  |  | 1
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.01237 |  |  |  | 0 |  | 1 | NEW | AE1-074 |  |  | 1
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 7.38 |  |  | 0.01205 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
316234 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.012 |  |  |  | 0 |  | 1 | CAPACITY | AE1-124 |  |  | 1
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.012 |  |  |  | 0 |  | 1 | NEW | AE1-124 |  |  | 1
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 127.52 |  |  | 0.01185 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316303 | AF2-085 | 230 | 345 | 76 | 0 | 20 | 13.41 |  |  | 0.01158 |  |  |  | 0.05 |  | 1 | CAPACITY |  |  |  | 1
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 165.2 | 123.92 |  |  | 0.01156 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 165.1 | 123.84 |  |  | 0.01156 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 126.7 | 95.04 |  |  | 0.01156 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 124.8 | 93.61 |  |  | 0.01156 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.01156 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.01156 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.01156 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.01156 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 8.7 |  |  | 0.01004 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316313 | AB2-026 C | 230 | 345 | 75 | 0 | 13.07 | 1.96 |  |  | 0.0095 |  |  |  | 0 |  | 1 | CAPACITY | AB2-026 |  |  | 1
316258 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.0095 |  |  |  | 0 |  | 1 | CAPACITY | AE1-075 |  |  | 1
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.0095 |  |  |  | 0 |  | 1 | NEW | AB2-026 |  |  | 1
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0.88 |  |  | 0.0095 |  |  |  | 0 |  | 1 | NEW | AE1-075 |  |  | 1
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00886 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00886 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 120.47 |  |  | 0.00886 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 120.09 |  |  | 0.00886 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 119.87 |  |  | 0.00886 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 2 |  |  | 0.00816 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 948.9 |  |  | 0.00788 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 948.5 |  |  | 0.00788 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 1.07 | 0.16 |  |  | 0.00756 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
316045 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00713 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 2 |  |  | 1
316044 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00713 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 1 |  |  | 1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00713 |  |  |  | 0 |  | 1 | NEW | AC1-158 2 |  |  | 1
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00713 |  |  |  | 0 |  | 1 | NEW | AC1-158 1 |  |  | 1
316192 | AB2-158 C | 230 | 345 | 75 | 0 | 71 | 10.65 |  |  | 0.00678 |  |  |  | 0 |  | 1 | CAPACITY | AB2-158 |  |  | 1
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 4.08 |  |  | 0.00678 |  |  |  | 0 |  | 1 | NEW | AB2-158 |  |  | 1
926004 | AC1-076_E | 0.6 | 345 | 75 | 0 | 39.42 | 5.91 |  |  | 0.00668 |  |  |  | 0 |  | 1 | NEW | AC1-076 |  |  | 1
316164 | AC1-076_C | 0.6 | 345 | 75 | 0 | 23.8 | 3.57 |  |  | 0.00668 |  |  |  | 0 |  | 1 | CAPACITY | AC1-076 |  |  | 1
316051 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00662 |  |  |  | 0 |  | 1 | CAPACITY | AC2-071 |  |  | 1
316322 | AB2-045 C | 230 | 345 | 75 | 0 | 11.43 | 1.72 |  |  | 0.00662 |  |  |  | 0 |  | 1 | CAPACITY | AB2-045 |  |  | 1
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00662 |  |  |  | 0 |  | 1 | NEW | AC2-071 |  |  | 1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.00662 |  |  |  | 0 |  | 1 | NEW | AB2-045 |  |  | 1
316254 | AC1-120 C | 0.6 | 345 | 75 | 0 | 39.6 | 5.94 |  |  | 0.00635 |  |  |  | 0 |  | 1 | CAPACITY | AC1-120 |  |  | 1
926486 | AC1-120 E | 0.6 | 345 | 75 | 0 | 20.4 | 3.06 |  |  | 0.00635 |  |  |  | 0 |  | 1 | NEW | AC1-120 |  |  | 1
316170 | AC1-121 C | 0.6 | 345 | 75 | 0 | 13.6 | 2.04 |  |  | 0.00635 |  |  |  | 0 |  | 1 | CAPACITY | AC1-121 |  |  | 1
926502 | AC1-121 E | 0.6 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.00635 |  |  |  | 0 |  | 1 | NEW | AC1-121 |  |  | 1
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 185.28 |  |  | 0.00634 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00634 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00634 |  |  |  | 0.036 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 188.28 |  |  | 0.00632 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00632 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00632 |  |  |  | 0.036 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 1.07 |  |  | 0.00632 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 1.07 |  |  | 0.00632 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
925672 | AC1-043 E | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.00626 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
316257 | AC1-043 C | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00626 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
961102 | AF2-401 E | 115 | 345 | 75 | 0 | 5.8 | 0.87 |  |  | 0.00618 |  |  |  | 0 |  | 1 | NEW | AF2-401 |  |  | 1
316302 | AF2-401 C | 115 | 345 | 75 | 0 | 3.52 | 0.53 |  |  | 0.00618 |  |  |  | 0 |  | 1 | CAPACITY | AF2-401 |  |  | 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00615 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00615 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00615 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00615 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
316267 | AC1-143 C | 0.38 | 345 | 75 | 0 | 41.2 | 6.18 |  |  | 0.00611 |  |  |  | 0 |  | 1 | CAPACITY | AC1-143 |  |  | 1
926615 | AC1-143 E | 0.38 | 345 | 75 | 0 | 18.8 | 2.82 |  |  | 0.00611 |  |  |  | 0 |  | 1 | NEW | AC1-143 |  |  | 1
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 118.52 |  |  | 0.0061 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.0061 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.0061 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.0061 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 57.83 |  |  | 0.0061 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 1.83 |  |  | 0.00608 |  |  |  | 0 |  | 1 | NEW | AB2-029 |  |  | 1
316006 | AB2-029 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.00608 |  |  |  | 0 |  | 1 | CAPACITY | AB2-029 |  |  | 1
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00605 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00605 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 120.39 |  |  | 0.00605 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 170 | 127.52 |  |  | 0.00604 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 113.79 |  |  | 0.00604 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.1 | 113.34 |  |  | 0.00604 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 112.29 |  |  | 0.00604 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00593 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00593 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314088 | 6VANDORN | 230 | 345 | 1 | 7 | 21 | 14.08 |  |  | 0.00593 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316052 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00581 |  |  |  | 0 |  | 1 | CAPACITY | AC2-072 |  |  | 1
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00581 |  |  |  | 0 |  | 1 | NEW | AC2-072 |  |  | 1
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 301.17 |  |  | 0.00569 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00569 |  |  |  | 0.036 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00569 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00569 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 448.57 |  |  | 0.00545 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00545 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00545 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00545 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 229.53 |  |  | 0.00515 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00515 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00515 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-039 |  |  | 1
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 327.3 | 176.05 |  |  | 0.00506 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.00506 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-035 |  |  | 1
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.00506 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 43.03 |  |  | 0.00503 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.00503 |  |  |  | 0.036 |  | 1 | CAPACITY | PANDA |  |  | 1
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.00503 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
226704 | AOCX4-046 E | 13.8 | 233 | 58 | 0 | 19.5 | 0 |  |  | 0.00503 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.00503 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226924 | AE1-015 E | 69 | 233 | 75 | 0 | 0.75 | 0.07 |  |  | 0.00503 |  |  |  | 0 |  | 1 | NEW | AE1-015 |  |  | 1
226923 | AE1-015 C | 69 | 233 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00503 |  |  |  | 0 |  | 1 | CAPACITY | AE1-015 |  |  | 1
226922 | AE1-013 E | 69 | 233 | 75 | 0 | 0.5 | 0.05 |  |  | 0.00503 |  |  |  | 0 |  | 1 | NEW | AE1-013 |  |  | 1
226921 | AE1-013 C | 69 | 233 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00503 |  |  |  | 0 |  | 1 | CAPACITY | AE1-013 |  |  | 1
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 1.17 |  |  | 0.00492 |  |  |  | 0 |  | 1 | NEW | AC1-116 |  |  | 1
316035 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 0.7 |  |  | 0.00492 |  |  |  | 0 |  | 1 | CAPACITY | AC1-116 |  |  | 1
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 182.23 |  |  | 0.00481 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.00481 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.00481 |  |  |  | 0.036 |  | 1 | CAPACITY | WALDORF |  |  | 1
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 1.86 |  |  | 0.00479 |  |  |  | 0 |  | 1 | NEW | AC2-101 |  |  | 1
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 1.58 |  |  | 0.00479 |  |  |  | 0 |  | 1 | NEW | AC2-120 |  |  | 1
227282 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 1.14 |  |  | 0.00479 |  |  |  | 0 |  | 1 | CAPACITY | AC2-101 |  |  | 1
227280 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 0.97 |  |  | 0.00479 |  |  |  | 0 |  | 1 | CAPACITY | AC2-120 |  |  | 1
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.0048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.0048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 619.4 |  |  | 0.0048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 613.3 |  |  | 0.0048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 11.01 |  |  | 0.00476 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 10.83 |  |  | 0.00476 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.00476 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.00476 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.00476 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.00476 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227024 | SMECOCT | 13.8 | 238 | 57 | 0 | 80.2 | 43.14 |  |  | 0.00476 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 13.12 |  |  | 0.00476 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 9.68 |  |  | 0.00476 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.91 |  |  | 0.00471 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0.16 |  |  | 0.0047 |  |  |  | 0 |  | 1 | NEW | AB2-157 |  |  | 1
226910 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.07 |  |  | 0.0047 |  |  |  | 0 |  | 1 | CAPACITY | AB2-157 |  |  | 1
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 841.8 |  |  | 0.00463 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 866 |  |  | 0.00463 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226920 | AE1-012 E | 115 | 233 | 75 | 0 | 0.34 | 0.03 |  |  | 0.00453 |  |  |  | 0 |  | 1 | NEW | AE1-012 |  |  | 1
226919 | AE1-012 C | 115 | 233 | 75 | 0 | 0.22 | 0.02 |  |  | 0.00453 |  |  |  | 0 |  | 1 | CAPACITY | AE1-012 |  |  | 1
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 0.33 |  |  | 0.00442 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.00441 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.00441 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 52 |  |  | 0.00441 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 422.31 |  |  | 0.00434 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00434 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00434 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00434 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00433 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.87 |  |  | 0.00424 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223967 | METZ E69 | 69 | 233 | 56 | 0 | 20 | 0 |  |  | 0.00422 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226895 | WOAKV2-037 E | 69 | 233 | 29 | 0 | 4.5 | 0 |  |  | 0.00422 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 45.6 |  |  | 0.00421 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.64 |  |  | 0.00415 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 5.18 |  |  | 0.0041 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 2.54 |  |  | 0.0041 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 395.08 |  |  | 0.00405 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00405 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00405 |  |  |  | 0.036 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00405 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 3.62 |  |  | 0.00396 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
237026 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 2.22 |  |  | 0.00396 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 7.34 |  |  | 0.00379 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 642.7 |  |  | 0.00379 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 638.9 |  |  | 0.00379 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 68.9 |  |  | 0.00374 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 289.09 |  |  | 0.00374 |  |  |  | 0.1042 |  | 1 | CAPACITY | Wagner3 |  |  | 1
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.00374 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 7.15 |  |  | 0.00374 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00368 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
923213 | AB1-125_E | 0.6 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00367 |  |  |  | 0 |  | 1 | NEW | AB1-125 |  |  | 1
237006 | AB1-125_C | 0.6 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00367 |  |  |  | 0 |  | 1 | CAPACITY | AB1-125 |  |  | 1
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 57 |  |  | 0.00367 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.2 | 16.24 |  |  | 0.00365 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 29.8 | 16.03 |  |  | 0.00365 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220904 | CRANE G2 | 20 | 232 | 12 | 0 | 14 | 0 |  |  | 0.00355 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 0.76 |  |  | 0.00347 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00347 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
237025 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00347 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00347 |  |  |  | 0 |  | 1 | NEW | Z2-030 |  |  | 1
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00347 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0.44 |  |  | 0.00347 |  |  |  | 0 |  | 1 | NEW | AB1-096 |  |  | 1
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00347 |  |  |  | 0 |  | 1 | CAPACITY | Z2-030 |  |  | 1
237077 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00347 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
237030 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 0.23 |  |  | 0.00347 |  |  |  | 0 |  | 1 | CAPACITY | AB1-096 |  |  | 1
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.39 |  |  | 0.00344 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 139.8 | 75.19 |  |  | 0.0034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 61.1 |  |  | 0.0034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 55.94 |  |  | 0.0034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 27.97 |  |  | 0.0034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223401 | AF1-299 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.0034 |  |  |  | 0 |  | 1 | CAPACITY | AF1-299 |  |  | 1
223402 | AF1-300 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.0034 |  |  |  | 0 |  | 1 | CAPACITY | AF1-300 |  |  | 1
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0.63 |  |  | 0.00341 |  |  |  | 0 |  | 1 | NEW | W1-116 |  |  | 1
946352 | AF1-299 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.0034 |  |  |  | 0 |  | 1 | NEW | AF1-299 |  |  | 1
946362 | AF1-300 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.0034 |  |  |  | 0 |  | 1 | NEW | AF1-300 |  |  | 1
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 0.39 |  |  | 0.00341 |  |  |  | 0 |  | 1 | CAPACITY | W1-116 |  |  | 1
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.4 |  |  | 0.0034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237003 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0.76 |  |  | 0.00339 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.00339 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.00339 |  |  |  | 0 |  | 1 | CAPACITY | AA1-109 |  |  | 1
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.00339 |  |  |  | 0 |  | 1 | NEW | AA1-109 |  |  | 1
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 1.87 |  |  | 0.00337 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 1.44 |  |  | 0.00331 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00329 |  |  |  | 0 |  | 1 | NEW | AA2-072 |  |  | 1
316299 | AC2-112 C | 0.6 | 345 | 75 | 0 | 103.1 | 15.47 |  |  | 0.00325 |  |  |  | 0 |  | 1 | CAPACITY | AC2-112 |  |  | 1
932855 | AC2-112 E | 0.6 | 345 | 75 | 0 | 46.9 | 0 |  |  | 0.00325 |  |  |  | 0 |  | 1 | NEW | AC2-112 |  |  | 1
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00322 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00317 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.61 |  |  | 0.00307 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00307 |  |  |  | 0 |  | 1 | NEW | W4-102 |  |  | 1
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00307 |  |  |  | 0 |  | 1 | CAPACITY | W4-102 |  |  | 1
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00305 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
237024 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0.51 |  |  | 0.00305 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0.24 |  |  | 0.00305 |  |  |  | 0 |  | 1 | NEW | AA1-095 |  |  | 1
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 0.21 |  |  | 0.00305 |  |  |  | 0 |  | 1 | CAPACITY | AA1-095 |  |  | 1
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0.73 |  |  | 0.00305 |  |  |  | 0 |  | 1 | NEW | AB2-097 |  |  | 1
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0.46 |  |  | 0.00304 |  |  |  | 0 |  | 1 | NEW | AC2-136 |  |  | 1
237034 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 0.4 |  |  | 0.00304 |  |  |  | 0 |  | 1 | CAPACITY | AC2-136 |  |  | 1
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00302 |  |  |  | 0 |  | 1 | CAPACITY | AA1-092 |  |  | 1
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.00302 |  |  |  | 0 |  | 1 | NEW | AA1-092 |  |  | 1
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 1.46 |  |  | 0.00296 |  |  |  | 0 |  | 1 | NEW | AD1-085 |  |  | 1
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 0.9 |  |  | 0.00296 |  |  |  | 0 |  | 1 | CAPACITY | AD1-085 |  |  | 1
316054 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00295 |  |  |  | 0 |  | 1 | CAPACITY | AC2-074 |  |  | 1
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 10.07 |  |  | 0.00295 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0.79 |  |  | 0.00295 |  |  |  | 0 |  | 1 | NEW | AC2-074 |  |  | 1
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 0.72 |  |  | 0.00296 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.44 |  |  | 0.00296 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237037 | AE1-188 C | 34.5 | 201 | 75 | 0 | 20.5 | 1.5 |  |  | 0.00293 |  |  |  | 0 |  | 1 | CAPACITY | AE1-188 |  |  | 1
939592 | AE1-188 E | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00293 |  |  |  | 0 |  | 1 | NEW | AE1-188 |  |  | 1
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00294 |  |  |  | 0 |  | 1 | NEW | AD1-060 |  |  | 1
237080 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00294 |  |  |  | 0 |  | 1 | CAPACITY | AD1-060 |  |  | 1
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.0029 |  |  |  | 0 |  | 1 | NEW | AB1-127 |  |  | 1
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.0029 |  |  |  | 0 |  | 1 | NEW | AB1-128 |  |  | 1
235043 | AF1-166 C | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.0029 |  |  |  | 0 |  | 1 | CAPACITY | AF1-166 |  |  | 1
237002 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.0029 |  |  |  | 0 |  | 1 | CAPACITY | AB1-128 |  |  | 1
237001 | AB1-127 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.0029 |  |  |  | 0 |  | 1 | CAPACITY | AB1-127 |  |  | 1
945012 | AF1-166 E | 34.5 | 201 | 75 | 0 | 6.4 | 0.47 |  |  | 0.0029 |  |  |  | 0 |  | 1 | NEW | AF1-166 |  |  | 1
237038 | AE2-054 C | 34.5 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00289 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
940672 | AE2-054 E | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00289 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 2.01 |  |  | 0.00287 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 1.23 |  |  | 0.00287 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 93.64 |  |  | 0.00287 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00286 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00286 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208904 | HOLT 696 | 13.2 | 229 | 60 | 16 | 58.4 | 41.06 |  |  | 0.00287 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208903 | HOLT 695 | 13.2 | 229 | 60 | 19 | 53.2 | 37.4 |  |  | 0.00287 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 0.45 |  |  | 0.00287 |  |  |  | 0 |  | 1 | CAPACITY | V4-027 |  |  | 1
208254 | AF2-280 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00287 |  |  |  | 0 |  | 1 | NEW | AF2-280 |  |  | 1
208474 | KINZ 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00287 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208253 | AF2-280 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00287 |  |  |  | 0 |  | 1 | MTX | AF2-280 |  |  | 1
916007 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 0.1 | 0.06 |  |  | 0.00287 |  |  |  | 0 |  | 1 | NEW | V4-027 |  |  | 1
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00281 |  |  |  | 0 |  | 1 | CAPACITY | AE1-099 |  |  | 1
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00281 |  |  |  | 0 |  | 1 | CAPACITY | AE1-098 |  |  | 1
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00281 |  |  |  | 0 |  | 1 | NEW | AE1-098 |  |  | 1
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00281 |  |  |  | 0 |  | 1 | NEW | AE1-099 |  |  | 1
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 19.81 |  |  | 0.00279 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
208769 | SISO | 12.5 | 229 | 2 | 2.5 | 1.6 | 0 |  |  | 0.00272 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
208876 | WLAN | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00272 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 68.19 |  |  | 0.0027 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 45.34 |  |  | 0.0027 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 44.99 |  |  | 0.0027 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 80.49 |  |  | 0.0027 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 53.78 |  |  | 0.0027 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
209030 | FRFA O01 | 12.5 | 229 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00267 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208527 | AF2-279 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00267 |  |  |  | 0 |  | 1 | NEW | AF2-279 |  |  | 1
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 2 | 1.22 |  |  | 0.00267 |  |  |  | 0 |  | 1 | NEW | V3-051 |  |  | 1
208526 | AF2-279 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00267 |  |  |  | 0 |  | 1 | MTX | AF2-279 |  |  | 1
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 205.47 |  |  | 0.00261 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00261 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00261 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 103.81 |  |  | 0.00261 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00261 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00261 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00261 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA |  |  | 1
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1288.2 |  |  | 0.00261 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1307 |  |  | 0.0026 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 20.5 | 11.03 |  |  | 0.00259 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205922 | AF2-268 E | 115 | 227 | 75 | 0 | 2 | 0.19 |  |  | 0.00259 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
205916 | AD1-020_C | 0.6 | 227 | 75 | 0 | 54 | 4.99 |  |  | 0.00259 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
205917 | AD1-020 ES | 0.55 | 227 | 75 | 0 | 21.5 | 1.99 |  |  | 0.00259 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 247.42 |  |  | 0.00258 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00258 |  |  |  | 0.036 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00258 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200054 | ROCKSP 3 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00258 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200055 | ROCKSP 4 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00258 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200052 | ROCKSP 1 | 18 | 235 | 57 | 145.7 | 167.5 | 90.09 |  |  | 0.00258 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200053 | ROCKSP 2 | 18 | 235 | 57 | 144.9 | 166.5 | 89.56 |  |  | 0.00258 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00257 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00257 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00257 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00257 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.00257 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.00257 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 67.49 |  |  | 0.00257 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.00257 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.00257 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 33.74 |  |  | 0.00257 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 64 | 34.42 |  |  | 0.00256 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 0.00252 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 20.6 | 11.08 |  |  | 0.00251 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 171.69 |  |  | 0.0025 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.0025 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 89.82 |  |  | 0.0025 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.0025 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 33.02 |  |  | 0.00248 |  |  |  | 0 |  | 1 | CAPACITY | P.H. GLATFELTER_IPP |  |  | 1
233935 | AB2-179 C | 0.38 | 235 | 75 | 0 | 37.6 | 3.48 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | AB2-179 |  |  | 1
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 41.2 | 22.16 |  |  | 0.00247 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 40.5 | 21.78 |  |  | 0.00247 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | AB2-179 |  |  | 1
204555 | 27QUEEN ST | 115 | 227 | 75 | 0 | 5 | 0.46 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 2.83 |  |  | 0.00246 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 102.2 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 8.6 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AA1-102 |  |  | 1
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 111.97 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AB1-056 |  |  | 1
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 1.28 |  |  | 0.00247 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00247 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 5.27 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AA1-102 |  |  | 1
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 0.83 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232915 | OH NUG4 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 0.82 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 38.35 |  |  | 0.00247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
924802 | AB2-133 E | 69 | 235 | 75 | 0 | 31.2 | 2.89 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | AB2-133 |  |  | 1
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 30.66 |  |  | 0.00247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 29.58 |  |  | 0.00247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233906 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 39.32 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AB1-056 |  |  | 1
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 388.63 |  |  | 0.00246 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
233939 | AB2-133 C | 69 | 235 | 75 | 0 | 24.6 | 2.28 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | AB2-133 |  |  | 1
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 16.08 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233930 | AB2-032 GEN | 0.6 | 235 | 75 | 0 | 13.6 | 1.26 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | AB2-032 |  |  | 1
232905 | CHERITON_25 | 24.9 | 235 | 65 | 0 | 12.5 | 0.23 |  |  | 0.00246 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | AB1-141 |  |  | 1
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | AB1-142 |  |  | 1
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | W1-005 |  |  | 1
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | W1-006 |  |  | 1
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | W1-004 |  |  | 1
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | W1-003 |  |  | 1
923925 | AB2-153 E | 0.6 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | AB2-153 |  |  | 1
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | X3-008 |  |  | 1
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | W1-006 |  |  | 1
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | W1-004 |  |  | 1
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | W1-005 |  |  | 1
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | W1-003 |  |  | 1
917082 | Z2-012 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | Z2-012 |  |  | 1
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.00246 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | Y3-058 |  |  | 1
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 9.57 |  |  | 0.00247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 8.9 | 0.82 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | Y3-058 |  |  | 1
232920 | IR10 | 13.2 | 235 | 55 | 14 | 16.1 | 8.66 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233933 | AB2-153 GEN | 0.6 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | AB2-153 |  |  | 1
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | X3-008 |  |  | 1
233901 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | Z2-012 |  |  | 1
232919 | VN10 | 13.2 | 235 | 55 | 0 | 14.3 | 7.69 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923928 | AB2-032 E | 0.6 | 235 | 75 | 0 | 6.4 | 0.59 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | AB2-032 |  |  | 1
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | AB1-142 |  |  | 1
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | AB1-141 |  |  | 1
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | Y1-079 |  |  | 1
925262 | AB2-180 E | 0.38 | 235 | 75 | 0 | 6 | 0.56 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AB2-180 |  |  | 1
233942 | AB2-180 C | 0.38 | 235 | 75 | 0 | 14 | 8.72 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AB2-180 |  |  | 1
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AB1-137 |  |  | 1
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 6.23 |  |  | 0.00246 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0.37 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | X1-032 |  |  | 1
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | Z2-077 |  |  | 1
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | Z2-076 |  |  | 1
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 20.25 |  |  | 0.00247 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | Y1-079 |  |  | 1
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00247 |  |  |  | 0 |  | 1 | NEW | X3-066 |  |  | 1
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 3.08 | 0.28 |  |  | 0.00247 |  |  |  | 0 |  | 1 | CAPACITY | X3-066 |  |  | 1
960882 | AF2-379 E | 69 | 235 | 75 | 0 | 2.26 | 0.21 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AF2-379 |  |  | 1
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0.19 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | Y1-080 |  |  | 1
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | Z2-077 |  |  | 1
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | Z2-076 |  |  | 1
205920 | AF2-101 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AF2-101 |  |  | 1
205921 | AF2-151 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AF2-151 |  |  | 1
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AB1-137 |  |  | 1
233940 | AF2-379 C | 69 | 235 | 75 | 0 | 1.64 | 0.15 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AF2-379 |  |  | 1
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 0.12 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | Y1-080 |  |  | 1
958072 | AF2-101 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AF2-101 |  |  | 1
958602 | AF2-151 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AF2-151 |  |  | 1
233900 | O-025 C | 25 | 235 | 64 | 0 | 6 | 5.11 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.23 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.55 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.21 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.00246 |  |  |  | 0.036 |  | 1 | NEW | Garrison |  |  | 1
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 103.81 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 62.5 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 26.36 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 25.82 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232901 | NORTHST | 69 | 235 | 56 | 5 | 45 | 24.2 |  |  | 0.00246 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 12.37 |  |  | 0.00245 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 12.32 |  |  | 0.00245 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 9.25 |  |  | 0.00245 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205930 | AF2-099 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AF2-099 |  |  | 1
205931 | AF2-100 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY | AF2-100 |  |  | 1
958052 | AF2-099 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AF2-099 |  |  | 1
958062 | AF2-100 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00246 |  |  |  | 0 |  | 1 | NEW | AF2-100 |  |  | 1
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 14.34 |  |  | 0.00246 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 30 |  |  | 0.00245 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00245 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00245 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00245 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 164.17 |  |  | 0.00245 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 7.64 |  |  | 0.00245 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 81.14 |  |  | 0.00245 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 8.32 |  |  | 0.00243 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 99.67 |  |  | 0.00243 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
213893 | PHLISST1 | 20 | 230 | 58 | 232.3 | 267 | 143.61 |  |  | 0.00241 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00241 |  |  |  | 0.036 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00241 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00241 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.77 |  |  | 0.00242 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 13.36 |  |  | 0.0024 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1178.3 |  |  | 0.0024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.0024 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 20.98 |  |  | 0.00239 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0.77 |  |  | 0.0024 |  |  |  | 0 |  | 1 | NEW | W1-045 |  |  | 1
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.1 | 0.47 |  |  | 0.0024 |  |  |  | 0 |  | 1 | CAPACITY | W1-045 |  |  | 1
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 1138.9 |  |  | 0.0024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 1145.8 |  |  | 0.0024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00239 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00239 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 222.4 | 119.62 |  |  | 0.00239 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00239 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00239 |  |  |  | 0.036 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 18.29 |  |  | 0.00239 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.00239 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.00239 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.00239 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.00238 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 87.67 |  |  | 0.00237 |  |  |  | 0.036 |  | 1 | CAPACITY | GRAYS FERRY |  |  | 1
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | 0.00238 |  |  |  | 0.1097 |  | 1 | ENERGY |  |  |  | 1
208697 | PRIN B34 | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00238 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208885 | WNHO | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00238 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.00237 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00237 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00237 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 75 |  |  | 0.00237 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 181.64 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | 0.00235 |  |  |  | 0.036 |  | 1 | CAPACITY | Q90 |  |  | 1
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
228203 | P06 | 13.8 | 234 | 57 | 78 | 89.7 | 48.25 |  |  | 0.00236 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 45.99 |  |  | 0.00235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 45.13 |  |  | 0.00235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 34.26 |  |  | 0.00235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 57.7 | 31.03 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 57.6 | 30.98 |  |  | 0.00235 |  |  |  | 0.036 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 30.66 |  |  | 0.00235 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 29.85 |  |  | 0.00235 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.1 | 39.2 | 21.08 |  |  | 0.00235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 20.22 |  |  | 0.00235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 226.44 |  |  | 0.00236 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 206.63 |  |  | 0.00235 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228357 | V2-046E | 12.9 | 234 | 75 | 0 | 12.9 | 1.19 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | V2-046 |  |  | 1
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.1 | 12.43 |  |  | 0.00235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228471 | VALERO1 | 13.8 | 234 | 58 | 19.1 | 22 | 11.83 |  |  | 0.00235 |  |  |  | 0.036 |  | 1 | CAPACITY | Valero |  |  | 1
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 0.72 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | V2-046 |  |  | 1
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | V4-054 |  |  | 1
228472 | VALERO2 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228484 | VALERO4 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228473 | VALERO3 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | V4-054 |  |  | 1
228712 | V2-041E | 13.2 | 234 | 75 | 0 | 2.48 | 0.23 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | V2-041 |  |  | 1
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.00235 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | V2-041 |  |  | 1
228721 | V2-035E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | V2-035 |  |  | 1
230410 | AE1-218 E O1 | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | AE1-218 |  |  | 1
230409 | AE1-218 C O1 | 12.9 | 234 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | AE1-218 |  |  | 1
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | V2-035 |  |  | 1
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 3 | 2.55 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.7 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 0.00234 |  |  |  | 0.036 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 43.08 |  |  | 0.00234 |  |  |  | 0.036 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
227801 | ONTC&DCT | 13.8 | 234 | 75 | 33.6 | 38.6 | 3.57 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 35.07 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 22.59 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.00235 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 16.14 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00235 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 16.18 |  |  | 0.00234 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | 0.00234 |  |  |  | 0.30476 |  | 1 | ENERGY |  |  |  | 1
924052 | AB2-049 E | 69 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | AB2-049 |  |  | 1
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | 0.00234 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0.56 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | W2-030 |  |  | 1
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0.53 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | W1-130 |  |  | 1
214030 | WAYNEJCT | 13.8 | 230 | 29 | 0 | 8.8 | 4.73 |  |  | 0.00234 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.2 | 7.55 |  |  | 0.00234 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 0.34 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | W2-030 |  |  | 1
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | W1-130 |  |  | 1
219765 | PARADISE E | 13 | 231 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | U4-036 |  |  | 1
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | Y2-081 |  |  | 1
230408 | AD2-065 E | 12.9 | 234 | 75 | 0 | 3.03 | 0.28 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | AD2-065 |  |  | 1
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0.28 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | X3-075 |  |  | 1
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | Y2-081 |  |  | 1
230414 | AF1-041 E | 69 | 234 | 75 | 0 | 2.4 | 0.22 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | AF1-041 |  |  | 1
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0.22 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | Y3-087 |  |  | 1
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 0.21 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | Y3-087 |  |  | 1
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | 0.00234 |  |  |  | 0 |  | 1 | MTX | X2-013 |  |  | 1
219904 | AC1-010 C | 26.4 | 231 | 75 | 0 | 2.2 | 0.2 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | U4-036 |  |  | 1
227928 | V4-067E | 12.9 | 234 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | V4-067 |  |  | 1
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0.13 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | AB1-001 |  |  | 1
219921 | AF1-264 | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | X3-075 |  |  | 1
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | AB2-122 |  |  | 1
230415 | AB2-049 C | 69 | 234 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | AB2-049 |  |  | 1
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | 0.00234 |  |  |  | 0 |  | 1 | MTX | Z1-082 |  |  | 1
230407 | AD2-065_C | 12.9 | 234 | 75 | 0 | 1.08 | 0.1 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | AD2-065 |  |  | 1
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.09 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | V4-067 |  |  | 1
219138 | THOSOLAR E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | 0.00235 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.08 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | AB1-001 |  |  | 1
230403 | AB1-116 E | 12.9 | 234 | 28 | 0 | 0.78 | 0 |  |  | 0.00235 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228733 | AB1-119 E | 12.9 | 234 | 28 | 0 | 0.73 | 0 |  |  | 0.00235 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
230413 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.06 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | AB2-122 |  |  | 1
228014 | PVILLEG | 0.48 | 234 | 65 | 0 | 1.3 | 0.77 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219137 | THOSOLAR C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 28 |  |  | 0.00235 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 1122.1 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00234 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00234 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00234 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219913 | AD2-042 E | 26.4 | 231 | 75 | 0 | 8.2 | 0.76 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | AD2-042 |  |  | 1
219915 | AD2-027 E | 26.4 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW | AD2-027 |  |  | 1
219912 | AD2-042 C | 26.4 | 231 | 75 | 0 | 5 | 0.46 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | AD2-042 |  |  | 1
219914 | AD2-027 C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY | AD2-027 |  |  | 1
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0.16 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | W2-071 |  |  | 1
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.55 | 0.14 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | AC1-030 |  |  | 1
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.1 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | W2-071 |  |  | 1
219907 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | AC1-030 |  |  | 1
930243 | AB1-063_E | 69 | 231 | 0 | 0 | 0 | -0.7 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.65 | 3.95 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | Y1-075 |  |  | 1
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0.05 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | X1-071 |  |  | 1
219917 | AB1-063 E | 69 | 231 | 75 | 0 | 0.4 | 0.04 |  |  | 0.00234 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | Y1-075 |  |  | 1
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.03 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | X1-071 |  |  | 1
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.43 |  |  | 0.00234 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 1119.7 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 345.42 |  |  | 0.00232 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris2 |  |  | 1
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 291.92 |  |  | 0.00232 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris1 |  |  | 1
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0.63 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | W2-056 |  |  | 1
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 0.39 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | W2-056 |  |  | 1
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0.21 |  |  | 0.00232 |  |  |  | 0 |  | 1 | NEW | AC1-017 |  |  | 1
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0.2 |  |  | 0.00232 |  |  |  | 0 |  | 1 | NEW | X1-070 |  |  | 1
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | AB1-025 S |  |  | 1
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | AB1-025 N |  |  | 1
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00233 |  |  |  | 0 |  | 1 | NEW | V4-005 |  |  | 1
219906 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | AC1-017 |  |  | 1
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 S |  |  | 1
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 N |  |  | 1
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | X1-070 |  |  | 1
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00233 |  |  |  | 0 |  | 1 | CAPACITY | V4-005 |  |  | 1
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 749 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 256.8 | 138.13 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 137.8 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00232 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00232 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00231 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 25.82 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00232 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213798 | MERCK 3 | 13.8 | 230 | 29 | 13 | 42 | 22.59 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
213797 | MERCK 2 | 13.8 | 230 | 29 | 4 | 32 | 17.21 |  |  | 0.00232 |  |  |  | 0.1042 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00232 |  |  |  | 0 |  | 1 | NEW | W3-080 |  |  | 1
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 0.00232 |  |  |  | 0 |  | 1 | NEW | W4-103 |  |  | 1
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 0.00232 |  |  |  | 0 |  | 1 | NEW | W2-102 |  |  | 1
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | 0.00231 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00232 |  |  |  | 0 |  | 1 | NEW | Y3-026 |  |  | 1
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | Y3-026 |  |  | 1
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 0.34 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | W3-080 |  |  | 1
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 3.56 | 0.33 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | W4-103 |  |  | 1
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY | W2-102 |  |  | 1
208580 | MGTN 2 | 12.5 | 229 | 77 | 0 | 4.8 | 2.98 |  |  | 0.00231 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 2.75 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00231 |  |  |  | 0 |  | 1 | CAPACITY | T20 |  |  | 1
219685 | NATIONAL_GYP | 26 | 231 | 77 | 0 | 2.8 | 1.89 |  |  | 0.00232 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
916010 | T20SOLAR E | 0.5 | 230 | 75 | 0 | 2 | 1.22 |  |  | 0.00231 |  |  |  | 0 |  | 1 | NEW | T20 |  |  | 1
219922 | AF1-261 | 26.4 | 231 | 75 | 0 | 0.9 | 0.61 |  |  | 0.00232 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W2-082 |  |  | 1
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W4-025 |  |  | 1
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W2-019 |  |  | 1
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W1-129 |  |  | 1
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W2-082 |  |  | 1
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | X4-015 |  |  | 1
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 0.24 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W4-025 |  |  | 1
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 0.21 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W2-019 |  |  | 1
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W1-129 |  |  | 1
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | X4-015 |  |  | 1
207179 | 28SIXFLAGS | 34.5 | 228 | 77 | 0 | 17 | 0 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 18.29 |  |  | 0.00229 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 16.67 |  |  | 0.00229 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0.75 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | Z2-102 |  |  | 1
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W1-120 |  |  | 1
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W1-119 |  |  | 1
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 0.46 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | Z2-102 |  |  | 1
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W1-119 |  |  | 1
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W1-120 |  |  | 1
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00228 |  |  |  | 0 |  | 1 | NEW | X1-085 |  |  | 1
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0.23 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W1-121 Z |  |  | 1
219728 | YARDVSOLFA E | 13.2 | 231 | 75 | 0 | 2.42 | 0.22 |  |  | 0.00228 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | 0.00229 |  |  |  | 0 |  | 1 | MTX | AA1-060 |  |  | 1
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00228 |  |  |  | 0 |  | 1 | CAPACITY | X1-085 |  |  | 1
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Z |  |  | 1
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00229 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Y |  |  | 1
219727 | YARDVSOLFA C | 13.2 | 231 | 75 | 0 | 1.48 | 0.14 |  |  | 0.00228 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00229 |  |  |  | 0 |  | 1 | NEW | W1-121 Y |  |  | 1
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 260.87 |  |  | 0.00228 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | 0.00227 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | 0.00227 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 76.9 | 88.4 | 47.55 |  |  | 0.00227 |  |  |  | 0.036 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
939122 | AE1-142 E O1 | 34.5 | 228 | 75 | 0 | 11.8 | 1.09 |  |  | 0.00228 |  |  |  | 0 |  | 1 | NEW | AE1-142 |  |  | 1
218780 | PRINCENTON_U | 26 | 231 | 77 | 0 | 31.56 | 21.27 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
207459 | AE1-142 C O1 | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | 0.00228 |  |  |  | 0 |  | 1 | CAPACITY | AE1-142 |  |  | 1
923293 | AB1-138 E | 0.36 | 228 | 75 | 0 | 6 | 0.56 |  |  | 0.00228 |  |  |  | 0 |  | 1 | NEW | AB1-138 |  |  | 1
207450 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | 0.00228 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0.45 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW | Z1-096 |  |  | 1
206280 | 28LAKEHURS | 34.5 | 228 | 55 | 0 | 13.7 | 10.22 |  |  | 0.00228 |  |  |  | 0.17131 |  | 1 | CAPACITY |  |  |  | 1
207445 | AB1-138 C | 0.38 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00228 |  |  |  | 0 |  | 1 | CAPACITY | AB1-138 |  |  | 1
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 0.28 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | Z1-096 |  |  | 1
219622 | TRENT_BIOGAS | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 30 |  |  | 0.00228 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 43.9 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204664 | 27AES GEN3 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204663 | 27AES GEN2 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204662 | 27AES GEN1 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00226 |  |  |  | 0.036 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 32.1 | 17.27 |  |  | 0.00227 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
207451 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | 0.00227 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW | W3-079 |  |  | 1
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | W3-079 |  |  | 1
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW | Y2-051 |  |  | 1
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 3.23 |  |  | 0.00226 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | Y2-051 |  |  | 1
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | W1-032 |  |  | 1
219650 | TRENT_COLLEG | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | 0.00226 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | W1-032 |  |  | 1
219818 | TRENTONSOL E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 5 | 4.26 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0.06 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
219817 | TRENTONSOL C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
932032 | AC2-009 E | 69 | 231 | 75 | -0.5 | 0.49 | 0.05 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | AC2-009 |  |  | 1
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0.04 |  |  | 0.00227 |  |  |  | 0 |  | 1 | NEW | W4-058 |  |  | 1
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.7 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | AA2-058 |  |  | 1
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | 0.00227 |  |  |  | 0 |  | 1 | CAPACITY | W4-058 |  |  | 1
219918 | AC2-009 C | 69 | 231 | 75 | -0.1 | 0.1 | 0.01 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | AC2-009 |  |  | 1
207454 | AA2-184 E | 34.5 | 228 | 75 | 0 | 11.6 | 1.07 |  |  | 0.00225 |  |  |  | 0 |  | 1 | NEW | BenMoreell |  |  | 1
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0.98 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | X1-037 |  |  | 1
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00225 |  |  |  | 0 |  | 1 | NEW | W1-124 |  |  | 1
207464 | AF1-023 | 34.5 | 228 | 75 | 0 | 8.4 | 0.78 |  |  | 0.00225 |  |  |  | 0 |  | 1 | CAPACITY | BenMoreell |  |  | 1
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | AC1-207 |  |  | 1
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0.52 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | W2-078 |  |  | 1
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | W1-113 |  |  | 1
207420 | AC1-207 TAP | 34.5 | 228 | 75 | 0 | 4.9 | 0.45 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | AC1-207 |  |  | 1
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | X1-037 |  |  | 1
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0.36 |  |  | 0.00225 |  |  |  | 0 |  | 1 | NEW | V2-009 3 |  |  | 1
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00225 |  |  |  | 0 |  | 1 | CAPACITY | W1-124 |  |  | 1
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | W2-078 |  |  | 1
205925 | AF2-428 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00225 |  |  |  | 0 |  | 1 | NEW | AF2-428 |  |  | 1
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 0.26 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | W1-113 |  |  | 1
901032 | W1-024E OP1 | 34.5 | 228 | 75 | 0 | 2.5 | 0.23 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | W1-024 |  |  | 1
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 0.22 |  |  | 0.00225 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 3 |  |  | 1
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0.22 |  |  | 0.00225 |  |  |  | 0 |  | 1 | NEW | V2-009 4 |  |  | 1
219679 | NRGCENTER E | 13.2 | 231 | 55 | 0 | 2 | 0 |  |  | 0.00225 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | X4-031 |  |  | 1
940922 | AE2-081 E | 34.5 | 228 | 75 | 0 | 1.75 | 0.16 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | AE2-081 |  |  | 1
207460 | AE2-056 C | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | AE2-056 |  |  | 1
207463 | AE2-081 C | 34.5 | 228 | 75 | 0 | 1.57 | 0.14 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | AE2-081 |  |  | 1
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | W1-024 |  |  | 1
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | 0.00225 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 4 |  |  | 1
940692 | AE2-056 E | 34.5 | 228 | 75 | 0 | 1.4 | 0.13 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | AE2-056 |  |  | 1
940702 | AE2-057 E | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | 0.00226 |  |  |  | 0 |  | 1 | NEW | AE2-057 |  |  | 1
207461 | AE2-057 C | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | 0.00226 |  |  |  | 0 |  | 1 | CAPACITY | AE2-057 |  |  | 1
207419 | AB2-139 E | 34.5 | 228 | 76 | -0.2 | 0.21 | 0 |  |  | 0.00226 |  |  |  | 0 |  | 1 | MTX | AB2-139 |  |  | 1
961373 | AF2-428 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00225 |  |  |  | 0 |  | 1 | MTX | AF2-428 |  |  | 1
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | W4-060 |  |  | 1
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 75.48 |  |  | 0.00224 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
205926 | AF2-429 E | 34.5 | 227 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | AF2-429 |  |  | 1
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00224 |  |  |  | 0 |  | 1 | CAPACITY | W4-060 |  |  | 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | V3-024 |  |  | 1
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0.28 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | V2-009 2 |  |  | 1
205923 | AF2-272 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | AF2-272 |  |  | 1
210323 | AF2-286 E | 13.8 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | AF2-286 |  |  | 1
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0.23 |  |  | 0.00225 |  |  |  | 0 |  | 1 | NEW | W1-112 |  |  | 1
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00224 |  |  |  | 0 |  | 1 | CAPACITY | V3-024 |  |  | 1
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 0.17 |  |  | 0.00224 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 2 |  |  | 1
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0.16 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | W3-124 |  |  | 1
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0.14 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | V2-009 1 |  |  | 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | X2-088 |  |  | 1
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.17 | 0.11 |  |  | 0.00225 |  |  |  | 0 |  | 1 | CAPACITY | W1-112 |  |  | 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.1 |  |  | 0.00224 |  |  |  | 0 |  | 1 | CAPACITY | W3-124 |  |  | 1
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | 0.00224 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 1 |  |  | 1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 0.00224 |  |  |  | 0 |  | 1 | CAPACITY | X2-088 |  |  | 1
208348 | EELI | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
959813 | AF2-272 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00224 |  |  |  | 0 |  | 1 | MTX | AF2-272 |  |  | 1
210322 | AF2-286 BAT | 13.8 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00224 |  |  |  | 0 |  | 1 | MTX | AF2-286 |  |  | 1
961383 | AF2-429 BAT | 34.5 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00224 |  |  |  | 0 |  | 1 | MTX | AF2-429 |  |  | 1
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 133.39 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 102.41 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 102.41 |  |  | 0.00223 |  |  |  | 0.036 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 94.67 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | 0.00223 |  |  |  | 0.036 |  | 1 | CAPACITY | RED OAK |  |  | 1
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 93.75 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206327 | 28S RIV G1 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | 0.00223 |  |  |  | 0.036 |  | 1 | CAPACITY | S RIV |  |  | 1
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 85.3 | 98 | 52.71 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 29.23 |  |  | 0.00223 |  |  |  | 0.036 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 29.23 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
924132 | AB2-057 E | 26 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00223 |  |  |  | 0 |  | 1 | NEW | AB2-057 |  |  | 1
219903 | AB2-057 C | 26 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | AB2-057 |  |  | 1
205927 | AF2-430 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | AF2-430 |  |  | 1
205924 | AF2-281 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00224 |  |  |  | 0 |  | 1 | NEW | AF2-281 |  |  | 1
217199 | V3-059 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | 0.00223 |  |  |  | 0 |  | 1 | NEW | V3-059 |  |  | 1
217198 | V3-058 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | 0.00223 |  |  |  | 0 |  | 1 | NEW | V3-058 |  |  | 1
218455 | CINNBAY_CGEN | 26.4 | 231 | 64 | 0 | 9 | 7.66 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
205928 | AF2-431 E | 69 | 227 | 75 | 0 | 1.17 | 0.11 |  |  | 0.00223 |  |  |  | 0 |  | 1 | NEW | AF2-431 |  |  | 1
218781 | BRIS_MYERS | 26 | 231 | 77 | 0 | 3 | 2.02 |  |  | 0.00223 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
961393 | AF2-430 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00224 |  |  |  | 0 |  | 1 | MTX | AF2-430 |  |  | 1
959903 | AF2-281 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00224 |  |  |  | 0 |  | 1 | MTX | AF2-281 |  |  | 1
961403 | AF2-431 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00223 |  |  |  | 0 |  | 1 | MTX | AF2-431 |  |  | 1
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 164.59 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | 0.00223 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | 0.00223 |  |  |  | 0.036 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 99.6 | 114.5 | 61.59 |  |  | 0.00223 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 93.2 | 107.1 | 57.61 |  |  | 0.00223 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00223 |  |  |  | 0 |  | 1 | NEW | W2-050 |  |  | 1
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0.46 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | V3-070 |  |  | 1
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | V3-070 |  |  | 1
219916 | AD2-025 E | 13.2 | 231 | 76 | -2 | 2 | 0 |  |  | 0.00222 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
936193 | AD2-025_E | 13.2 | 231 | 76 | 0 | 2 | 0 |  |  | 0.00222 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
218527 | CNTRALGAS2 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218525 | CNTRALGAS1 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0.12 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | X2-089 |  |  | 1
218526 | CNTRALGAS2 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
218524 | CNTRALGAS1 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
210022 | LING 2 | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00223 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | X2-089 |  |  | 1
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 0 |  |  | 0.00222 |  |  |  | 0.0692 |  | 1 | NEW |  |  |  | 1
219001 | SEWAREN7GT | 25 | 231 | 58 | 0 | 324.6 | 174.59 |  |  | 0.00221 |  |  |  | 0.036 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
219002 | SEWAREN7ST | 18 | 231 | 58 | 0 | 216.4 | 116.4 |  |  | 0.00221 |  |  |  | 0 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
208942 | HARR CT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00222 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | 0.00221 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | 0.00221 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | W3-029 |  |  | 1
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0.93 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | W3-003 |  |  | 1
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 7.45 |  |  | 0.00222 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0.38 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0.38 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | AB1-139 |  |  | 1
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00221 |  |  |  | 0 |  | 1 | NEW | X2-075 |  |  | 1
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | W3-029 |  |  | 1
219908 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 0.23 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | AB1-139 |  |  | 1
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 0.21 |  |  | 0.00221 |  |  |  | 0 |  | 1 | CAPACITY | X2-075 |  |  | 1
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | W1-132 |  |  | 1
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | W2-061 |  |  | 1
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | V4-069 |  |  | 1
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | V4-070 |  |  | 1
217212 | AMBOY SO E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | V3-069 |  |  | 1
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | V4-070 |  |  | 1
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | V4-069 |  |  | 1
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | W2-061 |  |  | 1
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | AE1-041 |  |  | 1
217213 | AMBOY SO C | 13.2 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | V3-069 |  |  | 1
219920 | AE1-041 EBAT | 26.4 | 231 | 76 | -0.5 | 0.5 | 0 |  |  | 0.00222 |  |  |  | 0 |  | 1 | MTX | AE1-041 |  |  | 1
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0.04 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | W2-036 |  |  | 1
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0.03 |  |  | 0.00222 |  |  |  | 0 |  | 1 | NEW | W2-052 |  |  | 1
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | W2-036 |  |  | 1
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | W2-052 |  |  | 1
219919 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY | AE1-041 |  |  | 1
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 10.2 |  |  | 0.00222 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 302.3 | 162.6 |  |  | 0.0022 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 302.1 | 162.49 |  |  | 0.00221 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
990902 | TOSCO_E | 18 | 231 | 2 | 0 | 137.5 | 0 |  |  | 0.00221 |  |  |  | 0.1042 |  | 1 | ENERGY | Tosco |  |  | 1
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | 0.00221 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | 0.00221 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | 0.00221 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | 0.00221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | 0.00221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 45.24 |  |  | 0.0022 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 72.1 | 82.9 | 44.59 |  |  | 0.0022 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208947 | WSHO CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218344 | TOSCO_G6 | 18 | 231 | 2 | 37 | 42.5 | 22.86 |  |  | 0.00221 |  |  |  | 0.1042 |  | 1 | CAPACITY | Tosco |  |  | 1
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 25.21 |  |  | 0.0022 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW | W2-016 |  |  | 1
218672 | KENILWRTH E | 26.4 | 231 | 65 | 0 | 8 | 0 |  |  | 0.0022 |  |  |  | 0.1097 |  | 1 | NEW |  |  |  | 1
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 3.55 |  |  | 0.0022 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | W2-016 |  |  | 1
218450 | LINSOLAR E | 26.4 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0.11 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW | W2-080 |  |  | 1
218449 | LINSOLAR C | 26.4 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | W2-080 |  |  | 1
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 139.31 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 135.65 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 0.00219 |  |  |  | 0.036 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 113.38 |  |  | 0.0022 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 96.22 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 96.22 |  |  | 0.00219 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 50.99 |  |  | 0.00219 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 0.00219 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 0.00219 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 0.00219 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 0.00219 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 43.57 |  |  | 0.00219 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 0.00219 |  |  |  | 0.036 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 18.4 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217831 | PB_NUTCLIF | 26 | 231 | 77 | 0 | 10.7 | 7.21 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217850 | MONTCLAIR_U | 26 | 231 | 77 | 0 | 10.6 | 7.15 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217825 | UMD_NJ | 26 | 231 | 77 | 0 | 10.5 | 7.08 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW | V2-025 |  |  | 1
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.15 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217194 | REDH C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | V2-025 |  |  | 1
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0.15 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW | W4-059 |  |  | 1
219910 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0.14 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.24 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW | W1-101 |  |  | 1
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0.06 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW | X2-087 |  |  | 1
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW | X1-072 |  |  | 1
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.05 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | W1-101 |  |  | 1
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0.05 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW | V3-067 |  |  | 1
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | X2-087 |  |  | 1
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | X1-072 |  |  | 1
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0.03 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW | V3-065 |  |  | 1
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.03 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | V3-067 |  |  | 1
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW | V3-066 |  |  | 1
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0.03 |  |  | 0.0022 |  |  |  | 0 |  | 1 | NEW | V3-068 |  |  | 1
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.02 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | W4-059 |  |  | 1
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.02 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | V3-065 |  |  | 1
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY | V3-068 |  |  | 1
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | V3-066 |  |  | 1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 0.0022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
207458 | AD2-210_C | 34.5 | 228 | 76 | 0 | 8 | 0 |  |  | 0.00218 |  |  |  | 0.05 |  | 1 | NEW |  |  |  | 1
211089 | AF2-277 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW | AF2-277 |  |  | 1
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00218 |  |  |  | 0 |  | 1 | NEW | X1-095 |  |  | 1
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00218 |  |  |  | 0 |  | 1 | CAPACITY | X1-095 |  |  | 1
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0.06 |  |  | 0.00219 |  |  |  | 0 |  | 1 | NEW | AB1-021 |  |  | 1
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.00219 |  |  |  | 0 |  | 1 | CAPACITY | AB1-021 |  |  | 1
211088 | AF2-277 BAT | 69 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00219 |  |  |  | 0 |  | 1 | MTX | AF2-277 |  |  | 1
207466 | AF1-324 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00218 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00217 |  |  |  | 0 |  | 1 | NEW | V4-001 |  |  | 1
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00217 |  |  |  | 0 |  | 1 | CAPACITY | V4-001 |  |  | 1
207456 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | 0.00217 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200048 | BETH CT5 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200044 | BETH CT1 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00216 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH1234 |  |  | 1
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 153 | 82.29 |  |  | 0.00216 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 91.3 | 105 | 56.48 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 89.6 | 103 | 55.4 |  |  | 0.00216 |  |  |  | 0.036 |  | 1 | CAPACITY | GILBERT |  |  | 1
206341 | 28GIL 8 | 13.8 | 228 | 58 | 82.2 | 94.5 | 50.83 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | W3-044 |  |  | 1
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | 0.00215 |  |  |  | 0.0975 |  | 1 | MTX | AA2-061 |  |  | 1
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | W3-044 |  |  | 1
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | 0.00215 |  |  |  | 0.0975 |  | 1 | MTX | AA2-060 |  |  | 1
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | W4-046 |  |  | 1
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0.57 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | BeaverRun |  |  | 1
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0.43 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | W3-110 |  |  | 1
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0.4 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | AD2-070 |  |  | 1
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BeaverRun |  |  | 1
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | AD2-070 |  |  | 1
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 0.26 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | W3-110 |  |  | 1
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 0.22 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | W4-046 |  |  | 1
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | W4-097 |  |  | 1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00216 |  |  |  | 0 |  | 1 | NEW | AC2-175 |  |  | 1
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0.12 |  |  | 0.00216 |  |  |  | 0 |  | 1 | NEW | AE1-081 |  |  | 1
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | W4-097 |  |  | 1
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.09 |  |  | 0.00216 |  |  |  | 0 |  | 1 | CAPACITY | AE1-081 |  |  | 1
207470 | AF1-327 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00215 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207468 | AF1-326 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00215 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207403 | 28AA2-082 E | 34.5 | 228 | 76 | -18 | 18 | 0 |  |  | 0.00215 |  |  |  | 0.05 |  | 1 | MTX | AA2-082 |  |  | 1
206747 | 28DSM_X3-029 | 34.5 | 228 | 58 | 0 | 11.15 | 0 |  |  | 0.00215 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
207462 | AF1-133 C | 34.5 | 228 | 75 | 0 | 12 | 1.11 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | AF1-133 |  |  | 1
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00214 |  |  |  | 0 |  | 1 | NEW | W4-073 |  |  | 1
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | W3-077 |  |  | 1
944682 | AF1-133 E | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | AF1-133 |  |  | 1
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | X1-012 |  |  | 1
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | 0.00215 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | X1-012 |  |  | 1
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | W2-091 |  |  | 1
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | W3-077 |  |  | 1
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 3.04 | 0.28 |  |  | 0.00214 |  |  |  | 0 |  | 1 | CAPACITY | W4-073 |  |  | 1
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00214 |  |  |  | 0 |  | 1 | NEW | W4-064 |  |  | 1
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00214 |  |  |  | 0 |  | 1 | NEW | W1-127 |  |  | 1
916006 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 4.4 | 2.69 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | W2-091 |  |  | 1
916005 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 3.45 | 2.11 |  |  | 0.00215 |  |  |  | 0 |  | 1 | NEW | Y2-018 |  |  | 1
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0.12 |  |  | 0.00214 |  |  |  | 0 |  | 1 | NEW | U2-059 |  |  | 1
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00214 |  |  |  | 0 |  | 1 | CAPACITY | W1-127 |  |  | 1
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00214 |  |  |  | 0 |  | 1 | CAPACITY | W4-064 |  |  | 1
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 81.18 |  |  | 0.00214 |  |  |  | 0 |  | 1 | NEW | T157 |  |  | 1
207402 | 28AA2-082 C | 34.5 | 228 | 76 | 0 | 2 | 1.19 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | AA2-082 |  |  | 1
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00214 |  |  |  | 0 |  | 1 | CAPACITY | U2-059 |  |  | 1
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.47 |  |  | 0.00214 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 0.35 | 0.03 |  |  | 0.00215 |  |  |  | 0 |  | 1 | CAPACITY | Y2-018 |  |  | 1
207455 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | 0.00215 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 20.3 |  |  | 0.00214 |  |  |  | 0 |  | 1 | CAPACITY | T157 |  |  | 1
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.00214 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH5678 |  |  | 1
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 3.8 | 2.04 |  |  | 0.00213 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 140.5 | 75.57 |  |  | 0.00212 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204651 | 27PORT CT | 13.8 | 227 | 55 | 4 | 37 | 19.9 |  |  | 0.00213 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00212 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00212 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 128.98 |  |  | 0.00212 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 107.57 |  |  | 0.00212 |  |  |  | 0.036 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 107.57 |  |  | 0.00212 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00211 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00211 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00211 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
208946 | MACR CT | 12.5 | 229 | 55 | 61.4 | 70.6 | 37.97 |  |  | 0.00211 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 21 | 11.3 |  |  | 0.00209 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 108.79 |  |  | 0.00208 |  |  |  | 0 |  | 1 | NEW | K11 |  |  | 1
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 18.41 |  |  | 0.00208 |  |  |  | 0 |  | 1 | CAPACITY | K11 |  |  | 1
209945 | AF2-278 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00208 |  |  |  | 0 |  | 1 | NEW | AF2-278 |  |  | 1
209944 | AF2-278 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00208 |  |  |  | 0 |  | 1 | MTX | AF2-278 |  |  | 1
208940 | ALLE CT | 12.5 | 229 | 55 | 48.7 | 56 | 30.12 |  |  | 0.00208 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209007 | NOEN IPP | 13.8 | 229 | 12 | 96.9 | 111.4 | 105.11 |  |  | 0.00207 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
935072 | AD1-143 E1 | 69 | 229 | 74 | 0 | 34.28 | 20.93 |  |  | 0.00207 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
211065 | PASP 1_2 C | 13.8 | 229 | 75 | 0 | 8 | 0.74 |  |  | 0.00207 |  |  |  | 0 |  | 1 | CAPACITY | AC1-087 |  |  | 1
942581 | PASP 2 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.00207 |  |  |  | 0 |  | 1 | NEW | AC1-087 |  |  | 1
926082 | PASP 1 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.00207 |  |  |  | 0 |  | 1 | NEW | U4-014 |  |  | 1
935071 | AD1-143 C1 | 69 | 229 | 75 | 0 | 5.72 | 0.53 |  |  | 0.00207 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
935082 | AD1-143 E2 | 69 | 229 | 75 | 0 | 4.8 | 0.44 |  |  | 0.00207 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
935081 | AD1-143 C2 | 69 | 229 | 75 | 0 | 0.2 | 0.02 |  |  | 0.00207 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 52.08 |  |  | 0.00203 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 7.75 |  |  | 0.00203 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
210319 | WCAR 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00204 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 0.36 |  |  | 0.00199 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 522.9 |  |  | 0.00199 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 553 |  |  | 0.00199 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM2 |  |  | 1
208920 | WLPK | 12.5 | 229 | 60 | 35.5 | 40.8 | 28.68 |  |  | 0.00199 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 548.2 |  |  | 0.00198 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM1 |  |  | 1
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 32 |  |  | 0.00196 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 31.63 |  |  | 0.00196 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
211375 | BEAC | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00196 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 15.92 |  |  | 0.00196 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
211591 | HARW | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00196 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00194 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00194 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1251.7 |  |  | 0.00194 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916009 | LOR2_Q27 E | 0.7 | 229 | 74 | 0 | 88.8 | 54.21 |  |  | 0.00193 |  |  |  | 0 |  | 1 | NEW | Q27 |  |  | 1
208941 | FISH CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00193 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916008 | LOR1 E | 0.7 | 229 | 74 | 0 | 23.8 | 14.53 |  |  | 0.00193 |  |  |  | 0 |  | 1 | NEW | N14 |  |  | 1
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 81.14 |  |  | 0.00193 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 77.37 |  |  | 0.00193 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.2 | 6.84 |  |  | 0.00193 |  |  |  | 0 |  | 1 | CAPACITY | Q27 |  |  | 1
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.14 |  |  | 0.00193 |  |  |  | 0 |  | 1 | CAPACITY | N14 |  |  | 1
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1253.3 |  |  | 0.00192 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 4.3 |  |  | 0.00191 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
211938 | AF2-285 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00192 |  |  |  | 0 |  | 1 | NEW | AF2-285 |  |  | 1
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 40.29 |  |  | 0.00191 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 30.66 |  |  | 0.00191 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 5.19 |  |  | 0.00191 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
211937 | AF2-285 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00192 |  |  |  | 0 |  | 1 | MTX | AF2-285 |  |  | 1
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.00189 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.00189 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
921653 | AA2-008 E | 230 | 229 | 58 | 0 | 57 | 0 |  |  | 0.00189 |  |  |  | 0.036 |  | 1 | ENERGY | MOXIE PATRIOT |  |  | 1
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 26.19 |  |  | 0.00189 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 26.03 |  |  | 0.00189 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 23.83 |  |  | 0.00189 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00189 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 15.71 |  |  | 0.00189 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
208944 | JENK CT | 12.5 | 229 | 55 | 24 | 27.6 | 14.85 |  |  | 0.00189 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208948 | WILL CT | 12.5 | 229 | 55 | 23.1 | 26.6 | 14.31 |  |  | 0.00189 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
946263 | BECR K09 E | 0.69 | 229 | 74 | 0 | 20.7 | 12.64 |  |  | 0.00189 |  |  |  | 0 |  | 1 | NEW | L18 |  |  | 1
212464 | AF2-289 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00189 |  |  |  | 0 |  | 1 | NEW | AF2-289 |  |  | 1
212451 | AF2-427 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00189 |  |  |  | 0 |  | 1 | NEW | AF2-427 |  |  | 1
212495 | AF2-284 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00189 |  |  |  | 0 |  | 1 | NEW | AF2-284 |  |  | 1
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.02 |  |  | 0.00189 |  |  |  | 0 |  | 1 | CAPACITY | L18 |  |  | 1
212005 | ALWD | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00189 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212461 | AF2-289 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00189 |  |  |  | 0 |  | 1 | MTX | AF2-289 |  |  | 1
212450 | AF2-427 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00189 |  |  |  | 0 |  | 1 | MTX | AF2-427 |  |  | 1
212494 | AF2-284 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00189 |  |  |  | 0 |  | 1 | MTX | AF2-284 |  |  | 1
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 758.5 |  |  | 0.0019 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 757.9 |  |  | 0.0019 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 0.26 |  |  | 0.00189 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212455 | AF2-290 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00188 |  |  |  | 0 |  | 1 | NEW | AF2-290 |  |  | 1
212435 | SMIL | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00188 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212454 | AF2-290 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00188 |  |  |  | 0 |  | 1 | MTX | AF2-290 |  |  | 1
209018 | SUNBIPCT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00187 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
212345 | PENS | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00187 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
211374 | AVOC | 12.5 | 229 | 77 | 0 | 17.4 | 10.8 |  |  | 0.00187 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00183 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00183 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00183 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 213 |  |  | 0.00184 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 130.16 |  |  | 0.00184 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00184 |  |  |  | 0.036 |  | 1 | CAPACITY | Hummel |  |  | 1
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00184 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 37.91 |  |  | 0.00183 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
209031 | WAYM IPP E | 34.5 | 229 | 74 | 0 | 55.5 | 33.88 |  |  | 0.00183 |  |  |  | 0 |  | 1 | NEW | K21 |  |  | 1
209009 | PEIP 2 | 13.8 | 229 | 56 | 38 | 43.7 | 23.5 |  |  | 0.00183 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | 0.00183 |  |  |  | 0.0975 |  | 1 | MTX | Z2-107 |  |  | 1
209010 | PEIP 1 | 13.8 | 229 | 64 | 17.4 | 26.5 | 21.42 |  |  | 0.00183 |  |  |  | 0.28996 |  | 1 | CAPACITY |  |  |  | 1
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 5.49 |  |  | 0.00183 |  |  |  | 0 |  | 1 | CAPACITY | K21 |  |  | 1
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 5.34 |  |  | 0.00183 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
211490 | AF2-282 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00183 |  |  |  | 0 |  | 1 | NEW | AF2-282 |  |  | 1
211554 | AF2-283 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00183 |  |  |  | 0 |  | 1 | NEW | AF2-283 |  |  | 1
211553 | AF2-283 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00183 |  |  |  | 0 |  | 1 | MTX | AF2-283 |  |  | 1
211489 | AF2-282 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00183 |  |  |  | 0 |  | 1 | MTX | AF2-282 |  |  | 1
209972 | AF2-288 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00178 |  |  |  | 0 |  | 1 | NEW | AF2-288 |  |  | 1
209937 | AF2-287 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00178 |  |  |  | 0 |  | 1 | NEW | AF2-287 |  |  | 1
209936 | AF2-287 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00178 |  |  |  | 0 |  | 1 | MTX | AF2-287 |  |  | 1
209971 | AF2-288 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00178 |  |  |  | 0 |  | 1 | MTX | AF2-288 |  |  | 1
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 134.03 |  |  | 0.00143 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | 0.00143 |  |  |  | 0.0975 |  | 1 | MTX | AA1-100 |  |  | 1
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 21.4 | 11.51 |  |  | 0.00138 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00128 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00128 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 26.98 |  |  | 0.00123 |  |  |  | 0 |  | 1 | NEW | S14 |  |  | 1
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 6.74 |  |  | 0.00123 |  |  |  | 0 |  | 1 | CAPACITY | S14 |  |  | 1
314860 | 4E MILL | 138 | 345 | 77 | 0 | 50 | 0 |  |  | 0.00119 |  |  |  | 0 |  | 1 | NEWENERGY | Covington |  |  | 1
314859 | 4WSTVACO | 138 | 345 | 2 | 0 | 40.5 | 0 |  |  | 0.00119 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
909222 | X2-060 E | 138 | 345 | 64 | 0 | 30 | 0 |  |  | 0.00119 |  |  |  | 0 |  | 1 | ENERGY | Covington |  |  | 1
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 0.76 |  |  | 0.00119 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 0.75 |  |  | 0.00119 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
918234 | AA1-038_E | 0.69 | 345 | 74 | 0 | 66.7 | 66.03 |  |  | 0.00119 |  |  |  | 0 |  | 1 | NEW | AA1-038 |  |  | 1
315616 | AA1-038_C | 0.69 | 345 | 74 | 0 | 9.9 | 9.8 |  |  | 0.00119 |  |  |  | 0 |  | 1 | CAPACITY | AA1-038 |  |  | 1
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 5.5 |  |  | 0.00119 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | 0.00115 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 55.94 |  |  | 0.00115 |  |  |  | 0 |  | 1 | NEW | U2-073 A |  |  | 1
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 73.26 |  |  | 0.00115 |  |  |  | 0 |  | 1 | NEW | P28 |  |  | 1
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 31.73 |  |  | 0.00115 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 24.52 |  |  | 0.00115 |  |  |  | 0 |  | 1 | NEW | U2-073 B |  |  | 1
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 11.51 |  |  | 0.00115 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 13.37 |  |  | 0.00115 |  |  |  | 0 |  | 1 | CAPACITY | P28 |  |  | 1
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 14.6 | 7.03 |  |  | 0.00115 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 A |  |  | 1
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 8.4 | 4.05 |  |  | 0.00115 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 B |  |  | 1
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.00112 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 502.2 |  |  | 0.00112 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 502.8 |  |  | 0.00112 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 502.3 |  |  | 0.00112 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 503.8 |  |  | 0.00112 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.00112 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916001 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 44.5 | 21.44 |  |  | 0.00104 |  |  |  | 0 |  | 1 | NEW | N47 |  |  | 1
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 5.16 |  |  | 0.00104 |  |  |  | 0 |  | 1 | CAPACITY | N47 |  |  | 1
203926 | AA2-133 GEN | 13.8 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.00101 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 25.15 |  |  | 0.00098 |  |  |  | 0 |  | 1 | NEW | U2-030 |  |  | 1
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 3.76 |  |  | 0.00098 |  |  |  | 0 |  | 1 | CAPACITY | U2-030 |  |  | 1
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 236.66 |  |  | 0.00094 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00094 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00094 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-076 |  |  | 1
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.00087 |  |  |  | 0 |  | 1 | CAPACITY | X1-109 |  |  | 1
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.00087 |  |  |  | 0.036 |  | 1 | CAPACITY | X1-109 |  |  | 1
203937 | 26AA1-144 G2 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203936 | 26AA1-144 G1 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.00086 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.11 |  |  | 0.00086 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 14.76 |  |  | 0.00079 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203938 | 26AA2-132 | 34.5 | 226 | 29 | 0 | 19.9 | 0 |  |  | 0.00075 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
237041 | AE2-055 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00074 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
940682 | AE2-055 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00074 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 850.6 |  |  | 0.00074 |  |  |  | 0 |  | 1 | CAPACITY | Cone1 |  |  | 1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 850 |  |  | 0.00074 |  |  |  | 0 |  | 1 | CAPACITY | Cone2 |  |  | 1
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | 0.00073 |  |  |  | 0 |  | 1 | MTX | AC1-025 |  |  | 1
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.00071 |  |  |  | 0 |  | 1 | NEW | K02 |  |  | 1
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.0007 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 11.3 |  |  | 0.0007 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
236828 | 01GRAYMONT | 46 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.00069 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
237083 | AE1-147_GEN | 0.6 | 201 | 75 | 0 | 19.98 | 1.46 |  |  | 0.00069 |  |  |  | 0 |  | 1 | CAPACITY | AE1-147 |  |  | 1
939171 | AE1-147_E | 0.6 | 201 | 75 | 0 | 7.98 | 0.58 |  |  | 0.00069 |  |  |  | 0 |  | 1 | NEW | AE1-147 |  |  | 1
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | 0.00067 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 11.3 |  |  | 0.00063 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 49.15 |  |  | 0.00058 |  |  |  | 0 |  | 1 | NEW | P47 |  |  | 1
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.2 | 9.28 |  |  | 0.00058 |  |  |  | 0 |  | 1 | CAPACITY | P47 |  |  | 1
203944 | AF2-271 E | 46 | 226 | 75 | 0 | 3 | 0.28 |  |  | 0.00057 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 21.5 | 11.56 |  |  | 0.00055 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 39.07 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | N39 |  |  | 1
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.00047 |  |  |  | 0 |  | 1 | NEW | O38 |  |  | 1
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 11.1 | 6.78 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | N39 |  |  | 1
957932 | AF2-087 E | 46 | 226 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00046 |  |  |  | 0 |  | 1 | NEW | AF2-087 |  |  | 1
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.1 | 5.56 |  |  | 0.00047 |  |  |  | 0 |  | 1 | CAPACITY | O38 |  |  | 1
203941 | AF2-087 C | 46 | 226 | 75 | 0 | 3.05 | 0.28 |  |  | 0.00046 |  |  |  | 0 |  | 1 | CAPACITY | AF2-087 |  |  | 1
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 28.23 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 11.56 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.3 | 8.34 |  |  | 0.00045 |  |  |  | 0 |  | 1 | CAPACITY | K28 |  |  | 1
943302 | AF1-001 E | 34.5 | 201 | 75 | 0 | 7.25 | 0.53 |  |  | 0.00043 |  |  |  | 0 |  | 1 | NEW | AF1-001 |  |  | 1
237039 | AF1-001 C | 34.5 | 201 | 75 | 0 | 6.5 | 0.47 |  |  | 0.00043 |  |  |  | 0 |  | 1 | CAPACITY | AF1-001 |  |  | 1
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 7.03 |  |  | 0.00041 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 6.96 |  |  | 0.00041 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200665 | 26SHAWVL 3 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.0004 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200666 | 26SHAWVL 4 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.0004 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 437.1 |  |  | 0.00039 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.2 | 441.2 |  |  | 0.00039 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200722 | 26SHAWVL 2 | 18 | 226 | 30 | 62 | 125 | 117.94 |  |  | 0.00036 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200715 | 26SHAWVL 1 | 18 | 226 | 30 | 62 | 123 | 116.05 |  |  | 0.00036 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 41.7 | 25.46 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | Q36 |  |  | 1
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 5.07 |  |  | 0.00036 |  |  |  | 0 |  | 1 | CAPACITY | Q36 |  |  | 1
203946 | AE2-131 C | 34.5 | 226 | 75 | 0 | 12 | 1.11 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AE2-131 |  |  | 1
941352 | AE2-131 E | 34.5 | 226 | 75 | 0 | 8 | 0.74 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AE2-131 |  |  | 1
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.22 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
913142 | Y1-033 E OP1 | 0.7 | 226 | 74 | 0 | 34.02 | 20.77 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | Y1-033 |  |  | 1
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4 |  |  | 0.00032 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 3.05 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | Y1-033 |  |  | 1
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 31.6 | 19.29 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | Q53 |  |  | 1
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 3.91 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | Q53 |  |  | 1
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | 0.00028 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 25.64 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | K23 |  |  | 1
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 19.54 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | L13 |  |  | 1
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 17.58 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
203940 | AF1-140 C | 23 | 226 | 75 | 0 | 9.78 | 0.9 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AF1-140 |  |  | 1
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | 0.00028 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
944752 | AF1-140 E | 23 | 226 | 75 | 0 | 6.52 | 0.6 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AF1-140 |  |  | 1
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 3.85 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | Lookout Wind |  |  | 1
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 3.6 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | L13 |  |  | 1
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 4.8 | 2.93 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | K23 |  |  | 1
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 1.1 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 525.7 |  |  | 0.00026 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200503 | 26C.SLOPE | 115 | 226 | 11 | 17 | 50 | 0 |  |  | 0.00026 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
203942 | AF2-270 E | 23 | 226 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 62.3 | 38.03 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | R32 |  |  | 1
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 54.4 | 33.21 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | O18 |  |  | 1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 44 | 26.86 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | P60 |  |  | 1
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 7.75 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | R32 |  |  | 1
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 5.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | P60 |  |  | 1
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | O18 |  |  | 1
916004 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | K22 |  |  | 1
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.55 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | K22 |  |  | 1
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.53 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 34.62 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | Z1-069 |  |  | 1
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 17.1 | 10.44 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Z1-069 |  |  | 1
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 26.2 | 15.99 |  |  | 0.00021 |  |  |  | 0 |  | 1 | NEW | K13 |  |  | 1
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 1.95 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | K13 |  |  | 1
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.00019 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 17.22 |  |  | 0.00017 |  |  |  | 0 |  | 1 | NEW | V3-030 |  |  | 1
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 3.24 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY | V3-030 |  |  | 1
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 852.3 | 852.3 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY | Keys1 |  |  | 1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 851.6 | 851.6 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY | Keys2 |  |  | 1
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 410 | 156.58 |  |  | 0.00017 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235622 | 01SBEND4 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00017 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235621 | 01SBEND3 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00017 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235620 | 01SBEND2 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00017 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235619 | 01SBEND1 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.00017 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.00012 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200809 | 26SITHE | 138 | 226 | 60 | 0 | 36 | 25.31 |  |  | 0.0001 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 620 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237050 | AF1-155 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | AF1-155 |  |  | 1
944902 | AF1-155 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 9e-05 |  |  |  | 0 |  | 1 | NEW | AF1-155 |  |  | 1
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 42.3 |  |  | 8e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 8.66 |  |  | 2e-05 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200805 | 26COLVER13 | 13.2 | 226 | 12 | 95.7 | 110 | 0 |  |  | 2e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 253.85 |  |  | -3e-05 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 614 |  |  | -3e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 650 |  |  | -3e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 317.2 | 121.14 |  |  | -6e-05 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | -6e-05 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | -6e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | RONCO |  |  | 1
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | -7e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 124.5 |  |  | -9e-05 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | -9e-05 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | -9e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | T-174 |  |  | 1
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 20.96 |  |  | -0.00023 |  |  |  | 0 |  | 1 | NEW | U2-061 |  |  | 1
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 3.13 |  |  | -0.00023 |  |  |  | 0 |  | 1 | CAPACITY | U2-061 |  |  | 1
916000 | 01BACKB E | 34.5 | 201 | 74 | 0 | 57.9 | 27.9 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | K19 |  |  | 1
916002 | 01ELLIOTTS E | 34.5 | 201 | 74 | 0 | 44.9 | 21.63 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | N32 |  |  | 1
237013 | AA2-103 E | 0.48 | 201 | 76 | 0 | 20 | 0 |  |  | -0.00026 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 3.9 |  |  | -0.00026 |  |  |  | 0 |  | 1 | CAPACITY | K19 |  |  | 1
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 2.65 |  |  | -0.00026 |  |  |  | 0 |  | 1 | CAPACITY | N32 |  |  | 1
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 164.5 |  |  | -0.00036 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 155.36 |  |  | -0.00036 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 21.09 |  |  | -0.00036 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 552 |  |  | -0.00039 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 545.5 |  |  | -0.00039 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 710 |  |  | -0.00043 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237052 | AF1-210 C | 25 | 201 | 75 | 0 | 9.54 | 0.7 |  |  | -0.00045 |  |  |  | 0 |  | 1 | CAPACITY | AF1-210 |  |  | 1
945452 | AF1-210 E | 25 | 201 | 75 | 0 | 6.36 | 0.46 |  |  | -0.00045 |  |  |  | 0 |  | 1 | NEW | AF1-210 |  |  | 1
237043 | AE2-125 C | 25 | 201 | 75 | 0 | 8.28 | 0.6 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
941312 | AE2-125 E | 25 | 201 | 75 | 0 | 5.52 | 0.4 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 4.22 |  |  | -0.00048 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 3.77 |  |  | -0.00048 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | -0.0005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | -0.0005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 21.23 |  |  | -0.0005 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
203932 | AE1-123 | 34.5 | 226 | 55 | 0 | 18 | 9.68 |  |  | -0.0005 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | -0.0005 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | -0.0005 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237054 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 195.92 |  |  | -0.00051 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 173.6 | 199.5 | 76.19 |  |  | -0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 167 | 191.9 | 73.29 |  |  | -0.00053 |  |  |  | 0.036 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 164.1 | 188.6 | 72.03 |  |  | -0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | -0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | -0.00053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237046 | AF1-021 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | -0.00052 |  |  |  | 0 |  | 1 | CAPACITY | AF1-021 |  |  | 1
916003 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 13.3 | 6.41 |  |  | -0.00052 |  |  |  | 0 |  | 1 | NEW | K20 |  |  | 1
943502 | AF1-021 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | -0.00052 |  |  |  | 0 |  | 1 | NEW | AF1-021 |  |  | 1
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 0.82 |  |  | -0.00052 |  |  |  | 0 |  | 1 | CAPACITY | K20 |  |  | 1
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 3.83 |  |  | -0.00053 |  |  |  | 0.0789 |  | 1 | CAPACITY | ALLEG LD_5 |  |  | 1
237048 | AF1-022 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | -0.00057 |  |  |  | 0 |  | 1 | CAPACITY | AF1-022 |  |  | 1
943512 | AF1-022 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | -0.00057 |  |  |  | 0 |  | 1 | NEW | AF1-022 |  |  | 1
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 62 | 33.35 |  |  | -0.00061 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 80.2 |  |  | -0.00082 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 28.78 |  |  | -0.00086 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.00086 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.00086 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.00086 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 28.78 |  |  | -0.00086 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235586 | 01HARRN2 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.00089 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235585 | 01HARRN1 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.00089 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235587 | 01HARRN3 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.00089 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
203939 | AE1-160 C | 34.5 | 226 | 75 | 0 | 12.7 | 1.17 |  |  | -0.0009 |  |  |  | 0 |  | 1 | CAPACITY | AE1-160 |  |  | 1
939292 | AE1-160 E | 34.5 | 226 | 75 | 0 | 7.3 | 0.68 |  |  | -0.0009 |  |  |  | 0 |  | 1 | NEW | AE1-160 |  |  | 1
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 59.57 |  |  | -0.00091 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
237036 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 7.64 |  |  | -0.00099 |  |  |  | 0.1042 |  | 1 | CAPACITY | AD2-002 |  |  | 1
237068 | AA2-119 GEN | 20.5 | 201 | 58 | 0 | 600 | 0 |  |  | -0.00112 |  |  |  | 0.036 |  | 1 | NEW | Harrison |  |  | 1
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 41.39 |  |  | -0.00113 |  |  |  | 0 |  | 1 | NEW | P59 |  |  | 1
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 5.64 |  |  | -0.00113 |  |  |  | 0 |  | 1 | CAPACITY | P59 |  |  | 1
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00131 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00131 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00131 |  |  |  | 0.036 |  | 1 | NEW | AB1-069 |  |  | 1
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.26 |  |  | -0.00131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316248 | AF1-058 C | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.00156 |  |  |  | 0 |  | 1 | CAPACITY | AF1-058 |  |  | 1
943902 | AF1-058 E | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.00156 |  |  |  | 0 |  | 1 | NEW | AF1-058 |  |  | 1
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  |  |  | -0.0016
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 2.69 |  |  | -0.00159 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239022 | 02NWCAG3 | 14.4 | 202 | 57 | 20 | 92.3 | 35.25 |  |  | -0.00194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
254026 | 15USSILL | 138 | 215 | 77 | 0 | 66 | 27.72 |  |  | -0.00197 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
239024 | 02NWCAG5 | 16.5 | 202 | 57 | 23 | 145 | 55.38 |  |  | -0.00198 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
254024 | 15CLAIRT | 138 | 215 | 77 | 0 | 35 | 14.7 |  |  | -0.00198 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
239023 | 02NWCAG4 | 14.4 | 202 | 57 | 20 | 93 | 35.52 |  |  | -0.002 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 0.04 |  |  | -0.002 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
254037 | 15UNIVRS | 138 | 215 | 77 | 0 | 1.1 | 0.46 |  |  | -0.00202 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 567.5 |  |  | -0.00206 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316003 | AC1-222 C | 0.6 | 345 | 75 | 0 | 38.8 | 5.82 |  |  | -0.00211 |  |  |  | 0 |  | 1 | CAPACITY | AC1-222 |  |  | 1
927264 | AC1-222 E | 0.6 | 345 | 75 | 0 | 25.9 | 3.88 |  |  | -0.00211 |  |  |  | 0 |  | 1 | NEW | AC1-222 |  |  | 1
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 13.77 |  |  | -0.00215 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 38.8 |  |  | -0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253970 | 15BI2 | 13.8 | 215 | 58 | 83.2 | 95.6 | 36.51 |  |  | -0.00216 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.5 | 18.52 |  |  | -0.00216 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 6.91 |  |  | -0.00216 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | -0.0022
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | -0.0022
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 156.58 |  |  | -0.00223 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | -0.00223 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | -0.00223 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 2.69 |  |  | -0.00223 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253924 | 15SHELL | 138 | 215 | 58 | 0 | 98 | 0 |  |  | -0.00226 |  |  |  | 0.036 |  | 1 | ENERGY | Y3-103 |  |  | 1
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | -0.00226 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | -0.00226 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 15.2 | 5.8 |  |  | -0.00226 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | -0.00226 |  |  |  | 0.036 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | -0.00226 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0.53 |  |  | -0.00226 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
254303 | AC2-168 C | 138 | 215 | 75 | 0 | 4.4 | 0.32 |  |  | -0.00226 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 216.9 |  |  | -0.00227 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
254305 | AE2-115 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | -0.00227 |  |  |  | 0 |  | 1 | CAPACITY | AE2-115 |  |  | 1
254304 | AE2-114 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | -0.00227 |  |  |  | 0 |  | 1 | CAPACITY | AE2-114 |  |  | 1
941202 | AE2-114 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | -0.00227 |  |  |  | 0 |  | 1 | NEW | AE2-114 |  |  | 1
941212 | AE2-115 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | -0.00227 |  |  |  | 0 |  | 1 | NEW | AE2-115 |  |  | 1
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | -0.00227 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | -0.00227 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 2.55 |  |  | -0.00228 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | -0.0023 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | -0.0023 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | -0.0023 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | -0.0023 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
253900 | 15BVRVL1 | 22 | 215 | 44 | 781.7 | 898.5 | 898.5 |  |  | -0.00232 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 899.3 |  |  | -0.00232 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 26.1 | 16.36 |  |  | -0.00238 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 307.6 | 117.47 |  |  | -0.0024 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | -0.0024 |  |  |  | 0.036 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | -0.0024 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00241 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
241951 | AB1-105 OP | 345 | 202 | 58 | 0 | 850 | 0 |  |  | -0.00243 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1247 |  |  | -0.00249 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 620.4 |  |  | -0.00268 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | -0.00268 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | -0.00268 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 7.55 |  |  | -0.0028 |  |  |  | 0 |  | 1 | NEW | Z1-035 |  |  | 1
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 1.13 |  |  | -0.0028 |  |  |  | 0 |  | 1 | CAPACITY | Z1-035 |  |  | 1
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 280 | 106.93 |  |  | -0.00285 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | -0.00285 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | -0.00285 |  |  |  | 0.036 |  | 1 | CAPACITY | Y2-050 |  |  | 1
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 25 | 0.37 |  |  | -0.00331 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
270122 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 185.22 |  |  | -0.00332 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235590 | 01PLEAS1 | 26 | 201 | 16 | 300 | 639 | 0 |  |  | -0.00336 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235591 | 01PLEAS2 | 26 | 201 | 16 | 350 | 639 | 0 |  |  | -0.00336 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | -0.00341 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | -0.00341 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 170.9 | 65.27 |  |  | -0.00344 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 170.8 | 65.23 |  |  | -0.00344 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 10.54 |  |  | -0.00345 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 790.2 |  |  | -0.00345 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 627.1 |  |  | -0.00348 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 770.1 |  |  | -0.00358 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
245305 | 05WOOSTER | 69 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.00358 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245304 | 05WOOSTER | 23 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.00362 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243158 | 05WOOSTE | 138 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.00365 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 29.6 |  |  | -0.00366 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.00366 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 28.95 |  |  | -0.00366 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 28.68 |  |  | -0.00366 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.00371 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 19.51 |  |  | -0.00371 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 18.94 |  |  | -0.00371 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 9.4 |  |  | -0.00379 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 5.74 |  |  | -0.00407 |  |  |  | 0 |  | 1 | CAPACITY | AC1-075 |  |  | 1
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 3.26 |  |  | -0.00407 |  |  |  | 0 |  | 1 | NEW | AC1-075 |  |  | 1
316205 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 1.92 |  |  | -0.00407 |  |  |  | 0 |  | 1 | CAPACITY | AC1-080 |  |  | 1
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 1.08 |  |  | -0.00407 |  |  |  | 0 |  | 1 | NEW | AC1-080 |  |  | 1
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.0041 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.0041 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.0041 |  |  |  | 0.036 |  | 1 | CAPACITY | Guernsey |  |  | 1
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 0.88 |  |  | -0.00415 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
907201 | AC2-103 E1 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.00416 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
907202 | AC2-103 E2 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.00416 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
241886 | AC2-103 C2 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.00416 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
241885 | AC2-103 C1 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.00416 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 113.43 |  |  | -0.00444 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | -0.00444 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | -0.00444 |  |  |  | 0.036 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 896 |  |  | -0.00462 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 345.1 | 131.79 |  |  | -0.00468 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 162.6 | 62.1 |  |  | -0.00468 |  |  |  | 0.036 |  | 1 | CAPACITY | FREMONT |  |  | 1
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 159.1 | 60.76 |  |  | -0.00468 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 41.19 |  |  | -0.00474 |  |  |  | 0 |  | 1 | NEW | M24 |  |  | 1
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00474 |  |  |  | 0.0975 |  | 1 | MTX | M24 BAT |  |  | 1
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 21.15 |  |  | -0.00474 |  |  |  | 0 |  | 1 | NEW | AB1-150 |  |  | 1
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 7.23 |  |  | -0.00474 |  |  |  | 0 |  | 1 | CAPACITY | M24 |  |  | 1
237033 | AB1-150 C | 138 | 201 | 74 | 0 | 7.3 | 3.52 |  |  | -0.00474 |  |  |  | 0 |  | 1 | CAPACITY | AB1-150 |  |  | 1
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00484 |  |  |  | 0 |  | 1 | NEW | V4-010 |  |  | 1
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.00484 |  |  |  | 0 |  | 1 | CAPACITY | V4-010 |  |  | 1
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.00488 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.00488 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
270174 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00488 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00488 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 243 | 92.8 |  |  | -0.00494 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -0.00494 |  |  |  | 0.036 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -0.00494 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
918421 | AA1-056 | 345 | 202 | 58 | 0 | 46 | 0 |  |  | -0.00494 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 101.27 |  |  | -0.00494 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 0.19 |  |  | -0.00494 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.00495 |  |  |  | 0.036 |  | 1 | NEW | AB1-107 |  |  | 1
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 0 |  |  | -0.00495 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.00495 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 124.58 |  |  | -0.00495 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.00495 |  |  |  | 0.036 |  | 1 | CAPACITY | OREGON |  |  | 1
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.00495 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 139.32 |  |  | -0.00499 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.00499 |  |  |  | 0.036 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.00499 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.00499 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.00499 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.00499 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.00499 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.00499 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 1.46 |  |  | -0.00502 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247454 | 05OGG STREET | 69 | 205 | 77 | 0 | 10 | 7.16 |  |  | -0.00506 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 4.3 |  |  | -0.00509 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 0.19 |  |  | -0.00526 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
244357 | 05GRANGER EL | 34.5 | 205 | 2 | 0 | 3.2 | 0 |  |  | -0.0053 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00535 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 20.96 |  |  | -0.00537 |  |  |  | 0 |  | 1 | NEW | U1-059 |  |  | 1
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 7.71 |  |  | -0.00537 |  |  |  | 0 |  | 1 | NEW | W1-056 |  |  | 1
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 4.63 |  |  | -0.00537 |  |  |  | 0 |  | 1 | CAPACITY | U1-059 |  |  | 1
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.16 |  |  | -0.00537 |  |  |  | 0 |  | 1 | CAPACITY | W1-056 |  |  | 1
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.00547 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.00547 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.2 | 45.52 |  |  | -0.00547 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 8.4 |  |  | -0.00547 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 0.16 |  |  | -0.00547 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270106 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.0055 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 125.75 |  |  | -0.00558 |  |  |  | 0 |  | 1 | NEW | U2-072 |  |  | 1
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 18.79 |  |  | -0.00558 |  |  |  | 0 |  | 1 | CAPACITY | U2-072 |  |  | 1
925135 | AB2-170 E | 0.55 | 205 | 75 | 0 | 80.6 | 0 |  |  | -0.0056 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
247549 | V3-028 C | 345 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.0056 |  |  |  | 0 |  | 1 | CAPACITY | V3-028 |  |  | 1
925133 | AB2-170 C | 0.55 | 205 | 75 | 0 | 49.4 | 0 |  |  | -0.0056 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | -0.0056 |  |  |  | 0 |  | 1 | NEW | V3-028 |  |  | 1
253158 | 09INDI L | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.00578 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1308.8 | 1308.8 |  |  | -0.00581 |  |  |  | 0 |  | 1 | CAPACITY | MTG1 |  |  | 1
253160 | 09JCKCEN | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.00586 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 44.38 |  |  | -0.00587 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 63.89 |  |  | -0.00588 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 63.82 |  |  | -0.00588 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.00588 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.00588 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.00588 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 25.91 |  |  | -0.00588 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.0059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.0059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.0059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 30.93 |  |  | -0.0059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 30.55 |  |  | -0.0059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 30.17 |  |  | -0.0059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1407 | 1407 |  |  | -0.00594 |  |  |  | 0 |  | 1 | CAPACITY | GVG2 |  |  | 1
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1389 | 1389 |  |  | -0.00594 |  |  |  | 0 |  | 1 | CAPACITY | GVG1 |  |  | 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.00598 |  |  |  | 0 |  | 1 | NEW | R60 2 |  |  | 1
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.00598 |  |  |  | 0 |  | 1 | NEW | R60 1 |  |  | 1
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 84.83 | 40.87 |  |  | -0.00598 |  |  |  | 0 |  | 1 | NEW | R60 3 |  |  | 1
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 7.95 |  |  | -0.00598 |  |  |  | 0 |  | 1 | CAPACITY | R60 3 |  |  | 1
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.00598 |  |  |  | 0 |  | 1 | CAPACITY | R60 1 |  |  | 1
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.00598 |  |  |  | 0 |  | 1 | CAPACITY | R60 2 |  |  | 1
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.00605 |  |  |  | 0 |  | 1 | CAPACITY | AC1-068 |  |  | 1
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.00605 |  |  |  | 0 |  | 1 | CAPACITY | AC1-069 |  |  | 1
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.00605 |  |  |  | 0 |  | 1 | CAPACITY | AC1-165 |  |  | 1
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.00605 |  |  |  | 0 |  | 1 | CAPACITY | AC1-166 |  |  | 1
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.00605 |  |  |  | 0 |  | 1 | NEW | AC1-165 |  |  | 1
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.00605 |  |  |  | 0 |  | 1 | NEW | AC1-166 |  |  | 1
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.00605 |  |  |  | 0 |  | 1 | NEW | AC1-068 |  |  | 1
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.00605 |  |  |  | 0 |  | 1 | NEW | AC1-069 |  |  | 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.00607 |  |  |  | 0 |  | 1 | NEW | V1-011 |  |  | 1
247607 | V1-011 GEN | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | V1-011 |  |  | 1
243017 | 05HAVILAND1 | 138 | 205 | 77 | 0 | 4.5 | 3.22 |  |  | -0.00607 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 124.2 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 72.8 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.00607 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.0061 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 57.21 |  |  | -0.00611 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 57.17 |  |  | -0.00611 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149 | 56.9 |  |  | -0.00611 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 25.52 |  |  | -0.00612 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
253363 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00612 |  |  |  | 0.05 |  | 1 | MTX | AC1-212 |  |  | 1
253178 | 09MINSTR | 69 | 209 | 77 | 0 | 10 | 4.61 |  |  | -0.00612 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
AC1-212 | BATEXP_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0061
253362 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.28 |  |  | -0.00612 |  |  |  | 0 |  | 1 | CAPACITY | AC1-212 |  |  | 1
253128 | 09CELINA | 69 | 209 | 77 | 0 | 4 | 2.89 |  |  | -0.00614 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 76.1 | 36.67 |  |  | -0.00618 |  |  |  | 0 |  | 1 | NEW | R49 |  |  | 1
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 11.03 |  |  | -0.00618 |  |  |  | 0 |  | 1 | CAPACITY | R49 |  |  | 1
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | -0.00617 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
253127 | 09CEDRVL | 69 | 209 | 77 | 0 | 1.8 | 1.3 |  |  | -0.00619 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253197 | 09PIQUA3 | 69 | 209 | 77 | 0 | 38.3 | 2.77 |  |  | -0.00621 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 57.82 |  |  | -0.00622 |  |  |  | 0 |  | 1 | NEW | T131 |  |  | 1
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 31.8 |  |  | -0.00622 |  |  |  | 0 |  | 1 | NEW | AC1-173 |  |  | 1
247521 | T131 | 0.69 | 205 | 74 | 26.1 | 30 | 14.45 |  |  | -0.00622 |  |  |  | 0 |  | 1 | CAPACITY | T131 |  |  | 1
270191 | AC1-173 C | 0.65 | 205 | 74 | 0 | 9.9 | 4.77 |  |  | -0.00622 |  |  |  | 0 |  | 1 | CAPACITY | AC1-173 |  |  | 1
247622 | Y3-025 | 69 | 205 | 64 | 0 | 3.18 | 0 |  |  | -0.00623 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.14 |  |  | -0.00623 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253234 | 09VERSAL | 69 | 209 | 77 | 0 | 5.4 | 3.91 |  |  | -0.00626 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | -0.00628 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 3.05 |  |  | -0.00629 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 77.49 |  |  | -0.00631 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.00631 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253029 | 09GRNVIL | 138 | 209 | 77 | 0 | 4.5 | 3.26 |  |  | -0.00631 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 800 |  |  | -0.00631 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 8.21 |  |  | -0.00633 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 127.94 |  |  | -0.00635 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 92.04 |  |  | -0.00635 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 0.15 |  |  | -0.00635 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 2.26 |  |  | -0.00636 |  |  |  | 0 |  | 1 | NEW | AC2-067 |  |  | 1
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 1.93 |  |  | -0.00636 |  |  |  | 0 |  | 1 | CAPACITY | AC2-067 |  |  | 1
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 41.94 |  |  | -0.00639 |  |  |  | 0.39467 |  | 1 | CAPACITY |  |  |  | 1
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0.11 |  |  | -0.00639 |  |  |  | 0 |  | 1 | NEW | V4-073 |  |  | 1
253303 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.07 |  |  | -0.00639 |  |  |  | 0 |  | 1 | CAPACITY | V4-073 |  |  | 1
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 10.04 |  |  | -0.0064 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247530 | 05COVRT3 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.0064 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247529 | 05COVRT2 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.0064 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 2 |  |  | 1
247528 | 05COVRT1 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.0064 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247531 | 05COVRT4 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.0064 |  |  |  | 0 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.0064 |  |  |  | 0 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 114.1 | 131.2 | 50.11 |  |  | -0.0064 |  |  |  | 0 |  | 1 | CAPACITY | Covert 2 |  |  | 1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1330 |  |  | -0.00642 |  |  |  | 0 |  | 1 | CAPACITY | AMG3 |  |  | 1
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 800 |  |  | -0.00642 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00643 |  |  |  | 0 |  | 1 | MTX | AB1-055 |  |  | 1
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 36.56 |  |  | -0.0065 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.00657 |  |  |  | 0 |  | 1 | NEW | Z2-113 |  |  | 1
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.00657 |  |  |  | 0 |  | 1 | CAPACITY | Z2-113 |  |  | 1
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 2.22 |  |  | -0.00656 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247604 | X1-042 | 12 | 205 | 64 | 0 | 3.8 | 2.55 |  |  | -0.00656 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.00658 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.00658 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
253317 | AC1-085 B_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.00658 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253314 | AC1-085 A_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.00658 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.3 | 0.72 |  |  | -0.00658 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246235 | 05BLUFFTON | 69 | 205 | 77 | 0 | 2 | 1.43 |  |  | -0.00657 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.02 |  |  | -0.00659 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 54.8 | 40.8 |  |  | -0.0066 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.00661 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.00661 |  |  |  | 0.036 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 127.17 |  |  | -0.00661 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 1.75 |  |  | -0.00661 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 1014.5 |  |  | -0.00661 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 3.33 |  |  | -0.00662 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 2.16 |  |  | -0.00663 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.00664 |  |  |  | 0 |  | 1 | CAPACITY | Z2-116 |  |  | 1
247969 | Z2-116 E | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.00664 |  |  |  | 0 |  | 1 | NEW | Z2-116 |  |  | 1
251828 | CLNTESP1 | 0 | 212 | 76 | 0 | 10 | 0 |  |  | -0.00666 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 22.88 |  |  | -0.00666 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 22.8 |  |  | -0.00666 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 22.19 |  |  | -0.00666 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 22.07 |  |  | -0.00666 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 3.89 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246477 | 05NILES | 69 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.00667 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246476 | 05NILES | 34.5 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.00667 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -0.00667 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
251832 | 08HLCRTG | 0.38 | 212 | 75 | 0 | 120 | 8.76 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY | AB1-014 |  |  | 1
930062 | AB1-014 E | 0.38 | 212 | 75 | 0 | 77.5 | 5.66 |  |  | -0.00667 |  |  |  | 0 |  | 1 | NEW | AB1-014 |  |  | 1
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 54.49 |  |  | -0.00667 |  |  |  | 0 |  | 1 | NEW | AC2-176 |  |  | 1
252507 | AC2-088 C | 0.57 | 212 | 75 | 0 | 38.4 | 2.8 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
932665 | AC2-088 E | 0.57 | 212 | 75 | 0 | 31.6 | 2.31 |  |  | -0.00667 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
270201 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 8.14 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY | AC2-176 |  |  | 1
252509 | AD1-136 C | 0.57 | 212 | 75 | 0 | 5.4 | 0.39 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
935033 | AD1-136 E | 0.57 | 212 | 75 | 0 | 4.6 | 0.34 |  |  | -0.00667 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.5 | 3.02 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.6 | 1.44 |  |  | -0.00667 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1186 | 1186 |  |  | -0.00668 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 29.06 |  |  | -0.00668 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76 | 29.02 |  |  | -0.00668 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 28.99 |  |  | -0.00668 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 28.91 |  |  | -0.00668 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 28.87 |  |  | -0.00668 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 28.8 |  |  | -0.00668 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243352 | 05NTRDAM | 138 | 205 | 77 | 0 | 57.6 | 41.21 |  |  | -0.00668 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.48 |  |  | -0.00668 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 113.58 |  |  | -0.0067 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.1 | 113.46 |  |  | -0.0067 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | -0.0067 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | -0.0067 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | -0.0067 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | -0.0067 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 46.25 |  |  | -0.0067 |  |  |  | 0 |  | 1 | NEW | S71 |  |  | 1
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 11.56 |  |  | -0.0067 |  |  |  | 0 |  | 1 | CAPACITY | S71 |  |  | 1
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 2.4 | 1.61 |  |  | -0.00669 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 272.1 | 103.92 |  |  | -0.00671 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-079 |  |  | 1
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 202.7 | 77.41 |  |  | -0.00671 |  |  |  | 0 |  | 1 | CAPACITY | Z1-079 |  |  | 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 6.79 |  |  | -0.00671 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
270186 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.00671 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 31.16 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.5 | 30.74 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 30.59 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 29.56 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251956 | 08MADSN5 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251953 | 08MADSN2 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251954 | 08MADSN3 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251958 | 08MADSN7 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251957 | 08MADSN6 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251952 | 08MADSN1 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251959 | 08MADSN8 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251955 | 08MADSN4 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00672 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 26.35 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 19.29 |  |  | -0.00673 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 11.46 |  |  | -0.00673 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251364 | 08LEBANO | 69 | 212 | 77 | 0 | 30.6 | 21.57 |  |  | -0.00672 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 4.93 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251387 | 08MDDLTW | 69 | 212 | 77 | 0 | 22.5 | 16.62 |  |  | -0.00673 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
243362 | 05RANDOLPH1 | 138 | 205 | 77 | 0 | 4 | 3.06 |  |  | -0.00673 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.00673 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244415 | 05OLIV SLR C | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.00676 |  |  |  | 0 |  | 1 | CAPACITY | OLIV SLR |  |  | 1
247967 | 05OLIV SLR E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.00676 |  |  |  | 0 |  | 1 | NEW | OLIV SLR |  |  | 1
243353 | 05OLIVE | 138 | 205 | 77 | 0 | 5 | 3.58 |  |  | -0.00676 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 95.86 |  |  | -0.00678 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.00678 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.00678 |  |  |  | 0.036 |  | 1 | CAPACITY | X2-052 |  |  | 1
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00678 |  |  |  | 0 |  | 1 | MTX | Y3-099 |  |  | 1
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00678 |  |  |  | 0 |  | 1 | MTX | Y3-100 |  |  | 1
250041 | 08HAMLTN | 138 | 212 | 77 | 0 | 2.2 | 1.55 |  |  | -0.00678 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247225 | 05FTHLG2 | 18 | 205 | 57 | 151.2 | 173.8 | 66.38 |  |  | -0.0068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247224 | 05FTHLG1 | 18 | 205 | 57 | 151.1 | 173.7 | 66.34 |  |  | -0.0068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.0068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247232 | 05RIVRG3 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.0068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247231 | 05RIVRG2 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.0068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251346 | 08IVYDL1 | 69 | 212 | 77 | 0 | 12.5 | 8.81 |  |  | -0.00682 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
913222 | Y1-054 E | 138 | 212 | 58 | 0 | 20 | 0 |  |  | -0.00683 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
250091 | 08RCHLE3 | 138 | 212 | 77 | 0 | 6.7 | 4.72 |  |  | -0.00683 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.00682 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.00682 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 586 |  |  | -0.00682 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 734 |  |  | -0.00682 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.00684 |  |  |  | 0.0975 |  | 1 | MTX | Z1-065 |  |  | 1
251269 | 08BEAVR2 | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.00684 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 600 |  |  | -0.00683 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00684 |  |  |  | 0 |  | 1 | NEW | V3-007 |  |  | 1
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00684 |  |  |  | 0 |  | 1 | NEW | U2-090 |  |  | 1
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.00684 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.00684 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.00684 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.00684 |  |  |  | 0 |  | 1 | CAPACITY | U2-090 |  |  | 1
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.00684 |  |  |  | 0 |  | 1 | CAPACITY | V3-007 |  |  | 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.00685 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.00685 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.00685 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.00685 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.00685 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.00685 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 227.1 |  |  | -0.00686 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
243415 | 05WWVSTA | 69 | 205 | 61 | 69.8 | 96 | 53.26 |  |  | -0.00687 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
247968 | Z2-115 E | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.00687 |  |  |  | 0 |  | 1 | NEW | Z2-115 |  |  | 1
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.00687 |  |  |  | 0 |  | 1 | CAPACITY | Z2-115 |  |  | 1
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 194.77 |  |  | -0.0069 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | -0.0069 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | -0.0069 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.0069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.0069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 52.4 |  |  | -0.00691 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00693 |  |  |  | 0 |  | 1 | NEW | U3-002 |  |  | 1
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 6.36 |  |  | -0.00693 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 6.17 |  |  | -0.00693 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
249991 | 08BUFTN1 | 138 | 212 | 77 | 0 | 2.2 | 0 |  |  | -0.00693 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 0.39 |  |  | -0.00694 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 0.37 |  |  | -0.00694 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
342031 | 2PACTOLUS | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | -0.00695 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 223.38 |  |  | -0.00698 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 174.1 | 83.88 |  |  | -0.00704 |  |  |  | 0 |  | 1 | NEW | S06 |  |  | 1
930042 | AB1-006 E2 | 0.69 | 205 | 74 | 0 | 96.75 | 46.61 |  |  | -0.00704 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 88.2 | 42.49 |  |  | -0.00704 |  |  |  | 0 |  | 1 | NEW | T127 4 |  |  | 1
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 84.8 | 40.86 |  |  | -0.00704 |  |  |  | 0 |  | 1 | NEW | T126 2 |  |  | 1
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 84.7 | 40.81 |  |  | -0.00704 |  |  |  | 0 |  | 1 | NEW | T126 3 |  |  | 1
247943 | T-127 E | 0.69 | 205 | 74 | 0 | 79.8 | 38.45 |  |  | -0.00704 |  |  |  | 0 |  | 1 | NEW | T127 5 |  |  | 1
930041 | AB1-006 E1 | 0.69 | 205 | 74 | 0 | 77.25 | 37.22 |  |  | -0.00704 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 12.48 |  |  | -0.00704 |  |  |  | 0 |  | 1 | CAPACITY | S06 |  |  | 1
270180 | AB1-006 W1 | 0.65 | 205 | 74 | 0 | 22.75 | 10.96 |  |  | -0.00704 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 9.73 |  |  | -0.00704 |  |  |  | 0 |  | 1 | CAPACITY | T127 5 |  |  | 1
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 7.37 |  |  | -0.00704 |  |  |  | 0 |  | 1 | CAPACITY | T126 3 |  |  | 1
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 7.32 |  |  | -0.00704 |  |  |  | 0 |  | 1 | CAPACITY | T126 2 |  |  | 1
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 5.68 |  |  | -0.00704 |  |  |  | 0 |  | 1 | CAPACITY | T127 4 |  |  | 1
270181 | AB1-006 W2 | 0.69 | 205 | 74 | 0 | 3.25 | 1.57 |  |  | -0.00704 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 76.89 |  |  | -0.00712 |  |  |  | 0 |  | 1 | NEW | Q01 3 |  |  | 1
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 60.22 |  |  | -0.00712 |  |  |  | 0 |  | 1 | NEW | Q01 4 |  |  | 1
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00713 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00713 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00713 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00713 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 39.65 |  |  | -0.00712 |  |  |  | 0 |  | 1 | NEW | Q01 21 |  |  | 1
247903 | 05FR-22G E | 0.69 | 205 | 74 | 0 | 78.8 | 37.97 |  |  | -0.00712 |  |  |  | 0 |  | 1 | NEW | Q01 22 |  |  | 1
247900 | 05FR-11G E | 0.6 | 205 | 74 | 0 | 78.3 | 37.72 |  |  | -0.00712 |  |  |  | 0 |  | 1 | NEW | Q01 11 |  |  | 1
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 37.1 |  |  | -0.00712 |  |  |  | 0 |  | 1 | NEW | Q01 12 |  |  | 1
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 14.02 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | Q01 4 |  |  | 1
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 12.38 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | Q01 11 |  |  | 1
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | Q01 21 |  |  | 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | Q01 22 |  |  | 1
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | Q01 3 |  |  | 1
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | Q01 12 |  |  | 1
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00712 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 62.67 |  |  | -0.00715 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 61.87 |  |  | -0.00716 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342550 | 4BAVARIAN LF | 138 | 320 | 77 | 0 | 4.8 | 3.24 |  |  | -0.00717 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 18.71 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 18.67 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 18.64 |  |  | -0.0072 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0.41 |  |  | -0.0072 |  |  |  | 0 |  | 1 | NEW | X3-005 |  |  | 1
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 0.25 |  |  | -0.0072 |  |  |  | 0 |  | 1 | CAPACITY | X3-005 |  |  | 1
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00721 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
341584 | 2GRIFFIN | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | -0.00721 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
251542 | 08VERONA | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.00721 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 27.95 |  |  | -0.00722 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.00722 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.00722 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293519 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 67.45 |  |  | -0.00724 |  |  |  | 0 |  | 1 | NEW | S36 |  |  | 1
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 67.45 |  |  | -0.00724 |  |  |  | 0 |  | 1 | NEW | S37 |  |  | 1
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00724 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00724 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | -0.00724 |  |  |  | 0 |  | 1 | CAPACITY | S36 |  |  | 1
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | -0.00724 |  |  |  | 0 |  | 1 | CAPACITY | S37 |  |  | 1
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 1.46 |  |  | -0.00725 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 1.03 |  |  | -0.00725 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270173 | AC1-122_C | 0.6 | 205 | 75 | 0 | 54.4 | 3.97 |  |  | -0.00725 |  |  |  | 0 |  | 1 | CAPACITY | AC1-122 |  |  | 1
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 20.47 |  |  | -0.00725 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00725 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00725 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00725 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
926516 | AC1-122_E | 0.6 | 205 | 75 | 0 | 21.5 | 1.57 |  |  | -0.00725 |  |  |  | 0 |  | 1 | NEW | AC1-122 |  |  | 1
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 1183 |  |  | -0.00724 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 1154 |  |  | -0.00724 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274661 | LASCO STA;2U | 25 | 222 | 49 | 132 | 1134.8 | 1134.8 |  |  | -0.00727 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274660 | LASCO STA;1U | 25 | 222 | 49 | 135 | 1131.2 | 1131.2 |  |  | -0.00727 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1356 |  |  | -0.00728 |  |  |  | 0 |  | 1 | CAPACITY | RKG1 |  |  | 1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1300 |  |  | -0.00728 |  |  |  | 0 |  | 1 | CAPACITY | RKG2 |  |  | 1
251298 | 08CRITDN | 69 | 212 | 77 | 0 | 2.7 | 1.9 |  |  | -0.0073 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 160.3 | 184.3 | 70.39 |  |  | -0.0073 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 158.6 | 182.3 | 69.62 |  |  | -0.0073 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 46.55 |  |  | -0.0073 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 46.55 |  |  | -0.0073 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274687 | WILL CNTY;4U | 20 | 222 | 15 | 49.4 | 510 | 510 |  |  | -0.0073 |  |  |  | 0 |  | 1 | CAPACITY | WILL4 |  |  | 1
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 289.95 |  |  | -0.00732 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet8 |  |  | 1
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 293.58 |  |  | -0.00732 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet7 |  |  | 1
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 209.23 |  |  | -0.00731 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet9 |  |  | 1
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00731 |  |  |  | 0.0975 |  | 1 | MTX | Z1-107 |  |  | 1
276617 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 5.88 |  |  | -0.00731 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276642 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | -0.00732 |  |  |  | 0 |  | 1 | CAPACITY | AC1-204 |  |  | 1
276640 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | -0.00732 |  |  |  | 0.036 |  | 1 | CAPACITY | AC1-204 |  |  | 1
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 73.43 |  |  | -0.00733 |  |  |  | 0 |  | 1 | NEW | P10 |  |  | 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 57.82 |  |  | -0.00733 |  |  |  | 0 |  | 1 | NEW | N15 |  |  | 1
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 13.2 |  |  | -0.00733 |  |  |  | 0 |  | 1 | CAPACITY | N15 |  |  | 1
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 4.91 |  |  | -0.00733 |  |  |  | 0 |  | 1 | CAPACITY | P10 |  |  | 1
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 69.62 |  |  | -0.00734 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 69.62 |  |  | -0.00734 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 46.55 |  |  | -0.00734 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 46.55 |  |  | -0.00734 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.00734 |  |  |  | 0 |  | 1 | NEW | AC1-145 |  |  | 1
925665 | AC1-042 E | 0.4 | 345 | 75 | 0 | 26.04 | 3.91 |  |  | -0.00734 |  |  |  | 0 |  | 1 | NEW | AC1-042 |  |  | 1
316217 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 2.85 |  |  | -0.00734 |  |  |  | 0 |  | 1 | CAPACITY | AC1-145 |  |  | 1
316197 | AC1-042 C | 0.4 | 345 | 75 | 0 | 15.96 | 2.39 |  |  | -0.00734 |  |  |  | 0 |  | 1 | CAPACITY | AC1-042 |  |  | 1
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 80.3 | 30.67 |  |  | -0.00734 |  |  |  | 0.036 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
276618 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 6.71 |  |  | -0.00734 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276660 | AB1-122 CT2 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | -0.00736 |  |  |  | 0 |  | 1 | CAPACITY | AB1-122 |  |  | 1
276658 | AB1-122 CT1 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | -0.00737 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-122 |  |  | 1
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 113.7 | 43.42 |  |  | -0.00736 |  |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | -0.00738 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | -0.00738 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00739 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00739 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00739 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00739 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00739 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00739 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 131.6 | 63.4 |  |  | -0.0074 |  |  |  | 0 |  | 1 | NEW | O22 2 |  |  | 1
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 114.9 | 55.36 |  |  | -0.0074 |  |  |  | 0 |  | 1 | NEW | O22 1 |  |  | 1
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 16.91 |  |  | -0.0074 |  |  |  | 0 |  | 1 | CAPACITY | O22 2 |  |  | 1
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 8.86 |  |  | -0.0074 |  |  |  | 0 |  | 1 | CAPACITY | O22 1 |  |  | 1
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | -0.0074 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | -0.0074 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 62.88 |  |  | -0.0074 |  |  |  | 0 |  | 1 | NEW | AA1-018 |  |  | 1
270839 | OTTER CRK; R | 345 | 222 | 74 | 0 | 19.5 | 9.4 |  |  | -0.0074 |  |  |  | 0 |  | 1 | CAPACITY | AA1-018 |  |  | 1
270205 | AE1-176 | 138 | 205 | 60 | 0 | 2.4 | 1.33 |  |  | -0.0074 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.00741 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00741 |  |  |  | 0.05 |  | 1 | MTX | Z1-106 |  |  | 1
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00741 |  |  |  | 0.0975 |  | 1 | MTX | Z1-106 |  |  | 1
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | -0.00743 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | -0.00743 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | -0.00743 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 45.87 |  |  | -0.00743 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 244.23 |  |  | -0.00745 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK7 |  |  | 1
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 90.5 | 104 | 39.72 |  |  | -0.00745 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 88.4 | 101.6 | 38.8 |  |  | -0.00745 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 87.5 | 100.6 | 38.42 |  |  | -0.00745 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 24 | 27.6 | 10.54 |  |  | -0.00745 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 10.1 | 6.78 |  |  | -0.00744 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 263.89 |  |  | -0.00746 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK8 |  |  | 1
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 38.5 |  |  | -0.00746 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | -0.00746 |  |  |  | 0 |  | 1 | NEW | O51 1 |  |  | 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | -0.00746 |  |  |  | 0 |  | 1 | NEW | O51 2 |  |  | 1
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | -0.00746 |  |  |  | 0 |  | 1 | CAPACITY | O51 1 |  |  | 1
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | -0.00746 |  |  |  | 0 |  | 1 | CAPACITY | O51 2 |  |  | 1
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1063 |  |  |  | -0.0075
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 63.01 |  |  | -0.00748 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | -0.00748 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | -0.00748 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 77.09 |  |  | -0.00748 |  |  |  | 0 |  | 1 | NEW | O50 |  |  | 1
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | -0.00748 |  |  |  | 0 |  | 1 | CAPACITY | O50 |  |  | 1
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00747 |  |  |  | 0.0975 |  | 1 | MTX | Z1-108 |  |  | 1
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 197.5 | 95.16 |  |  | -0.00752 |  |  |  | 0 |  | 1 | NEW | Q57 |  |  | 1
242587 | 05CELAN | 138 | 205 | 77 | 0 | 81.6 | 58.39 |  |  | -0.00751 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | -0.00752 |  |  |  | 0 |  | 1 | CAPACITY | Q57 |  |  | 1
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00753 |  |  |  | 0.0975 |  | 1 | MTX | AA2-123 |  |  | 1
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 83.83 |  |  | -0.00754 |  |  |  | 0 |  | 1 | NEW | Z2-087 |  |  | 1
924049 | AB2-047 E2 | 0.69 | 222 | 74 | 0 | 109.6 | 52.81 |  |  | -0.00754 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
924048 | AB2-047 E1 | 0.69 | 222 | 74 | 0 | 107.9 | 51.99 |  |  | -0.00754 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
270681 | BRIGHTSTK; R | 345 | 222 | 74 | 0 | 26 | 12.53 |  |  | -0.00754 |  |  |  | 0 |  | 1 | CAPACITY | Z2-087 |  |  | 1
276655 | AB2-047 C1 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | -0.00754 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
276656 | AB2-047 C2 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | -0.00754 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 42.21 |  |  | -0.00757 |  |  |  | 0 |  | 1 | NEW | P26 |  |  | 1
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 56 | 26.98 |  |  | -0.00757 |  |  |  | 0 |  | 1 | NEW | Z1-073 |  |  | 1
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 22.6 |  |  | -0.00757 |  |  |  | 0 |  | 1 | NEW | WestBrooklyn |  |  | 1
272363 | ESS H440 ; R | 138 | 222 | 2 | 0 | 22 | 0 |  |  | -0.00756 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 10.98 |  |  | -0.00757 |  |  |  | 0 |  | 1 | NEW | Sublette |  |  | 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 10.55 |  |  | -0.00757 |  |  |  | 0 |  | 1 | CAPACITY | P26 |  |  | 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 14.4 | 6.94 |  |  | -0.00757 |  |  |  | 0 |  | 1 | CAPACITY | Z1-073 |  |  | 1
276602 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 3.42 |  |  | -0.00757 |  |  |  | 0 |  | 1 | CAPACITY | WestBrooklyn |  |  | 1
276603 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 1.54 |  |  | -0.00757 |  |  |  | 0 |  | 1 | CAPACITY | Sublette |  |  | 1
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | -0.00757 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | -0.00757 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 156.6 | 180 | 68.74 |  |  | -0.00761 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 155.8 | 179.1 | 68.4 |  |  | -0.00761 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 154.7 | 177.8 | 67.9 |  |  | -0.00761 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 4.3 |  |  | -0.0076 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
341200 | 2BROMLEYEK | 69 | 320 | 77 | 0 | 2 | 1.35 |  |  | -0.00762 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
274656 | BYRON ;1U | 25 | 222 | 45 | 648.1 | 1168.5 | 1168.5 |  |  | -0.00762 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274657 | BYRON ;2U | 25 | 222 | 45 | 658.5 | 1141.5 | 1141.5 |  |  | -0.00762 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 163.2 | 78.63 |  |  | -0.00764 |  |  |  | 0 |  | 1 | NEW | S27 |  |  | 1
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 162.2 | 78.15 |  |  | -0.00764 |  |  |  | 0 |  | 1 | NEW | S28 |  |  | 1
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 32.9 |  |  |  | -0.0076
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 17.25 |  |  | -0.00764 |  |  |  | 0 |  | 1 | CAPACITY | S28 |  |  | 1
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 16.77 |  |  | -0.00764 |  |  |  | 0 |  | 1 | CAPACITY | S27 |  |  | 1
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.3 | 6.25 |  |  | -0.00763 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80.6 | 38.83 |  |  | -0.00764 |  |  |  | 0 |  | 1 | NEW | P46 |  |  | 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 9.35 |  |  | -0.00764 |  |  |  | 0 |  | 1 | CAPACITY | P46 |  |  | 1
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 28.52 |  |  | -0.00767 |  |  |  | 0 |  | 1 | NEW | O35 |  |  | 1
927209 | AC1-214 E2 | 0.69 | 222 | 74 | 0 | 55.15 | 26.57 |  |  | -0.00767 |  |  |  | 0 |  | 1 | NEW | AC1-214 2 |  |  | 1
916212 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 44.75 | 21.56 |  |  | -0.00767 |  |  |  | 0 |  | 1 | NEW | Z1-072 |  |  | 1
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 14.8 | 7.13 |  |  | -0.00767 |  |  |  | 0 |  | 1 | CAPACITY | O35 |  |  | 1
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 9.7 | 4.67 |  |  | -0.00767 |  |  |  | 0 |  | 1 | CAPACITY | Z1-072 |  |  | 1
276645 | AC1-214 C1 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | -0.00767 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 1 |  |  | 1
276646 | AC1-214 C2 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | -0.00767 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 2 |  |  | 1
927208 | AC1-214 E1 | 0.69 | 222 | 74 | 0 | 5.25 | 2.53 |  |  | -0.00767 |  |  |  | 0 |  | 1 | NEW | AC1-214 1 |  |  | 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | -0.00769 |  |  |  | 0 |  | 1 | NEW | P36 2 |  |  | 1
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | -0.00769 |  |  |  | 0 |  | 1 | NEW | P36 1 |  |  | 1
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 32.12 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | -0.00769 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | -0.00769 |  |  |  | 0 |  | 1 | CAPACITY | P36 1 |  |  | 1
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | -0.00769 |  |  |  | 0 |  | 1 | CAPACITY | P36 2 |  |  | 1
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 137 | 66.01 |  |  | -0.0077 |  |  |  | 0 |  | 1 | NEW | L05_CE22 |  |  | 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | -0.0077 |  |  |  | 0 |  | 1 | NEW | P11 1 |  |  | 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | -0.0077 |  |  |  | 0 |  | 1 | NEW | P11 2 |  |  | 1
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | -0.0077 |  |  |  | 0 |  | 1 | CAPACITY | P11 1 |  |  | 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | -0.0077 |  |  |  | 0 |  | 1 | CAPACITY | P11 2 |  |  | 1
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 13 | 6.26 |  |  | -0.0077 |  |  |  | 0 |  | 1 | CAPACITY | L05_CE22 |  |  | 1
293516 | O-009 E | 0.69 | 222 | 74 | 0 | 169.6 | 81.71 |  |  | -0.00773 |  |  |  | 0 |  | 1 | NEW | O09 |  |  | 1
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 42.26 |  |  | -0.00773 |  |  |  | 0 |  | 1 | NEW | O29 1 |  |  | 1
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 23.17 |  |  | -0.00773 |  |  |  | 0 |  | 1 | NEW | O29 2 |  |  | 1
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 21.3 |  |  | -0.00773 |  |  |  | 0 |  | 1 | NEW | O29 3 |  |  | 1
274881 | WALNUT RG;1U | 0.69 | 222 | 74 | 0 | 42.4 | 20.43 |  |  | -0.00773 |  |  |  | 0 |  | 1 | CAPACITY | O09 |  |  | 1
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 10.55 |  |  | -0.00773 |  |  |  | 0 |  | 1 | CAPACITY | O29 1 |  |  | 1
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 5.78 |  |  | -0.00773 |  |  |  | 0 |  | 1 | CAPACITY | O29 2 |  |  | 1
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 5.35 |  |  | -0.00773 |  |  |  | 0 |  | 1 | CAPACITY | O29 3 |  |  | 1
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 64.77 |  |  | -0.00774 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 64.28 |  |  | -0.00774 |  |  |  | 0.036 |  | 1 | CAPACITY | NELSON |  |  | 1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 47.32 |  |  | -0.00774 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 46.9 |  |  | -0.00774 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
276174 | W4-005 E | 0.69 | 222 | 74 | 0 | 260.4 | 125.46 |  |  | -0.00777 |  |  |  | 0 |  | 1 | NEW | W4-005 |  |  | 1
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 21.97 |  |  | -0.00777 |  |  |  | 0 |  | 1 | CAPACITY | W4-005 |  |  | 1
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | -0.00779 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | -0.0078 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 59.6 |  |  |  | -0.0078
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 89.13 |  |  | -0.00783 |  |  |  | 0 |  | 1 | NEW | X2-022 |  |  | 1
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 31.32 |  |  | -0.00783 |  |  |  | 0.1042 |  | 1 | NEW | W2-048 |  |  | 1
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 68.74 |  |  | -0.00792 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | -0.00792 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | -0.00792 |  |  |  | 0.036 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274663 | QUAD CITI;2U | 18 | 222 | 48 | 132 | 911.2 | 911.2 |  |  | -0.00792 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274662 | QUAD CITI;1U | 18 | 222 | 48 | 132 | 909.5 | 909.5 |  |  | -0.00792 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | -0.00794 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | -0.00794 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | -0.00795 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | -0.00795 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 42.01 |  |  | -0.00799 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 108.1 | 41.28 |  |  | -0.00799 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 106.7 | 40.75 |  |  | -0.00799 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 27.88 |  |  | -0.00799 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 70.9 | 27.08 |  |  | -0.00799 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.00799 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.00799 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 2.75 |  |  | -0.0082 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
936570 | AD2-072_C | 0.6 | 320 | 75 | 0 | 63.75 | 0 |  |  | -0.00823 |  |  |  | 0 |  | 1 | CAPACITY | AD2-072 |  |  | 1
936576 | AD2-072_E | 0.6 | 320 | 75 | 0 | 31.25 | 0 |  |  | -0.00823 |  |  |  | 0 |  | 1 | NEW | AD2-072 |  |  | 1
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0083
341329 | 2COLESBURG | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | -0.00835 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.0087
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 30.18 |  |  | -0.00882 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
270183 | AB2-010_C | 138 | 205 | 75 | 0 | 10 | 0.73 |  |  | -0.00882 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
270182 | AB2-011_C | 138 | 205 | 75 | 0 | 8 | 0.58 |  |  | -0.00882 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
270111 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 4.51 |  |  | -0.00882 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
923772 | AB2-011_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.00882 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
923762 | AB2-010_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.00882 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.2 | 27.3 |  |  | -0.00888 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00891 |  |  |  | 0.0789 |  | 1 | ENERGY |  |  |  | 1
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 12.2 | 6.77 |  |  | -0.00891 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.1 | 5.05 |  |  | -0.00891 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00891 |  |  |  | 0 |  | 1 | MTX | AD2-205 |  |  | 1
939134 | AE1-143 C | 0.64 | 320 | 75 | 0 | 64.14 | 4.68 |  |  | -0.00909 |  |  |  | 0 |  | 1 | CAPACITY | AE1-143 |  |  | 1
939135 | AE1-143 E | 0.64 | 320 | 75 | 0 | 31.86 | 2.33 |  |  | -0.00909 |  |  |  | 0 |  | 1 | NEW | AE1-143 |  |  | 1
342070 | 2PINE GROVE | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | -0.00913 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 93.75 |  |  | -0.00922 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG2 |  |  | 1
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 125.1 | 93.15 |  |  | -0.00922 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG1 |  |  | 1
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 38.84 |  |  | -0.00923 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 78.63 |  |  | -0.00922 |  |  |  | 0 |  | 1 | CAPACITY | CRG2 |  |  | 1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 104.7 | 77.96 |  |  | -0.00922 |  |  |  | 0 |  | 1 | CAPACITY | CRG1 |  |  | 1
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 610.3 |  |  | -0.00922 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 85.93 |  |  | -0.00938 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 44.3 |  |  | -0.00938 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | -0.00968 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | -0.00968 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.00968 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342442 | 2W GLASGOW | 69 | 320 | 77 | 0 | 1 | 0.67 |  |  | -0.00994 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 107.08 |  |  | -0.01032 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 105.41 |  |  | -0.01032 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 67.13 |  |  | -0.01032 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 41.06 |  |  | -0.01032 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 39.39 |  |  | -0.01032 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 1348 |  |  |  | -0.0106
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 18 |  |  |  | -0.0116
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 4.44 |  |  | -0.01182 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0124
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0125
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | -0.01388 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
270130 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0.56 |  |  | -0.01388 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
244012 | 05PINNACLE | 4 | 205 | 75 | 0 | 11 | 0.8 |  |  | -0.02113 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 682 |  |  |  | -0.0237
316222 | AC1-221 C | 0.6 | 345 | 75 | 0 | 51.2 | 7.68 |  |  | -0.02418 |  |  |  | 0 |  | 1 | CAPACITY | AC1-221 |  |  | 1
316283 | AC2-100 C | 0.57 | 345 | 75 | 0 | 45.6 | 6.84 |  |  | -0.02418 |  |  |  | 0 |  | 1 | CAPACITY | AC2-100 |  |  | 1
932763 | AC2-100 E | 0.57 | 345 | 75 | 0 | 16.4 | 2.46 |  |  | -0.02418 |  |  |  | 0 |  | 1 | NEW | AC2-100 |  |  | 1
927255 | AC1-221 E | 0.6 | 345 | 75 | 0 | 14.6 | 2.19 |  |  | -0.02418 |  |  |  | 0 |  | 1 | NEW | AC1-221 |  |  | 1
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 94.5 |  |  |  | -0.0307

## GD-W8
****** PJM Winter Generator Deliverability Detailed Report ****** PJM [TARA Ver 2101.1.0.0 64-bit - Mon Jun 21 18:04:02 2021]
FG Index [All Queue] | 8 | FG ID | 35 | Monitored Facility:324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1 / Contingency:EKPC_P2-3_COOP S42-1014_SRT-A[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
141 | 100.19 | 103.67 | AC | 138.83 | 0 | 0 | 2.44 | 0 | 141.27 | 146.2 | 0 | 0 | 12716.9 | 0 | 12716.9 | 0.05 | 0 | 0 | 0 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | FRMP | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited? | Ramping Limit
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00268 | 0.6913 | 0.6913 | 0
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00265 | 0.557 | 0.557 | 0
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.0026 | 0.1418 | 0.1418 | 0
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.3 |  | 173.3 | CLTF | 0.00243 | 0.4214 | 0.4214 | 0
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00208 | 0.1156 | 0.1156 | 0
MDU | PJM->LTFIMP_MDU |  |  | LTF |  | 10.1 |  | 10.1 | CLTF | 0.00192 | 0.0195 | 0.0195 | 0
TILTON | PJM->LTFIMP_TILTON |  |  | LTF |  | 63 |  | 63 | CLTF | 0.00163 | 0.1025 | 0.1025 | 0
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00062 | 0.031 | 0.031 | 0
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.0006 | 0.03 | 0.03 | 0
AF2-085 | BATEXP_AF2-085->PJM |  |  | LTF |  | 20 |  | 20 | LTF/CMTX | 0.00035 | 0.007 | 0.007 | 0
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  | 645 | LTF/CMTX | 0.00024 | 0.1563 | 0.1563 | 0
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  | 239.8 | LTF/CMTX | 0.00024 | 0.0583 | 0.0583 | 0
AD2-210 | BATEXP_AD2-210->PJM |  |  | LTF |  | 8 |  | 8 | LTF/CMTX | 0.00024 | 0.0019 | 0.0019 | 0
AA2-082 | BATEXP_AA2-082->PJM |  |  | LTF |  | 2 |  | 2 | LTF/CMTX | 0.00024 | 0.0005 | 0.0005 | 0
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 389 |  | 389 | LTF/CBM | 0.00022 | 0.0864 | 0.0864 | 0
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 94.5 |  | 94.5 | CLTF | 0.00016 | 0.0155 | 0.0155 | 0
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 682 |  | 682 | LTF/CBM | 1e-05 | 0.0047 | 0.0047 | 0
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 85.93 |  |  | 0.09275 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 38.84 |  |  | 0.06642 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
342070 | 2PINE GROVE | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | 0.03856 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 93.75 |  |  | 0.00417 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG2 |  |  | 1
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 125.1 | 93.15 |  |  | 0.00417 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG1 |  |  | 1
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 78.63 |  |  | 0.00417 |  |  |  | 0 |  | 1 | CAPACITY | CRG2 |  |  | 1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 104.7 | 77.96 |  |  | 0.00417 |  |  |  | 0 |  | 1 | CAPACITY | CRG1 |  |  | 1
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 610.3 |  |  | 0.00417 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00405 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00405 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | 0.00323 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | 0.00323 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | 0.00323 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270183 | AB2-010_C | 138 | 205 | 75 | 0 | 10 | 0.73 |  |  | 0.00257 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
270182 | AB2-011_C | 138 | 205 | 75 | 0 | 8 | 0.58 |  |  | 0.00257 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
923772 | AB2-011_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00257 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 1
923762 | AB2-010_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | 0.00257 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 1
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | 0.00233 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | 0.00233 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 30.18 |  |  | 0.00127 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
270111 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 4.51 |  |  | 0.00127 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 1
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 12.2 | 6.77 |  |  | 0.00122 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | 0.00123 |  |  |  | 0.0789 |  | 1 | ENERGY |  |  |  | 1
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.1 | 5.05 |  |  | 0.00122 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | 0.00122 |  |  |  | 0 |  | 1 | MTX | AD2-205 |  |  | 1
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 2.75 |  |  | 0.00104 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242587 | 05CELAN | 138 | 205 | 77 | 0 | 81.6 | 58.39 |  |  | 0.00104 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | 0.00099 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | 0.00099 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 4.44 |  |  | 0.00087 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 227.1 |  |  | 0.00085 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 2.4 | 1.61 |  |  | 0.00084 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270205 | AE1-176 | 138 | 205 | 60 | 0 | 2.4 | 1.33 |  |  | 0.00084 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00083 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
270130 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00083 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 1
270173 | AC1-122_C | 0.6 | 205 | 75 | 0 | 54.4 | 3.97 |  |  | 0.0008 |  |  |  | 0 |  | 1 | CAPACITY | AC1-122 |  |  | 1
926516 | AC1-122_E | 0.6 | 205 | 75 | 0 | 21.5 | 1.57 |  |  | 0.0008 |  |  |  | 0 |  | 1 | NEW | AC1-122 |  |  | 1
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 2.22 |  |  | 0.0008 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 107.08 |  |  | 0.00074 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 105.41 |  |  | 0.00074 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 67.13 |  |  | 0.00074 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 41.06 |  |  | 0.00074 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 39.39 |  |  | 0.00074 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.2 | 27.3 |  |  | 0.00072 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00071 |  |  |  | 0 |  | 1 | NEW | AC1-145 |  |  | 1
925665 | AC1-042 E | 0.4 | 345 | 75 | 0 | 26.04 | 3.91 |  |  | 0.00071 |  |  |  | 0 |  | 1 | NEW | AC1-042 |  |  | 1
316217 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 2.85 |  |  | 0.00071 |  |  |  | 0 |  | 1 | CAPACITY | AC1-145 |  |  | 1
316197 | AC1-042 C | 0.4 | 345 | 75 | 0 | 15.96 | 2.39 |  |  | 0.00071 |  |  |  | 0 |  | 1 | CAPACITY | AC1-042 |  |  | 1
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 52.4 |  |  | 0.00069 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 44.38 |  |  | 0.00068 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | 0.00066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | 0.00062 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 3.05 |  |  | 0.00061 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 29.06 |  |  | 0.00059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76 | 29.02 |  |  | 0.00059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 28.99 |  |  | 0.00059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 28.91 |  |  | 0.00059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 28.87 |  |  | 0.00059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 28.8 |  |  | 0.00059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244012 | 05PINNACLE | 4 | 205 | 75 | 0 | 11 | 0.8 |  |  | 0.00059 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247225 | 05FTHLG2 | 18 | 205 | 57 | 151.2 | 173.8 | 66.38 |  |  | 0.00058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247224 | 05FTHLG1 | 18 | 205 | 57 | 151.1 | 173.7 | 66.34 |  |  | 0.00058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247231 | 05RIVRG2 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247232 | 05RIVRG3 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | 0.00058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
314860 | 4E MILL | 138 | 345 | 77 | 0 | 50 | 0 |  |  | 0.00055 |  |  |  | 0 |  | 1 | NEWENERGY | Covington |  |  | 1
314859 | 4WSTVACO | 138 | 345 | 2 | 0 | 40.5 | 0 |  |  | 0.00055 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
909222 | X2-060 E | 138 | 345 | 64 | 0 | 30 | 0 |  |  | 0.00055 |  |  |  | 0 |  | 1 | ENERGY | Covington |  |  | 1
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 0.76 |  |  | 0.00055 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 0.75 |  |  | 0.00055 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
918234 | AA1-038_E | 0.69 | 345 | 74 | 0 | 66.7 | 66.03 |  |  | 0.00055 |  |  |  | 0 |  | 1 | NEW | AA1-038 |  |  | 1
315616 | AA1-038_C | 0.69 | 345 | 74 | 0 | 9.9 | 9.8 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | AA1-038 |  |  | 1
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 5.5 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 41.19 |  |  | 0.00055 |  |  |  | 0 |  | 1 | NEW | M24 |  |  | 1
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | 0.00055 |  |  |  | 0.0975 |  | 1 | MTX | M24 BAT |  |  | 1
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 21.15 |  |  | 0.00055 |  |  |  | 0 |  | 1 | NEW | AB1-150 |  |  | 1
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 7.23 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | M24 |  |  | 1
237033 | AB1-150 C | 138 | 201 | 74 | 0 | 7.3 | 3.52 |  |  | 0.00055 |  |  |  | 0 |  | 1 | CAPACITY | AB1-150 |  |  | 1
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 502.3 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 502.8 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 502.2 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 503.8 |  |  | 0.00054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 5.74 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-075 |  |  | 1
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 3.26 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-075 |  |  | 1
316205 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 1.92 |  |  | 0.00053 |  |  |  | 0 |  | 1 | CAPACITY | AC1-080 |  |  | 1
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | 0.00053 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 1.08 |  |  | 0.00053 |  |  |  | 0 |  | 1 | NEW | AC1-080 |  |  | 1
247622 | Y3-025 | 69 | 205 | 64 | 0 | 3.18 | 0 |  |  | 0.00051 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.14 |  |  | 0.00051 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316299 | AC2-112 C | 0.6 | 345 | 75 | 0 | 103.1 | 15.47 |  |  | 0.00048 |  |  |  | 0 |  | 1 | CAPACITY | AC2-112 |  |  | 1
932855 | AC2-112 E | 0.6 | 345 | 75 | 0 | 46.9 | 0 |  |  | 0.00048 |  |  |  | 0 |  | 1 | NEW | AC2-112 |  |  | 1
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | 0.00047 |  |  |  | 0 |  | 1 | MTX | AB1-055 |  |  | 1
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 8.21 |  |  | 0.00046 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 301.17 |  |  | 0.00044 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00044 |  |  |  | 0.036 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00044 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | 0.00044 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00045 |  |  |  | 0 |  | 1 | CAPACITY | AE1-098 |  |  | 1
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00045 |  |  |  | 0 |  | 1 | CAPACITY | AE1-099 |  |  | 1
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW | AE1-099 |  |  | 1
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00045 |  |  |  | 0 |  | 1 | NEW | AE1-098 |  |  | 1
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 1.17 |  |  | 0.00044 |  |  |  | 0 |  | 1 | NEW | AC1-116 |  |  | 1
316035 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 0.7 |  |  | 0.00044 |  |  |  | 0 |  | 1 | CAPACITY | AC1-116 |  |  | 1
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 1.46 |  |  | 0.00043 |  |  |  | 0 |  | 1 | NEW | AD1-085 |  |  | 1
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 54.8 | 40.8 |  |  | 0.00042 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 0.9 |  |  | 0.00043 |  |  |  | 0 |  | 1 | CAPACITY | AD1-085 |  |  | 1
316054 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | 0.00042 |  |  |  | 0 |  | 1 | CAPACITY | AC2-074 |  |  | 1
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0.79 |  |  | 0.00042 |  |  |  | 0 |  | 1 | NEW | AC2-074 |  |  | 1
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 0.72 |  |  | 0.00043 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.44 |  |  | 0.00043 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 800 |  |  | 0.00043 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 185.28 |  |  | 0.00042 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00042 |  |  |  | 0.036 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | 0.00042 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
316003 | AC1-222 C | 0.6 | 345 | 75 | 0 | 38.8 | 5.82 |  |  | 0.00042 |  |  |  | 0 |  | 1 | CAPACITY | AC1-222 |  |  | 1
927264 | AC1-222 E | 0.6 | 345 | 75 | 0 | 25.9 | 3.88 |  |  | 0.00042 |  |  |  | 0 |  | 1 | NEW | AC1-222 |  |  | 1
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 800 |  |  | 0.00041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1330 |  |  | 0.00041 |  |  |  | 0 |  | 1 | CAPACITY | AMG3 |  |  | 1
316051 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.0004 |  |  |  | 0 |  | 1 | CAPACITY | AC2-071 |  |  | 1
316322 | AB2-045 C | 230 | 345 | 75 | 0 | 11.43 | 1.72 |  |  | 0.0004 |  |  |  | 0 |  | 1 | CAPACITY | AB2-045 |  |  | 1
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.0004 |  |  |  | 0 |  | 1 | NEW | AC2-071 |  |  | 1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.0004 |  |  |  | 0 |  | 1 | NEW | AB2-045 |  |  | 1
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 5.18 |  |  | 0.00038 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 2.54 |  |  | 0.00038 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 1
316248 | AF1-058 C | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00039 |  |  |  | 0 |  | 1 | CAPACITY | AF1-058 |  |  | 1
943902 | AF1-058 E | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00039 |  |  |  | 0 |  | 1 | NEW | AF1-058 |  |  | 1
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00038 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 45.6 |  |  | 0.00038 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 118.52 |  |  | 0.00037 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00037 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00037 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | 0.00037 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 57.83 |  |  | 0.00037 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00037 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | 0.00037 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
316313 | AB2-026 C | 230 | 345 | 75 | 0 | 13.07 | 1.96 |  |  | 0.00038 |  |  |  | 0 |  | 1 | CAPACITY | AB2-026 |  |  | 1
316258 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00038 |  |  |  | 0 |  | 1 | CAPACITY | AE1-075 |  |  | 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00037 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | 0.00037 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
316074 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00037 |  |  |  | 0 |  | 1 | CAPACITY | AD1-157 |  |  | 1
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00038 |  |  |  | 0 |  | 1 | NEW | AB2-026 |  |  | 1
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 15.7 | 10.53 |  |  | 0.00037 |  |  |  | 0.1097 |  | 1 | CAPACITY | AMELIA LF_1-A |  |  | 1
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00037 |  |  |  | 0 |  | 1 | NEW | AD1-157 |  |  | 1
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0.88 |  |  | 0.00038 |  |  |  | 0 |  | 1 | NEW | AE1-075 |  |  | 1
313853 | 3PONTONDP | 115 | 345 | 65 | 0 | 4 | 0 |  |  | 0.00037 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 1.39 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AC1-036 |  |  | 1
316034 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 1.29 |  |  | 0.00036 |  |  |  | 0 |  | 1 | CAPACITY | AC1-036 |  |  | 1
342031 | 2PACTOLUS | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00035 |  |  |  | 0.036 |  | 1 | NEW | AC1-107 |  |  | 1
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316192 | AB2-158 C | 230 | 345 | 75 | 0 | 71 | 10.65 |  |  | 0.00036 |  |  |  | 0 |  | 1 | CAPACITY | AB2-158 |  |  | 1
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 8.16 |  |  | 0.00036 |  |  |  | 0 |  | 1 | CAPACITY | AB2-060 |  |  | 1
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-043 |  |  | 1
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 4.08 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-158 |  |  | 1
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 3.84 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-060 |  |  | 1
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 2.84 |  |  | 0.00036 |  |  |  | 0 |  | 1 | CAPACITY | AB2-043 |  |  | 1
316312 | AB1-027 C | 230 | 345 | 75 | 0 | 17.5 | 2.63 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AB1-027 |  |  | 1
316233 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AE1-074 |  |  | 1
316239 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
316237 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
316238 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
316004 | AC1-112 C | 230 | 345 | 75 | 0 | 10.9 | 1.63 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AC1-112 |  |  | 1
316050 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 1.38 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AC2-070 |  |  | 1
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 1
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 1
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00036 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 1
316303 | AF2-085 | 230 | 345 | 76 | 0 | 20 | 13.41 |  |  | 0.00035 |  |  |  | 0.05 |  | 1 | CAPACITY |  |  |  | 1
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 7.5 | 1.13 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AB1-027 |  |  | 1
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AE1-074 |  |  | 1
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0.92 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC1-112 |  |  | 1
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 7.38 |  |  | 0.00035 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0.57 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC2-070 |  |  | 1
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 4 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316169 | AC1-164 GEN | 0.44 | 345 | 75 | 192.1 | 220.8 | 33.12 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AC1-164 |  |  | 1
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 16.8 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AB2-190 |  |  | 1
926785 | AC1-164_E | 0.44 | 345 | 75 | 91 | 104.6 | 15.69 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC1-164 |  |  | 1
925672 | AC1-043 E | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 127.52 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
316201 | AC1-065 C | 0.39 | 345 | 75 | 0 | 49.4 | 7.41 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AC1-065 |  |  | 1
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 165.2 | 123.92 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 165.1 | 123.84 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 7.2 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AB2-190 |  |  | 1
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | 0.00034 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
313053 | 6PAPERMILL | 230 | 345 | 77 | 12 | 37 | 0 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
316254 | AC1-120 C | 0.6 | 345 | 75 | 0 | 39.6 | 5.94 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AC1-120 |  |  | 1
926004 | AC1-076_E | 0.6 | 345 | 75 | 0 | 39.42 | 5.91 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC1-076 |  |  | 1
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 98.04 |  |  | 0.00035 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316257 | AC1-043 C | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 1
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 96.46 |  |  | 0.00035 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 126.7 | 95.04 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 94.51 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 124.8 | 93.61 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC1-065 |  |  | 1
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.00035 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 4.56 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 1
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.00035 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
316280 | AD1-041 C | 0.55 | 345 | 75 | 0 | 30 | 4.5 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AD1-041 |  |  | 1
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 0.75 |  |  | 0.00034 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 0.72 |  |  | 0.00034 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 64.51 |  |  | 0.00035 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 64.43 |  |  | 0.00035 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 64.21 |  |  | 0.00035 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 64.14 |  |  | 0.00035 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00034 |  |  |  | 0.036 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
316164 | AC1-076_C | 0.6 | 345 | 75 | 0 | 23.8 | 3.57 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AC1-076 |  |  | 1
926486 | AC1-120 E | 0.6 | 345 | 75 | 0 | 20.4 | 3.06 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC1-120 |  |  | 1
934146 | AD1-041 E | 0.55 | 345 | 75 | 0 | 20 | 3 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AD1-041 |  |  | 1
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 49.66 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 45.01 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316304 | AE2-227 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AE2-227 |  |  | 1
316301 | AE2-228 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AE2-228 |  |  | 1
316170 | AC1-121 C | 0.6 | 345 | 75 | 0 | 13.6 | 2.04 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AC1-121 |  |  | 1
316159 | AE1-175 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AE1-175 |  |  | 1
316223 | AC1-118 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AC1-118 |  |  | 1
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 1.97 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AD2-030 |  |  | 1
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 12.7 | 1.9 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY | AC2-137 |  |  | 1
316240 | AF1-291 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AF1-291 |  |  | 1
316314 | AB2-024 C | 230 | 345 | 75 | 0 | 11.13 | 1.67 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AB2-024 |  |  | 1
942152 | AE2-227 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AE2-227 |  |  | 1
942162 | AE2-228 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AE2-228 |  |  | 1
315085 | 1SPRUNCC | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315086 | 1SPRUNCD | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | 0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316059 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AD1-063 |  |  | 1
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AC2-138 |  |  | 1
946262 | AF1-291 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AF1-291 |  |  | 1
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC2-137 |  |  | 1
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC1-118 |  |  | 1
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AD2-030 |  |  | 1
316160 | AE1-175 E | 230 | 345 | 75 | 0 | 6.6 | 0.99 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AE1-175 |  |  | 1
926502 | AC1-121 E | 0.6 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.00035 |  |  |  | 0 |  | 1 | NEW | AC1-121 |  |  | 1
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.1 | 10.8 |  |  | 0.00035 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHARLES CITY_LF |  |  | 1
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AB2-024 |  |  | 1
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AD1-063 |  |  | 1
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC2-138 |  |  | 1
961102 | AF2-401 E | 115 | 345 | 75 | 0 | 5.8 | 0.87 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AF2-401 |  |  | 1
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 9.99 |  |  | 0.00035 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHESTERFIELD LF_A |  |  | 1
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 6.71 |  |  | 0.00034 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
316302 | AF2-401 C | 115 | 345 | 75 | 0 | 3.52 | 0.53 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AF2-401 |  |  | 1
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 6.2 |  |  | 0.00035 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 20 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 437.1 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.2 | 441.2 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 52.8 | 52.8 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 787.1 | 23.61 |  |  | 0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316045 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 2 |  |  | 1
316044 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 1 |  |  | 1
316294 | AC1-161 C | 0.44 | 345 | 75 | 0 | 168.2 | 25.23 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC1-161 |  |  | 1
926755 | AC1-161 E | 0.44 | 345 | 75 | 0 | 71.8 | 0 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC1-161 |  |  | 1
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC1-158 1 |  |  | 1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC1-158 2 |  |  | 1
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 10.77 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AB2-134 |  |  | 1
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 10.59 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AB2-134 |  |  | 1
932596 | AC2-079 E | 0.64 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC2-079 |  |  | 1
316222 | AC1-221 C | 0.6 | 345 | 75 | 0 | 51.2 | 7.68 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC1-221 |  |  | 1
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 170 | 127.52 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | 0.00034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 120.47 |  |  | 0.00034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 120.09 |  |  | 0.00034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 119.87 |  |  | 0.00034 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316283 | AC2-100 C | 0.57 | 345 | 75 | 0 | 45.6 | 6.84 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC2-100 |  |  | 1
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 113.79 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.1 | 113.34 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 112.29 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316185 | AD1-033 C | 0.6 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AD1-033 |  |  | 1
316267 | AC1-143 C | 0.38 | 345 | 75 | 0 | 41.2 | 6.18 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AC1-143 |  |  | 1
932586 | AC2-078 E | 0.64 | 345 | 75 | 0 | 37.2 | 5.58 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC2-078 |  |  | 1
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 0.89 |  |  | 0.00034 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 83.11 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316311 | AC2-079 C | 0.64 | 345 | 75 | 0 | 32.3 | 4.84 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC2-079 |  |  | 1
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 82.06 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 80.64 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
315099 | 1CHESPKB | 13.8 | 345 | 20 | 0 | 24.7 | 0 |  |  | 0.00033 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
934065 | AD1-033 E | 0.6 | 345 | 75 | 0 | 28 | 4.2 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AD1-033 |  |  | 1
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 65.18 |  |  | 0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 65.11 |  |  | 0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | 0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316289 | AC2-078 C | 0.64 | 345 | 75 | 0 | 22.8 | 3.42 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AC2-078 |  |  | 1
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 2.85 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 1
926615 | AC1-143 E | 0.38 | 345 | 75 | 0 | 18.8 | 2.82 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AC1-143 |  |  | 1
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 0.45 |  |  | 0.00033 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
932763 | AC2-100 E | 0.57 | 345 | 75 | 0 | 16.4 | 2.46 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC2-100 |  |  | 1
927255 | AC1-221 E | 0.6 | 345 | 75 | 0 | 14.6 | 2.19 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC1-221 |  |  | 1
316234 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AE1-124 |  |  | 1
316241 | AE2-078 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AE2-078 |  |  | 1
316247 | AF1-033 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AF1-033 |  |  | 1
316242 | AE2-079 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AE2-079 |  |  | 1
316036 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC1-147 |  |  | 1
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 1.83 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AB2-029 |  |  | 1
316236 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY | AE1-162 |  |  | 1
316316 | AC1-027 C | 115 | 345 | 75 | 0 | 11.2 | 1.68 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC1-027 |  |  | 1
316057 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC2-196 |  |  | 1
316150 | AD2-215 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AD2-215 |  |  | 1
316072 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 1.46 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AD1-144 |  |  | 1
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AE1-162 |  |  | 1
316006 | AB2-029 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AB2-029 |  |  | 1
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC1-147 |  |  | 1
943622 | AF1-033 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AF1-033 |  |  | 1
940892 | AE2-078 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AE2-078 |  |  | 1
940902 | AE2-079 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AE2-079 |  |  | 1
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00034 |  |  |  | 0 |  | 1 | NEW | AE1-124 |  |  | 1
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 1 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC2-196 |  |  | 1
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC1-027 |  |  | 1
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AD1-144 |  |  | 1
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AD2-215 |  |  | 1
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 7.56 |  |  | 0.00033 |  |  |  | 0.1097 |  | 1 | CAPACITY | VIRGINIA BEACH LF_A |  |  | 1
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 10.4 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | Z1-068 |  |  | 1
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.49 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | Z1-068 |  |  | 1
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 4.5 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 15 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 843.5 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 844.6 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 948.5 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 948.9 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 8.7 |  |  | 0.00034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 11 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 12.9 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 11.9 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 15.2 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 2 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 11.81 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AA1-139 |  |  | 1
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 7.5 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AB2-015 |  |  | 1
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00033 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | 0.00033 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 120.39 |  |  | 0.00033 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 6.68 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AC1-054 |  |  | 1
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | 0.00032 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 6.15 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AB2-015 |  |  | 1
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AA1-139 |  |  | 1
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 3.08 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AC1-054 |  |  | 1
316321 | Z2-027 C | 230 | 345 | 75 | 0 | 13.8 | 2.07 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | Z2-027 |  |  | 1
316315 | AB2-025 C | 230 | 345 | 75 | 0 | 13.65 | 2.05 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AB2-025 |  |  | 1
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 1.95 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AB2-022 |  |  | 1
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 1.86 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | Y1-086 |  |  | 1
316244 | AE2-225 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AE2-225 |  |  | 1
316305 | AF2-043 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AF2-043 |  |  | 1
316246 | AF1-032 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AF1-032 |  |  | 1
316245 | AE2-229 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | AE2-229 |  |  | 1
942132 | AE2-225 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AE2-225 |  |  | 1
957492 | AF2-043 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AF2-043 |  |  | 1
316320 | Y1-086 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY | Y1-086 |  |  | 1
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 1.05 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AB2-022 |  |  | 1
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | Z2-030 |  |  | 1
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AB2-025 |  |  | 1
942172 | AE2-229 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AE2-229 |  |  | 1
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | Z2-027 |  |  | 1
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 10.06 |  |  | 0.00033 |  |  |  | 0.44065 |  | 1 | CAPACITY |  |  |  | 1
943612 | AF1-032 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW | AF1-032 |  |  | 1
961092 | AF2-400 E | 115 | 345 | 75 | 0 | 4.43 | 0.66 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | af2-400 |  |  | 1
237077 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 1
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | Z2-030 |  |  | 1
314541 | 3WATKINS | 115 | 345 | 75 | 0 | 4 | 0.6 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 258.69 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | 0.00032 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
316300 | AF2-400 C | 115 | 345 | 75 | 0 | 2.71 | 0.41 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AF2-400 |  |  | 1
901082 | W1-029 E | 230 | 345 | 74 | 0 | 169 | 167.31 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | W1-029 |  |  | 1
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 0.76 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 1.07 | 0.16 |  |  | 0.00033 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | W1-029 |  |  | 1
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 1
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.39 |  |  | 0.00033 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53 | 53 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 113.58 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.1 | 113.46 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 448.57 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 422.31 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 395.08 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 108.79 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | K11 |  |  | 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | 0.00031 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | 0.00031 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00032 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00032 |  |  |  | 0.036 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00032 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 188.28 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
923994 | AB2-040_E | 0.6 | 345 | 75 | 0 | 69.51 | 10.43 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AB2-040 |  |  | 1
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AA2-088 |  |  | 1
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 8.4 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | AA2-178 |  |  | 1
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 8.22 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | AA2-053 |  |  | 1
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 7.64 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | AA1-063A |  |  | 1
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | 0.00032 |  |  |  | 0.036 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 6.3 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AB2-174 |  |  | 1
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 1.07 |  |  | 0.00032 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 1.07 |  |  | 0.00032 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 6.06 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AB1-173 |  |  | 1
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AB2-174 |  |  | 1
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AA2-088 |  |  | 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 2 |  |  | 1
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 1 |  |  | 1
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AA1-063A |  |  | 1
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AA2-178 |  |  | 1
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 18.41 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | K11 |  |  | 1
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 3.38 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AA2-053 |  |  | 1
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AB2-100 1 |  |  | 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AB2-100 2 |  |  | 1
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 0.36 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316052 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AC2-072 |  |  | 1
316181 | AB2-040 GEN | 0.6 | 345 | 75 | 0 | 12 | 1.8 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY | AB2-040 |  |  | 1
314088 | 6VANDORN | 230 | 345 | 1 | 7 | 21 | 14.08 |  |  | 0.00032 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AC2-072 |  |  | 1
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | 0.00032 |  |  |  | 0 |  | 1 | NEW | AB1-173 |  |  | 1
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 1.87 |  |  | 0.00031 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316318 | V4-068 C | 115 | 345 | 75 | 0 | 3.2 | 0.48 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | V4-068 |  |  | 1
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0.27 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | V4-068 |  |  | 1
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | 0.00032 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 48 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 50.3 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1407 | 1407 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | GVG2 |  |  | 1
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1389 | 1389 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | GVG1 |  |  | 1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1308.8 | 1308.8 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | MTG1 |  |  | 1
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 553 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM2 |  |  | 1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 522.9 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 327.3 | 176.05 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | 0.0003 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-035 |  |  | 1
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 229.53 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
316011 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 12.6 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 1
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 67 | 10.05 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AA1-065 |  |  | 1
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00031 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-039 |  |  | 1
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 43.03 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.0003 |  |  |  | 0.036 |  | 1 | CAPACITY | PANDA |  |  | 1
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 1
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 25.52 |  |  | 0.0003 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AA1-065 |  |  | 1
226704 | AOCX4-046 E | 13.8 | 233 | 58 | 0 | 19.5 | 0 |  |  | 0.0003 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 74.1 | 55.58 |  |  | 0.0003 |  |  |  | 0.036 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 37.51 |  |  | 0.0003 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 45.9 | 34.43 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
316317 | KELFORD C | 115 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | Z2-043 |  |  | 1
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 34.7 | 26.03 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
917332 | KELFORD E | 115 | 345 | 75 | 0 | 7 | 1.05 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | Z2-043 |  |  | 1
316243 | AE2-151 C | 115 | 345 | 75 | 0 | 6.5 | 0.98 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | AE2-151 |  |  | 1
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
941542 | AE2-151 E | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AE2-151 |  |  | 1
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0.22 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 1
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 81.18 |  |  | 0.00031 |  |  |  | 0 |  | 1 | NEW | T157 |  |  | 1
226924 | AE1-015 E | 69 | 233 | 75 | 0 | 0.75 | 0.07 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AE1-015 |  |  | 1
226923 | AE1-015 C | 69 | 233 | 75 | 0 | 0.57 | 0.05 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AE1-015 |  |  | 1
226922 | AE1-013 E | 69 | 233 | 75 | 0 | 0.5 | 0.05 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AE1-013 |  |  | 1
226921 | AE1-013 C | 69 | 233 | 75 | 0 | 0.38 | 0.04 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AE1-013 |  |  | 1
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 20.3 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | T157 |  |  | 1
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 548.2 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM1 |  |  | 1
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | 0.00031 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 11.01 |  |  | 0.0003 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 10.83 |  |  | 0.0003 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 182.23 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | 0.0003 |  |  |  | 0.036 |  | 1 | CAPACITY | WALDORF |  |  | 1
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316274 | AC1-208 C | 0.38 | 345 | 75 | 0 | 55.4 | 8.31 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AC1-208 |  |  | 1
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 3.62 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
316327 | AA2-057 C | 0.63 | 345 | 75 | 0 | 50 | 7.5 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY | AA2-057 |  |  | 1
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227024 | SMECOCT | 13.8 | 238 | 57 | 0 | 80.2 | 43.14 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316174 | AB2-169_C | 0.63 | 345 | 75 | 0 | 39 | 5.85 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY | AB2-169 |  |  | 1
316210 | AC1-098 C | 0.6 | 345 | 75 | 0 | 37.6 | 5.64 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AC1-098 |  |  | 1
925122 | AB2-169 E | 0.63 | 345 | 75 | 0 | 35 | 5.25 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AB2-169 |  |  | 1
237026 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 2.22 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 1
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
927146 | AC1-208 E | 0.38 | 345 | 75 | 0 | 24.5 | 0 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AC1-208 |  |  | 1
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00029 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
919710 | AA2-057 E | 0.63 | 345 | 75 | 0 | 24.9 | 3.73 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AA2-057 |  |  | 1
926206 | AC1-098 E | 0.6 | 345 | 75 | 0 | 22.4 | 3.36 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AC1-098 |  |  | 1
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 1.86 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AC2-101 |  |  | 1
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 0.33 |  |  | 0.0003 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 1.58 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AC2-120 |  |  | 1
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 13.12 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227282 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 1.14 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AC2-101 |  |  | 1
316212 | AC1-099 C | 0.6 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AC1-099 |  |  | 1
227280 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 0.97 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AC2-120 |  |  | 1
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 9.68 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | 0.0003 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
926214 | AC1-099 E | 0.6 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AC1-099 |  |  | 1
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0.16 |  |  | 0.0003 |  |  |  | 0 |  | 1 | NEW | AB2-157 |  |  | 1
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 1.44 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226910 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.07 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY | AB2-157 |  |  | 1
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.91 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.87 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226920 | AE1-012 E | 115 | 233 | 75 | 0 | 0.34 | 0.03 |  |  | 0.00029 |  |  |  | 0 |  | 1 | NEW | AE1-012 |  |  | 1
226919 | AE1-012 C | 115 | 233 | 75 | 0 | 0.22 | 0.02 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY | AE1-012 |  |  | 1
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 613.3 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 619.4 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 52 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 841.8 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 866 |  |  | 0.0003 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 41.39 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | P59 |  |  | 1
223967 | METZ E69 | 69 | 233 | 56 | 0 | 20 | 0 |  |  | 0.00029 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
923213 | AB1-125_E | 0.6 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB1-125 |  |  | 1
316319 | Z2-044 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | Z2-044 |  |  | 1
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 5.64 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | P59 |  |  | 1
237006 | AB1-125_C | 0.6 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AB1-125 |  |  | 1
226895 | WOAKV2-037 E | 69 | 233 | 29 | 0 | 4.5 | 0 |  |  | 0.00029 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0.54 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | Z2-044 |  |  | 1
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.64 |  |  | 0.00029 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 7.34 |  |  | 0.00028 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 139.8 | 75.19 |  |  | 0.00027 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 68.9 |  |  | 0.00028 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315131 | 1EDGECMA | 13.8 | 345 | 11 | 7.5 | 58 | 0 |  |  | 0.00028 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 9.9 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AB2-059 |  |  | 1
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 61.1 |  |  | 0.00027 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 55.94 |  |  | 0.00027 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316049 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 8.4 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AB1-081 |  |  | 1
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | Z2-088 |  |  | 1
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | Z2-088 |  |  | 1
316263 | AC1-034 C | 0.55 | 345 | 75 | 0 | 42.75 | 6.41 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AC1-034 |  |  | 1
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 36.56 |  |  | 0.00027 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 5.1 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB2-059 |  |  | 1
925595 | AC1-034 E | 0.55 | 345 | 75 | 0 | 32.25 | 4.84 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AC1-034 |  |  | 1
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 27.97 |  |  | 0.00027 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB1-081 |  |  | 1
237037 | AE1-188 C | 34.5 | 201 | 75 | 0 | 20.5 | 1.5 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AE1-188 |  |  | 1
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 289.09 |  |  | 0.00028 |  |  |  | 0.1042 |  | 1 | CAPACITY | Wagner3 |  |  | 1
220904 | CRANE G2 | 20 | 232 | 12 | 0 | 14 | 0 |  |  | 0.00027 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.2 | 16.24 |  |  | 0.00028 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 29.8 | 16.03 |  |  | 0.00028 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | W4-102 |  |  | 1
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AB1-128 |  |  | 1
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AB1-127 |  |  | 1
237038 | AE2-054 C | 34.5 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
939592 | AE1-188 E | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AE1-188 |  |  | 1
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.00028 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
237003 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0.76 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0.73 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AB2-097 |  |  | 1
316005 | AA1-067 C | 230 | 345 | 75 | 0 | 10.5 | 1.58 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AA1-067 |  |  | 1
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 1
235043 | AF1-166 C | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AF1-166 |  |  | 1
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AD1-060 |  |  | 1
223402 | AF1-300 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AF1-300 |  |  | 1
223401 | AF1-299 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AF1-299 |  |  | 1
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0.63 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | W1-116 |  |  | 1
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AA1-092 |  |  | 1
940672 | AE2-054 E | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 1
946362 | AF1-300 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AF1-300 |  |  | 1
946352 | AF1-299 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AF1-299 |  |  | 1
237025 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 1
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | W4-102 |  |  | 1
237002 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AB1-128 |  |  | 1
237001 | AB1-127 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AB1-127 |  |  | 1
237024 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0.51 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 1
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 7.15 |  |  | 0.00028 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
945012 | AF1-166 E | 34.5 | 201 | 75 | 0 | 6.4 | 0.47 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AF1-166 |  |  | 1
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0.46 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AC2-136 |  |  | 1
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0.44 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AB1-096 |  |  | 1
237080 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AD1-060 |  |  | 1
237034 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 0.4 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY | AC2-136 |  |  | 1
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 0.39 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | W1-116 |  |  | 1
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 10.07 |  |  | 0.00027 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AA1-109 |  |  | 1
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AA1-109 |  |  | 1
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0.68 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AA1-067 |  |  | 1
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AA1-092 |  |  | 1
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0.24 |  |  | 0.00028 |  |  |  | 0 |  | 1 | NEW | AA1-095 |  |  | 1
237030 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 0.23 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AB1-096 |  |  | 1
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 0.21 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY | AA1-095 |  |  | 1
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00028 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.4 |  |  | 0.00027 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.61 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 638.9 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 642.7 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 57 |  |  | 0.00028 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 2.01 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00027 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | 0.00027 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 1.23 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 1
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 19.81 |  |  | 0.00027 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00027 |  |  |  | 0 |  | 1 | NEW | AA2-072 |  |  | 1
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 247.42 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 205.47 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 171.69 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 63.89 |  |  | 0.00026 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 63.82 |  |  | 0.00026 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00026 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00026 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | 0.00026 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 103.81 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00025 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | 0.00025 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00025 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | 0.00025 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
200055 | ROCKSP 4 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200054 | ROCKSP 3 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200052 | ROCKSP 1 | 18 | 235 | 57 | 145.7 | 167.5 | 90.09 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 89.82 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200053 | ROCKSP 2 | 18 | 235 | 57 | 144.9 | 166.5 | 89.56 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 55.94 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | U2-073 A |  |  | 1
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA |  |  | 1
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
205916 | AD1-020_C | 0.6 | 227 | 75 | 0 | 54 | 4.99 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 134.03 |  |  | 0.00026 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 93.64 |  |  | 0.00026 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 80.49 |  |  | 0.00025 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
916000 | 01BACKB E | 34.5 | 201 | 74 | 0 | 57.9 | 27.9 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | K19 |  |  | 1
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 64 | 34.42 |  |  | 0.00025 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 26.98 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | S14 |  |  | 1
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 68.19 |  |  | 0.00025 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 67.49 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 24.52 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | U2-073 B |  |  | 1
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
916001 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 44.5 | 21.44 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | N47 |  |  | 1
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 53.78 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 20.96 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | U2-061 |  |  | 1
237013 | AA2-103 E | 0.48 | 201 | 76 | 0 | 20 | 0 |  |  | 0.00026 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
205917 | AD1-020 ES | 0.55 | 227 | 75 | 0 | 21.5 | 1.99 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 1
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 45.34 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 44.99 |  |  | 0.00025 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 40.5 | 21.78 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
208904 | HOLT 696 | 13.2 | 229 | 60 | 16 | 58.4 | 41.06 |  |  | 0.00026 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208903 | HOLT 695 | 13.2 | 229 | 60 | 19 | 53.2 | 37.4 |  |  | 0.00026 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 33.74 |  |  | 0.00025 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | 0.00026 |  |  |  | 0.0975 |  | 1 | MTX | AA1-100 |  |  | 1
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 20.6 | 11.08 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 20.5 | 11.03 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0.77 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W1-045 |  |  | 1
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 14.6 | 7.03 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 A |  |  | 1
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 6.74 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | S14 |  |  | 1
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 1
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 5.16 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | N47 |  |  | 1
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.1 | 0.47 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W1-045 |  |  | 1
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 0.45 |  |  | 0.00026 |  |  |  | 0 |  | 1 | CAPACITY | V4-027 |  |  | 1
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 8.4 | 4.05 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 B |  |  | 1
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 3.9 |  |  | 0.00026 |  |  |  | 0 |  | 1 | CAPACITY | K19 |  |  | 1
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 3.13 |  |  | 0.00026 |  |  |  | 0 |  | 1 | CAPACITY | U2-061 |  |  | 1
209030 | FRFA O01 | 12.5 | 229 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208254 | AF2-280 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | AF2-280 |  |  | 1
208527 | AF2-279 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AF2-279 |  |  | 1
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 33.02 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | P.H. GLATFELTER_IPP |  |  | 1
205922 | AF2-268 E | 115 | 227 | 75 | 0 | 2 | 0.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
205920 | AF2-101 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AF2-101 |  |  | 1
205921 | AF2-151 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AF2-151 |  |  | 1
208769 | SISO | 12.5 | 229 | 2 | 2.5 | 1.6 | 0 |  |  | 0.00026 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
208474 | KINZ 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208876 | WLAN | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
958072 | AF2-101 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AF2-101 |  |  | 1
958602 | AF2-151 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AF2-151 |  |  | 1
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.77 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 2 | 1.22 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V3-051 |  |  | 1
208253 | AF2-280 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00026 |  |  |  | 0 |  | 1 | MTX | AF2-280 |  |  | 1
208526 | AF2-279 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | MTX | AF2-279 |  |  | 1
916007 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 0.1 | 0.06 |  |  | 0.00026 |  |  |  | 0 |  | 1 | NEW | V4-027 |  |  | 1
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1288.2 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1307 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 0 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | NEW |  |  |  | 1
237068 | AA2-119 GEN | 20.5 | 201 | 58 | 0 | 600 | 0 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | NEW | Harrison |  |  | 1
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | NEW | Garrison |  |  | 1
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 8.32 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 260.87 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 181.64 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 2.83 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
219001 | SEWAREN7GT | 25 | 231 | 58 | 0 | 324.6 | 174.59 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 164.59 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 302.3 | 162.6 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 302.1 | 162.49 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
990902 | TOSCO_E | 18 | 231 | 2 | 0 | 137.5 | 0 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | ENERGY | Tosco |  |  | 1
213893 | PHLISST1 | 20 | 230 | 58 | 232.3 | 267 | 143.61 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
204662 | 27AES GEN1 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204663 | 27AES GEN2 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204664 | 27AES GEN3 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 139.31 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 256.8 | 138.13 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 137.8 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 135.65 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 133.39 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 128.98 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 222.4 | 119.62 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
219002 | SEWAREN7ST | 18 | 231 | 58 | 0 | 216.4 | 116.4 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 113.38 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Q90 |  |  | 1
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 107.57 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 107.57 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH5678 |  |  | 1
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 103.81 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 102.41 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 102.41 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 102.2 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 99.67 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 8.6 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AA1-102 |  |  | 1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 96.22 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 96.22 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 94.67 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | RED OAK |  |  | 1
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 93.75 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 87.67 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | GRAYS FERRY |  |  | 1
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 111.97 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB1-056 |  |  | 1
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 153 | 82.29 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 1.28 |  |  | 0.00025 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 140.5 | 75.57 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
200044 | BETH CT1 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200048 | BETH CT5 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 62.5 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 99.6 | 114.5 | 61.59 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 5.27 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AA1-102 |  |  | 1
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 93.2 | 107.1 | 57.61 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 91.3 | 105 | 56.48 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 89.6 | 103 | 55.4 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | GILBERT |  |  | 1
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206327 | 28S RIV G1 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | S RIV |  |  | 1
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 85.3 | 98 | 52.71 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 0.83 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232915 | OH NUG4 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 50.99 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206341 | 28GIL 8 | 13.8 | 228 | 58 | 82.2 | 94.5 | 50.83 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 0.82 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228203 | P06 | 13.8 | 234 | 57 | 78 | 89.7 | 48.25 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 76.9 | 88.4 | 47.55 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 45.99 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 45.24 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 45.13 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 72.1 | 82.9 | 44.59 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 43.57 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 43.08 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
227801 | ONTC&DCT | 13.8 | 234 | 75 | 33.6 | 38.6 | 3.57 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
233935 | AB2-179 C | 0.38 | 235 | 75 | 0 | 37.6 | 3.48 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB2-179 |  |  | 1
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 38.35 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 28.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 35.07 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 34.26 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
924802 | AB2-133 E | 69 | 235 | 75 | 0 | 31.2 | 2.89 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB2-133 |  |  | 1
208947 | WSHO CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 25.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | U2-030 |  |  | 1
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 57.7 | 31.03 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 57.6 | 30.98 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 30.66 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 30.66 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 29.85 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 29.58 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 29.23 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 29.23 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
233906 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 39.32 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB1-056 |  |  | 1
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00025 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | 0.00025 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 388.63 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233939 | AB2-133 C | 69 | 235 | 75 | 0 | 24.6 | 2.28 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB2-133 |  |  | 1
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 25.82 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 25.82 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232901 | NORTHST | 69 | 235 | 56 | 5 | 45 | 24.2 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 345.42 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris2 |  |  | 1
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
207466 | AF1-324 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00024 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207470 | AF1-327 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00024 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207468 | AF1-326 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.00024 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218344 | TOSCO_G6 | 18 | 231 | 2 | 37 | 42.5 | 22.86 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY | Tosco |  |  | 1
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 22.59 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
213798 | MERCK 3 | 13.8 | 230 | 29 | 13 | 42 | 22.59 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 41.2 | 22.16 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
208942 | HARR CT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.1 | 39.2 | 21.08 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 20.98 |  |  | 0.00025 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
207403 | 28AA2-082 E | 34.5 | 228 | 76 | -18 | 18 | 0 |  |  | 0.00024 |  |  |  | 0.05 |  | 1 | MTX | AA2-082 |  |  | 1
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 291.92 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris1 |  |  | 1
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 20.22 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204651 | 27PORT CT | 13.8 | 227 | 55 | 4 | 37 | 19.9 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
207179 | 28SIXFLAGS | 34.5 | 228 | 77 | 0 | 17 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 18.4 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 18.29 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 18.29 |  |  | 0.00024 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 32.1 | 17.27 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213797 | MERCK 2 | 13.8 | 230 | 29 | 4 | 32 | 17.21 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 16.67 |  |  | 0.00024 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 16.14 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 16.08 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 226.44 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 11.56 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 1
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 206.63 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
233930 | AB2-032 GEN | 0.6 | 235 | 75 | 0 | 13.6 | 1.26 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB2-032 |  |  | 1
232905 | CHERITON_25 | 24.9 | 235 | 65 | 0 | 12.5 | 0.23 |  |  | 0.00025 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB1-141 |  |  | 1
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB1-142 |  |  | 1
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 25.21 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W1-003 |  |  | 1
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W1-004 |  |  | 1
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W1-005 |  |  | 1
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W1-006 |  |  | 1
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | 0.00025 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
228357 | V2-046E | 12.9 | 234 | 75 | 0 | 12.9 | 1.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V2-046 |  |  | 1
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | 0.00025 |  |  |  | 0.1097 |  | 1 | ENERGY |  |  |  | 1
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB2-179 |  |  | 1
923925 | AB2-153 E | 0.6 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB2-153 |  |  | 1
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | X3-008 |  |  | 1
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W1-003 |  |  | 1
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W1-005 |  |  | 1
917082 | Z2-012 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Z2-012 |  |  | 1
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W1-006 |  |  | 1
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W1-004 |  |  | 1
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W3-080 |  |  | 1
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 1.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W3-044 |  |  | 1
206747 | 28DSM_X3-029 | 34.5 | 228 | 58 | 0 | 11.15 | 0 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
207462 | AF1-133 C | 34.5 | 228 | 75 | 0 | 12 | 1.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AF1-133 |  |  | 1
939122 | AE1-142 E O1 | 34.5 | 228 | 75 | 0 | 11.8 | 1.09 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE1-142 |  |  | 1
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.1 | 12.43 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 12.37 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 12.32 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
207454 | AA2-184 E | 34.5 | 228 | 75 | 0 | 11.6 | 1.07 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | BenMoreell |  |  | 1
218780 | PRINCENTON_U | 26 | 231 | 77 | 0 | 31.56 | 21.27 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
228471 | VALERO1 | 13.8 | 234 | 58 | 19.1 | 22 | 11.83 |  |  | 0.00025 |  |  |  | 0.036 |  | 1 | CAPACITY | Valero |  |  | 1
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 164.17 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0.98 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X1-037 |  |  | 1
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-082 |  |  | 1
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-124 |  |  | 1
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W3-029 |  |  | 1
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-073 |  |  | 1
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0.93 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W3-003 |  |  | 1
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.3 | 8.34 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | K28 |  |  | 1
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Y3-058 |  |  | 1
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-016 |  |  | 1
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W3-077 |  |  | 1
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 9.57 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 8.9 | 0.82 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y3-058 |  |  | 1
218672 | KENILWRTH E | 26.4 | 231 | 65 | 0 | 8 | 0 |  |  | 0.00024 |  |  |  | 0.1097 |  | 1 | NEW |  |  |  | 1
207458 | AD2-210_C | 34.5 | 228 | 76 | 0 | 8 | 0 |  |  | 0.00024 |  |  |  | 0.05 |  | 1 | NEW |  |  |  | 1
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | 0.00024 |  |  |  | 0.0975 |  | 1 | MTX | AA2-061 |  |  | 1
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 9.25 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 16.18 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | 0.00025 |  |  |  | 0.30476 |  | 1 | ENERGY |  |  |  | 1
207464 | AF1-023 | 34.5 | 228 | 75 | 0 | 8.4 | 0.78 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BenMoreell |  |  | 1
219913 | AD2-042 E | 26.4 | 231 | 75 | 0 | 8.2 | 0.76 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AD2-042 |  |  | 1
207459 | AE1-142 C O1 | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AE1-142 |  |  | 1
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AC1-207 |  |  | 1
232920 | IR10 | 13.2 | 235 | 55 | 14 | 16.1 | 8.66 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0.75 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | Z2-102 |  |  | 1
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-050 |  |  | 1
944682 | AF1-133 E | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF1-133 |  |  | 1
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 0.72 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | V2-046 |  |  | 1
207451 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | 0.00024 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
233933 | AB2-153 GEN | 0.6 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB2-153 |  |  | 1
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | X3-008 |  |  | 1
233901 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Z2-012 |  |  | 1
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 0.7 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W3-044 |  |  | 1
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232919 | VN10 | 13.2 | 235 | 55 | 0 | 14.3 | 7.69 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 7.64 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0.63 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W2-056 |  |  | 1
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | 0.00024 |  |  |  | 0.0975 |  | 1 | MTX | AA2-060 |  |  | 1
923928 | AB2-032 E | 0.6 | 235 | 75 | 0 | 6.4 | 0.59 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB2-032 |  |  | 1
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB1-141 |  |  | 1
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB1-142 |  |  | 1
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 13.36 |  |  | 0.00025 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Y1-079 |  |  | 1
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V4-054 |  |  | 1
924052 | AB2-049 E | 69 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB2-049 |  |  | 1
219915 | AD2-027 E | 26.4 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AD2-027 |  |  | 1
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-060 |  |  | 1
924132 | AB2-057 E | 26 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AB2-057 |  |  | 1
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-046 |  |  | 1
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X1-012 |  |  | 1
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0.57 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | BeaverRun |  |  | 1
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | 0.00025 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
925262 | AB2-180 E | 0.38 | 235 | 75 | 0 | 6 | 0.56 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB2-180 |  |  | 1
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0.56 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W2-030 |  |  | 1
923293 | AB1-138 E | 0.36 | 228 | 75 | 0 | 6 | 0.56 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AB1-138 |  |  | 1
233942 | AB2-180 C | 0.38 | 235 | 75 | 0 | 14 | 8.72 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB2-180 |  |  | 1
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0.53 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W1-130 |  |  | 1
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0.52 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-078 |  |  | 1
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-119 |  |  | 1
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-120 |  |  | 1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 81.14 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228484 | VALERO4 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228472 | VALERO2 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228473 | VALERO3 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 7.45 |  |  | 0.00024 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
204555 | 27QUEEN ST | 115 | 227 | 75 | 0 | 5 | 0.46 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219912 | AD2-042 C | 26.4 | 231 | 75 | 0 | 5 | 0.46 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AD2-042 |  |  | 1
207450 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-113 |  |  | 1
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 75.48 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0.46 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-070 |  |  | 1
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 0.46 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Z2-102 |  |  | 1
207420 | AC1-207 TAP | 34.5 | 228 | 75 | 0 | 4.9 | 0.45 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AC1-207 |  |  | 1
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0.45 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | Z1-096 |  |  | 1
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0.43 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W3-110 |  |  | 1
214030 | WAYNEJCT | 13.8 | 230 | 29 | 0 | 8.8 | 4.73 |  |  | 0.00025 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 3.76 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | U2-030 |  |  | 1
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-025 |  |  | 1
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W3-079 |  |  | 1
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W2-102 |  |  | 1
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W4-103 |  |  | 1
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0.4 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AD2-070 |  |  | 1
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB1-137 |  |  | 1
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X1-037 |  |  | 1
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 0.39 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W2-056 |  |  | 1
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 6.23 |  |  | 0.00025 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0.38 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0.38 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AB1-139 |  |  | 1
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.2 | 7.55 |  |  | 0.00025 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0.37 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | X1-032 |  |  | 1
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Z2-077 |  |  | 1
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Z2-076 |  |  | 1
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 20.25 |  |  | 0.00025 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0.36 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V2-009 3 |  |  | 1
217831 | PB_NUTCLIF | 26 | 231 | 77 | 0 | 10.7 | 7.21 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
206280 | 28LAKEHURS | 34.5 | 228 | 55 | 0 | 13.7 | 10.22 |  |  | 0.00024 |  |  |  | 0.17131 |  | 1 | CAPACITY |  |  |  | 1
217850 | MONTCLAIR_U | 26 | 231 | 77 | 0 | 10.6 | 7.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y1-079 |  |  | 1
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | V4-054 |  |  | 1
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
219914 | AD2-027 C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AD2-027 |  |  | 1
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y3-026 |  |  | 1
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Y3-026 |  |  | 1
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-124 |  |  | 1
219903 | AB2-057 C | 26 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AB2-057 |  |  | 1
217825 | UMD_NJ | 26 | 231 | 77 | 0 | 10.5 | 7.08 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | X3-066 |  |  | 1
205926 | AF2-429 E | 34.5 | 227 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-429 |  |  | 1
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X2-075 |  |  | 1
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | BeaverRun |  |  | 1
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 0.34 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W3-080 |  |  | 1
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-019 |  |  | 1
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X1-012 |  |  | 1
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 0.34 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W2-030 |  |  | 1
207445 | AB1-138 C | 0.38 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AB1-138 |  |  | 1
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W3-079 |  |  | 1
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-091 |  |  | 1
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 3.56 | 0.33 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W4-103 |  |  | 1
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 1
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AD2-070 |  |  | 1
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 3.55 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-119 |  |  | 1
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-120 |  |  | 1
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W1-130 |  |  | 1
219765 | PARADISE E | 13 | 231 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | U4-036 |  |  | 1
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-060 |  |  | 1
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W3-029 |  |  | 1
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W3-077 |  |  | 1
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Y2-081 |  |  | 1
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-129 |  |  | 1
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X4-015 |  |  | 1
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-082 |  |  | 1
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X1-085 |  |  | 1
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | Y2-051 |  |  | 1
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-078 |  |  | 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-024 |  |  | 1
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V2-025 |  |  | 1
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 3.08 | 0.28 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | X3-066 |  |  | 1
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V2-009 2 |  |  | 1
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 3.23 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 3.04 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-073 |  |  | 1
230408 | AD2-065 E | 12.9 | 234 | 75 | 0 | 3.03 | 0.28 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AD2-065 |  |  | 1
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0.28 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | X3-075 |  |  | 1
205925 | AF2-428 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-428 |  |  | 1
210323 | AF2-286 E | 13.8 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-286 |  |  | 1
205923 | AF2-272 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-272 |  |  | 1
205927 | AF2-430 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-430 |  |  | 1
205924 | AF2-281 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-281 |  |  | 1
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V3-070 |  |  | 1
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-016 |  |  | 1
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Z1-096 |  |  | 1
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 0.26 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W3-110 |  |  | 1
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 0.26 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-113 |  |  | 1
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y2-081 |  |  | 1
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W2-102 |  |  | 1
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 0.24 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-025 |  |  | 1
901032 | W1-024E OP1 | 34.5 | 228 | 75 | 0 | 2.5 | 0.23 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-024 |  |  | 1
219908 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 0.23 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AB1-139 |  |  | 1
228712 | V2-041E | 13.2 | 234 | 75 | 0 | 2.48 | 0.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V2-041 |  |  | 1
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0.23 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-121 Z |  |  | 1
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0.23 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-112 |  |  | 1
219728 | YARDVSOLFA E | 13.2 | 231 | 75 | 0 | 2.42 | 0.22 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
230414 | AF1-041 E | 69 | 234 | 75 | 0 | 2.4 | 0.22 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AF1-041 |  |  | 1
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 0.22 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-046 |  |  | 1
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 0.22 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 3 |  |  | 1
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0.22 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Y3-087 |  |  | 1
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0.22 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V2-009 4 |  |  | 1
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0.21 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AC1-017 |  |  | 1
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 0.21 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-019 |  |  | 1
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 0.21 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y3-087 |  |  | 1
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 0.21 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X2-075 |  |  | 1
960882 | AF2-379 E | 69 | 235 | 75 | 0 | 2.26 | 0.21 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AF2-379 |  |  | 1
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | MTX | X2-013 |  |  | 1
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AA1-060 |  |  | 1
219679 | NRGCENTER E | 13.2 | 231 | 55 | 0 | 2 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
219916 | AD2-025 E | 13.2 | 231 | 76 | -2 | 2 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
936193 | AD2-025_E | 13.2 | 231 | 76 | 0 | 2 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
219904 | AC1-010 C | 26.4 | 231 | 75 | 0 | 2.2 | 0.2 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 1
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0.2 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | X1-070 |  |  | 1
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Y1-080 |  |  | 1
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB1-025 S |  |  | 1
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB1-025 N |  |  | 1
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Z2-076 |  |  | 1
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Z2-077 |  |  | 1
208580 | MGTN 2 | 12.5 | 229 | 77 | 0 | 4.8 | 2.98 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X4-031 |  |  | 1
217198 | V3-058 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-058 |  |  | 1
217199 | V3-059 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-059 |  |  | 1
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-132 |  |  | 1
211089 | AF2-277 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-277 |  |  | 1
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V4-001 |  |  | 1
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 3.8 | 2.04 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | U4-036 |  |  | 1
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-129 |  |  | 1
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X4-015 |  |  | 1
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X1-085 |  |  | 1
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Y2-051 |  |  | 1
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V3-024 |  |  | 1
217194 | REDH C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V2-025 |  |  | 1
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-097 |  |  | 1
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-127 |  |  | 1
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-064 |  |  | 1
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 0.17 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 2 |  |  | 1
916006 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 4.4 | 2.69 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-091 |  |  | 1
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-032 |  |  | 1
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-061 |  |  | 1
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V4-069 |  |  | 1
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V4-070 |  |  | 1
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X1-095 |  |  | 1
205930 | AF2-099 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AF2-099 |  |  | 1
205931 | AF2-100 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AF2-100 |  |  | 1
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB1-137 |  |  | 1
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0.17 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V4-005 |  |  | 1
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0.16 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W3-124 |  |  | 1
940922 | AE2-081 E | 34.5 | 228 | 75 | 0 | 1.75 | 0.16 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE2-081 |  |  | 1
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0.16 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | W2-071 |  |  | 1
233940 | AF2-379 C | 69 | 235 | 75 | 0 | 1.64 | 0.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AF2-379 |  |  | 1
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-059 |  |  | 1
227928 | V4-067E | 12.9 | 234 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V4-067 |  |  | 1
207460 | AE2-056 C | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AE2-056 |  |  | 1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AC2-175 |  |  | 1
207463 | AE2-081 C | 34.5 | 228 | 75 | 0 | 1.57 | 0.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AE2-081 |  |  | 1
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.55 | 0.14 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AC1-030 |  |  | 1
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V2-009 1 |  |  | 1
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | V2-041 |  |  | 1
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Y |  |  | 1
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Z |  |  | 1
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 0.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-024 |  |  | 1
219910 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 2.75 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
916005 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 3.45 | 2.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | Y2-018 |  |  | 1
219727 | YARDVSOLFA C | 13.2 | 231 | 75 | 0 | 1.48 | 0.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
218455 | CINNBAY_CGEN | 26.4 | 231 | 64 | 0 | 9 | 7.66 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0.13 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB1-001 |  |  | 1
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 4 |  |  | 1
218450 | LINSOLAR E | 26.4 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
217212 | AMBOY SO E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-069 |  |  | 1
218527 | CNTRALGAS2 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218525 | CNTRALGAS1 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X2-088 |  |  | 1
219906 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AC1-017 |  |  | 1
940692 | AE2-056 E | 34.5 | 228 | 75 | 0 | 1.4 | 0.13 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE2-056 |  |  | 1
219650 | TRENT_COLLEG | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219622 | TRENT_BIOGAS | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0.12 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE1-081 |  |  | 1
208697 | PRIN B34 | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208885 | WNHO | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
219921 | AF1-264 | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | X3-075 |  |  | 1
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 S |  |  | 1
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 N |  |  | 1
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 0.12 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | T20 |  |  | 1
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 0.12 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y1-080 |  |  | 1
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0.12 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X2-089 |  |  | 1
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0.12 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | U2-059 |  |  | 1
958062 | AF2-100 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AF2-100 |  |  | 1
958052 | AF2-099 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AF2-099 |  |  | 1
228721 | V2-035E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | V2-035 |  |  | 1
230410 | AE1-218 E O1 | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AE1-218 |  |  | 1
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | AB2-122 |  |  | 1
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | X1-070 |  |  | 1
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-080 |  |  | 1
218526 | CNTRALGAS2 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
218524 | CNTRALGAS1 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.24 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.17 | 0.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-112 |  |  | 1
205928 | AF2-431 E | 69 | 227 | 75 | 0 | 1.17 | 0.11 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-431 |  |  | 1
230415 | AB2-049 C | 69 | 234 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB2-049 |  |  | 1
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-032 |  |  | 1
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V4-069 |  |  | 1
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V4-070 |  |  | 1
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X1-095 |  |  | 1
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-127 |  |  | 1
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | MTX | Z1-082 |  |  | 1
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | V4-005 |  |  | 1
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-061 |  |  | 1
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-097 |  |  | 1
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-064 |  |  | 1
230407 | AD2-065_C | 12.9 | 234 | 75 | 0 | 1.08 | 0.1 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AD2-065 |  |  | 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.1 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W3-124 |  |  | 1
218781 | BRIS_MYERS | 26 | 231 | 77 | 0 | 3 | 2.02 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.1 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | W2-071 |  |  | 1
219685 | NATIONAL_GYP | 26 | 231 | 77 | 0 | 2.8 | 1.89 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
233900 | O-025 C | 25 | 235 | 64 | 0 | 6 | 5.11 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.09 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | V4-067 |  |  | 1
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.09 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AE1-081 |  |  | 1
219907 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AC1-030 |  |  | 1
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 1 |  |  | 1
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 14.34 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219138 | THOSOLAR E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
219818 | TRENTONSOL E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X2-088 |  |  | 1
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE1-041 |  |  | 1
217213 | AMBOY SO C | 13.2 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V3-069 |  |  | 1
207402 | 28AA2-082 C | 34.5 | 228 | 76 | 0 | 2 | 1.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AA2-082 |  |  | 1
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.08 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB1-001 |  |  | 1
218449 | LINSOLAR C | 26.4 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-101 |  |  | 1
230403 | AB1-116 E | 12.9 | 234 | 28 | 0 | 0.78 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
916010 | T20SOLAR E | 0.5 | 230 | 75 | 0 | 2 | 1.22 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | T20 |  |  | 1
208348 | EELI | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210022 | LING 2 | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 5 | 4.26 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
228733 | AB1-119 E | 12.9 | 234 | 28 | 0 | 0.73 | 0 |  |  | 0.00025 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
230409 | AE1-218 C O1 | 12.9 | 234 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AE1-218 |  |  | 1
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-080 |  |  | 1
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | U2-059 |  |  | 1
930243 | AB1-063_E | 69 | 231 | 0 | 0 | 0 | -0.7 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.65 | 3.95 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | V2-035 |  |  | 1
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X2-089 |  |  | 1
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.07 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V4-001 |  |  | 1
230413 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.06 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | AB2-122 |  |  | 1
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0.06 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AB1-021 |  |  | 1
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0.06 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X2-087 |  |  | 1
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.23 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | Y1-075 |  |  | 1
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | X1-072 |  |  | 1
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0.06 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 1
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0.05 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW | X1-071 |  |  | 1
228014 | PVILLEG | 0.48 | 234 | 65 | 0 | 1.3 | 0.77 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219137 | THOSOLAR C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W1-121 Y |  |  | 1
219817 | TRENTONSOL C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 1
219920 | AE1-041 EBAT | 26.4 | 231 | 76 | -0.5 | 0.5 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AE1-041 |  |  | 1
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.05 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W1-101 |  |  | 1
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0.05 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-067 |  |  | 1
207461 | AE2-057 C | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AE2-057 |  |  | 1
940702 | AE2-057 E | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AE2-057 |  |  | 1
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.55 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 3 | 2.55 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
932032 | AC2-009 E | 69 | 231 | 75 | -0.5 | 0.49 | 0.05 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AC2-009 |  |  | 1
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.47 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0.04 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-036 |  |  | 1
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0.04 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W4-058 |  |  | 1
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.21 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219917 | AB1-063 E | 69 | 231 | 75 | 0 | 0.4 | 0.04 |  |  | 0.00025 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | Y1-075 |  |  | 1
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X2-087 |  |  | 1
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | X1-072 |  |  | 1
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | W2-052 |  |  | 1
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.03 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY | X1-071 |  |  | 1
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 0.35 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Y2-018 |  |  | 1
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-065 |  |  | 1
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.7 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.7 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219922 | AF1-261 | 26.4 | 231 | 75 | 0 | 0.9 | 0.61 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AA2-058 |  |  | 1
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-036 |  |  | 1
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AB1-021 |  |  | 1
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V3-067 |  |  | 1
207455 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-066 |  |  | 1
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-058 |  |  | 1
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0.03 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | V3-068 |  |  | 1
207419 | AB2-139 E | 34.5 | 228 | 76 | -0.2 | 0.21 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AB2-139 |  |  | 1
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.02 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W4-059 |  |  | 1
207456 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.02 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V3-065 |  |  | 1
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | W2-052 |  |  | 1
219919 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AE1-041 |  |  | 1
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V3-068 |  |  | 1
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | V3-066 |  |  | 1
961373 | AF2-428 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-428 |  |  | 1
210322 | AF2-286 BAT | 13.8 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-286 |  |  | 1
959813 | AF2-272 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-272 |  |  | 1
961383 | AF2-429 BAT | 34.5 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-429 |  |  | 1
961393 | AF2-430 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-430 |  |  | 1
959903 | AF2-281 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-281 |  |  | 1
961403 | AF2-431 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-431 |  |  | 1
211088 | AF2-277 BAT | 69 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-277 |  |  | 1
219918 | AC2-009 C | 69 | 231 | 75 | -0.1 | 0.1 | 0.01 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AC2-009 |  |  | 1
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.43 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 30 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1178.3 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 1145.8 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 1138.9 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 75 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 28 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 1122.1 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 1119.7 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 749 |  |  | 0.00025 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 30 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 43.9 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 10.2 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | 0.00024 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00023 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00023 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | 0.00023 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 213 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 130.16 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | 0.00023 |  |  |  | 0.036 |  | 1 | CAPACITY | Hummel |  |  | 1
921653 | AA2-008 E | 230 | 229 | 58 | 0 | 57 | 0 |  |  | 0.00023 |  |  |  | 0.036 |  | 1 | ENERGY | MOXIE PATRIOT |  |  | 1
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00024 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00024 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | 0.00024 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
916009 | LOR2_Q27 E | 0.7 | 229 | 74 | 0 | 88.8 | 54.21 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | Q27 |  |  | 1
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 52.08 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
208946 | MACR CT | 12.5 | 229 | 55 | 61.4 | 70.6 | 37.97 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 32 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208941 | FISH CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 31.63 |  |  | 0.00024 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
208940 | ALLE CT | 12.5 | 229 | 55 | 48.7 | 56 | 30.12 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 37.91 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 26.19 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 26.03 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
209031 | WAYM IPP E | 34.5 | 229 | 74 | 0 | 55.5 | 33.88 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | K21 |  |  | 1
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 23.83 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
209009 | PEIP 2 | 13.8 | 229 | 56 | 38 | 43.7 | 23.5 |  |  | 0.00023 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
211375 | BEAC | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00024 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | 0.00023 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
209018 | SUNBIPCT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | 0.00023 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 0.26 |  |  | 0.00023 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 15.92 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 15.71 |  |  | 0.00023 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
935072 | AD1-143 E1 | 69 | 229 | 74 | 0 | 34.28 | 20.93 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
208944 | JENK CT | 12.5 | 229 | 55 | 24 | 27.6 | 14.85 |  |  | 0.00023 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208948 | WILL CT | 12.5 | 229 | 55 | 23.1 | 26.6 | 14.31 |  |  | 0.00023 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208920 | WLPK | 12.5 | 229 | 60 | 35.5 | 40.8 | 28.68 |  |  | 0.00024 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | 0.00023 |  |  |  | 0.0975 |  | 1 | MTX | Z2-107 |  |  | 1
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 21 | 11.3 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916008 | LOR1 E | 0.7 | 229 | 74 | 0 | 23.8 | 14.53 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | N14 |  |  | 1
946263 | BECR K09 E | 0.69 | 229 | 74 | 0 | 20.7 | 12.64 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | L18 |  |  | 1
211065 | PASP 1_2 C | 13.8 | 229 | 75 | 0 | 8 | 0.74 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AC1-087 |  |  | 1
943302 | AF1-001 E | 34.5 | 201 | 75 | 0 | 7.25 | 0.53 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF1-001 |  |  | 1
211374 | AVOC | 12.5 | 229 | 77 | 0 | 17.4 | 10.8 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
209007 | NOEN IPP | 13.8 | 229 | 12 | 96.9 | 111.4 | 105.11 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
237039 | AF1-001 C | 34.5 | 201 | 75 | 0 | 6.5 | 0.47 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | AF1-001 |  |  | 1
942581 | PASP 2 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AC1-087 |  |  | 1
926082 | PASP 1 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | U4-014 |  |  | 1
935071 | AD1-143 C1 | 69 | 229 | 75 | 0 | 5.72 | 0.53 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
209010 | PEIP 1 | 13.8 | 229 | 64 | 17.4 | 26.5 | 21.42 |  |  | 0.00023 |  |  |  | 0.28996 |  | 1 | CAPACITY |  |  |  | 1
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 7.75 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 1
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 81.14 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 77.37 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.2 | 6.84 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | Q27 |  |  | 1
935082 | AD1-143 E2 | 69 | 229 | 75 | 0 | 4.8 | 0.44 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 4.3 |  |  | 0.00024 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 5.49 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | K21 |  |  | 1
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 5.34 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 1
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 7.03 |  |  | 0.00023 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 6.96 |  |  | 0.00023 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
209945 | AF2-278 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AF2-278 |  |  | 1
212451 | AF2-427 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-427 |  |  | 1
212464 | AF2-289 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-289 |  |  | 1
211938 | AF2-285 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-285 |  |  | 1
209972 | AF2-288 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-288 |  |  | 1
209937 | AF2-287 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-287 |  |  | 1
211490 | AF2-282 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-282 |  |  | 1
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 40.29 |  |  | 0.00024 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 30.66 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212495 | AF2-284 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-284 |  |  | 1
212455 | AF2-290 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-290 |  |  | 1
211554 | AF2-283 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW | AF2-283 |  |  | 1
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.14 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY | N14 |  |  | 1
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.02 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY | L18 |  |  | 1
212005 | ALWD | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210319 | WCAR 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212345 | PENS | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 5.19 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
211591 | HARW | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212435 | SMIL | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | 0.00023 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
935081 | AD1-143 C2 | 69 | 229 | 75 | 0 | 0.2 | 0.02 |  |  | 0.00024 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 1
209944 | AF2-278 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00024 |  |  |  | 0 |  | 1 | MTX | AF2-278 |  |  | 1
212494 | AF2-284 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-284 |  |  | 1
212461 | AF2-289 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-289 |  |  | 1
212450 | AF2-427 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-427 |  |  | 1
212454 | AF2-290 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-290 |  |  | 1
211937 | AF2-285 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-285 |  |  | 1
209936 | AF2-287 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-287 |  |  | 1
209971 | AF2-288 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-288 |  |  | 1
211489 | AF2-282 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-282 |  |  | 1
211553 | AF2-283 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | 0.00023 |  |  |  | 0 |  | 1 | MTX | AF2-283 |  |  | 1
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1251.7 |  |  | 0.00024 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1253.3 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 758.5 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 757.9 |  |  | 0.00023 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 253.85 |  |  | 0.00022 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 317.2 | 121.14 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | 0.00022 |  |  |  | 0.036 |  | 1 | CAPACITY | RONCO |  |  | 1
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 59.57 |  |  | 0.00023 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 552 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 545.5 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 710 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235587 | 01HARRN3 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235586 | 01HARRN2 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235585 | 01HARRN1 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 236.66 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00021 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
916002 | 01ELLIOTTS E | 34.5 | 201 | 74 | 0 | 44.9 | 21.63 |  |  | 0.00022 |  |  |  | 0 |  | 1 | NEW | N32 |  |  | 1
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | 0.00021 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | 0.00021 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
913142 | Y1-033 E OP1 | 0.7 | 226 | 74 | 0 | 34.02 | 20.77 |  |  | 0.00021 |  |  |  | 0 |  | 1 | NEW | Y1-033 |  |  | 1
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | 0.00021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | 0.00021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 21.4 | 11.51 |  |  | 0.00022 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 2.65 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY | N32 |  |  | 1
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 3.05 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | Y1-033 |  |  | 1
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.22 |  |  | 0.00022 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235590 | 01PLEAS1 | 26 | 201 | 16 | 300 | 639 | 0 |  |  | 0.00021 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235591 | 01PLEAS2 | 26 | 201 | 16 | 350 | 639 | 0 |  |  | 0.00021 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 124.5 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | 0.00021 |  |  |  | 0.036 |  | 1 | CAPACITY | T-174 |  |  | 1
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | 0.00021 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 73.26 |  |  | 0.00021 |  |  |  | 0 |  | 1 | NEW | P28 |  |  | 1
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 31.73 |  |  | 0.00021 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | 0.0002 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 25.64 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | K23 |  |  | 1
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 19.54 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | L13 |  |  | 1
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 17.58 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 11.51 |  |  | 0.00021 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
203926 | AA2-133 GEN | 13.8 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.0002 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 13.37 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | P28 |  |  | 1
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | 0.0002 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
237048 | AF1-022 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | AF1-022 |  |  | 1
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 14.76 |  |  | 0.0002 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
943512 | AF1-022 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | 0.00021 |  |  |  | 0 |  | 1 | NEW | AF1-022 |  |  | 1
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 3.85 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | Lookout Wind |  |  | 1
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 3.6 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | L13 |  |  | 1
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 4.8 | 2.93 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | K23 |  |  | 1
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 1.1 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 1
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 850.6 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | Cone1 |  |  | 1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 850 |  |  | 0.00021 |  |  |  | 0 |  | 1 | CAPACITY | Cone2 |  |  | 1
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 410 | 156.58 |  |  | 0.0002 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.0002 |  |  |  | 0.036 |  | 1 | CAPACITY | X1-109 |  |  | 1
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | X1-109 |  |  | 1
235621 | 01SBEND3 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.0002 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235622 | 01SBEND4 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.0002 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235620 | 01SBEND2 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.0002 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235619 | 01SBEND1 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | 0.0002 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 170.9 | 65.27 |  |  | 0.00019 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 170.8 | 65.23 |  |  | 0.00019 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203936 | 26AA1-144 G1 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.0002 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203937 | 26AA1-144 G2 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | AA1-144 |  |  | 1
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 39.07 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | N39 |  |  | 1
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 62.3 | 38.03 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | R32 |  |  | 1
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | O38 |  |  | 1
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 34.19 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | K02 |  |  | 1
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 54.4 | 33.21 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | O18 |  |  | 1
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 25.91 |  |  | 0.0002 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
203938 | 26AA2-132 | 34.5 | 226 | 29 | 0 | 19.9 | 0 |  |  | 0.00019 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
237083 | AE1-147_GEN | 0.6 | 201 | 75 | 0 | 19.98 | 1.46 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | AE1-147 |  |  | 1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 44 | 26.86 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | P60 |  |  | 1
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 31.6 | 19.29 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | Q53 |  |  | 1
237041 | AE2-055 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 26.2 | 15.99 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | K13 |  |  | 1
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | 0.00019 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 11.3 |  |  | 0.00019 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 11.3 |  |  | 0.00019 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | 0.0002 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | 0.0002 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203940 | AF1-140 C | 23 | 226 | 75 | 0 | 9.78 | 0.9 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | AF1-140 |  |  | 1
237046 | AF1-021 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | AF1-021 |  |  | 1
940682 | AE2-055 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 1
939171 | AE1-147_E | 0.6 | 201 | 75 | 0 | 7.98 | 0.58 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AE1-147 |  |  | 1
916003 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 13.3 | 6.41 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | K20 |  |  | 1
944752 | AF1-140 E | 23 | 226 | 75 | 0 | 6.52 | 0.6 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AF1-140 |  |  | 1
943502 | AF1-021 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | AF1-021 |  |  | 1
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 7.75 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | R32 |  |  | 1
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 11.1 | 6.78 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | N39 |  |  | 1
957932 | AF2-087 E | 46 | 226 | 75 | 0 | 4.2 | 0.39 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AF2-087 |  |  | 1
236828 | 01GRAYMONT | 46 | 201 | 75 | 0 | 4 | 0.29 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.1 | 5.56 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | O38 |  |  | 1
203942 | AF2-270 E | 23 | 226 | 75 | 0 | 3.72 | 0.34 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 5.19 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | P60 |  |  | 1
916004 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW | K22 |  |  | 1
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | O18 |  |  | 1
203941 | AF2-087 C | 46 | 226 | 75 | 0 | 3.05 | 0.28 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | AF2-087 |  |  | 1
203944 | AF2-271 E | 46 | 226 | 75 | 0 | 3 | 0.28 |  |  | 0.0002 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | 0.0002 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 3.91 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | Q53 |  |  | 1
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | 0.0002 |  |  |  | 0 |  | 1 | MTX | AC1-025 |  |  | 1
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 1.95 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | K13 |  |  | 1
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 0.82 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | K20 |  |  | 1
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.55 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | K22 |  |  | 1
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.53 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.11 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 852.3 | 852.3 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | Keys1 |  |  | 1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 851.6 | 851.6 |  |  | 0.0002 |  |  |  | 0 |  | 1 | CAPACITY | Keys2 |  |  | 1
237054 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 195.92 |  |  | 0.00019 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200503 | 26C.SLOPE | 115 | 226 | 11 | 17 | 50 | 0 |  |  | 0.00019 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 49.15 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | P47 |  |  | 1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 41.7 | 25.46 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | Q36 |  |  | 1
237036 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 7.64 |  |  | 0.00019 |  |  |  | 0.1042 |  | 1 | CAPACITY | AD2-002 |  |  | 1
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 17.22 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | V3-030 |  |  | 1
203946 | AE2-131 C | 34.5 | 226 | 75 | 0 | 12 | 1.11 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | AE2-131 |  |  | 1
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.00019 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 0.2 |  |  | 0.00019 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200809 | 26SITHE | 138 | 226 | 60 | 0 | 36 | 25.31 |  |  | 0.00018 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 21.5 | 11.56 |  |  | 0.00019 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200665 | 26SHAWVL 3 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.00018 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200666 | 26SHAWVL 4 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | 0.00018 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
237043 | AE2-125 C | 25 | 201 | 75 | 0 | 8.28 | 0.6 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
941352 | AE2-131 E | 34.5 | 226 | 75 | 0 | 8 | 0.74 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AE2-131 |  |  | 1
200722 | 26SHAWVL 2 | 18 | 226 | 30 | 62 | 125 | 117.94 |  |  | 0.00018 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200715 | 26SHAWVL 1 | 18 | 226 | 30 | 62 | 123 | 116.05 |  |  | 0.00018 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.2 | 9.28 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | P47 |  |  | 1
941312 | AE2-125 E | 25 | 201 | 75 | 0 | 5.52 | 0.4 |  |  | 0.00019 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 1
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 8.66 |  |  | 0.00018 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 5.07 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | Q36 |  |  | 1
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 3.24 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY | V3-030 |  |  | 1
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4 |  |  | 0.00018 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | 0.00018 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | 0.00018 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 525.7 |  |  | 0.00019 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 620 |  |  | 0.00018 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | 0.00018 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00018 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00018 |  |  |  | 0.036 |  | 1 | NEW | AB1-069 |  |  | 1
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 173.6 | 199.5 | 76.19 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 167 | 191.9 | 73.29 |  |  | 0.00017 |  |  |  | 0.036 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 164.1 | 188.6 | 72.03 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
200805 | 26COLVER13 | 13.2 | 226 | 12 | 95.7 | 110 | 0 |  |  | 0.00018 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 34.62 |  |  | 0.00018 |  |  |  | 0 |  | 1 | NEW | Z1-069 |  |  | 1
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | 0.00017 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | 0.00017 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237050 | AF1-155 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY | AF1-155 |  |  | 1
944902 | AF1-155 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | 0.00017 |  |  |  | 0 |  | 1 | NEW | AF1-155 |  |  | 1
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 17.1 | 10.44 |  |  | 0.00018 |  |  |  | 0 |  | 1 | CAPACITY | Z1-069 |  |  | 1
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 3.83 |  |  | 0.00017 |  |  |  | 0.0789 |  | 1 | CAPACITY | ALLEG LD_5 |  |  | 1
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 614 |  |  | 0.00018 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 650 |  |  | 0.00018 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 42.3 |  |  | 0.00017 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237052 | AF1-210 C | 25 | 201 | 75 | 0 | 9.54 | 0.7 |  |  | 0.00016 |  |  |  | 0 |  | 1 | CAPACITY | AF1-210 |  |  | 1
945452 | AF1-210 E | 25 | 201 | 75 | 0 | 6.36 | 0.46 |  |  | 0.00016 |  |  |  | 0 |  | 1 | NEW | AF1-210 |  |  | 1
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 4.22 |  |  | 0.00017 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 3.77 |  |  | 0.00016 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 164.5 |  |  | 0.00015 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 155.36 |  |  | 0.00015 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 21.23 |  |  | 0.00015 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 21.09 |  |  | 0.00015 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203932 | AE1-123 | 34.5 | 226 | 55 | 0 | 18 | 9.68 |  |  | 0.00015 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 2.69 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 72.8 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 124.2 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | 0.00015 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 62 | 33.35 |  |  | 0.00014 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00013 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00013 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 28.78 |  |  | 0.00013 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 28.78 |  |  | 0.00013 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | 0.00013 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 10.54 |  |  | 0.00013 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 80.2 |  |  | 0.00013 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
254026 | 15USSILL | 138 | 215 | 77 | 0 | 66 | 27.72 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
254024 | 15CLAIRT | 138 | 215 | 77 | 0 | 35 | 14.7 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
203939 | AE1-160 C | 34.5 | 226 | 75 | 0 | 12.7 | 1.17 |  |  | 0.00013 |  |  |  | 0 |  | 1 | CAPACITY | AE1-160 |  |  | 1
939292 | AE1-160 E | 34.5 | 226 | 75 | 0 | 7.3 | 0.68 |  |  | 0.00013 |  |  |  | 0 |  | 1 | NEW | AE1-160 |  |  | 1
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 770.1 |  |  | 0.00013 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270122 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 185.22 |  |  | 0.00011 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 38.8 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253970 | 15BI2 | 13.8 | 215 | 58 | 83.2 | 95.6 | 36.51 |  |  | 0.00011 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
239022 | 02NWCAG3 | 14.4 | 202 | 57 | 20 | 92.3 | 35.25 |  |  | 0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.5 | 18.52 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 6.91 |  |  | 0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
254037 | 15UNIVRS | 138 | 215 | 77 | 0 | 1.1 | 0.46 |  |  | 0.00012 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 790.2 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 567.5 |  |  | 0.00012 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 139.32 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.0001 |  |  |  | 0.036 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
253924 | 15SHELL | 138 | 215 | 58 | 0 | 98 | 0 |  |  | 0.0001 |  |  |  | 0.036 |  | 1 | ENERGY | Y3-103 |  |  | 1
239024 | 02NWCAG5 | 16.5 | 202 | 57 | 23 | 145 | 55.38 |  |  | 0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 216.9 |  |  | 0.0001 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239023 | 02NWCAG4 | 14.4 | 202 | 57 | 20 | 93 | 35.52 |  |  | 0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 15.2 | 5.8 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | 0.0001 |  |  |  | 0.036 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0.53 |  |  | 0.0001 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 13.77 |  |  | 0.0001 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
254303 | AC2-168 C | 138 | 215 | 75 | 0 | 4.4 | 0.32 |  |  | 0.0001 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 1
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 0.04 |  |  | 0.00011 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.26 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 620.4 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | 0.00011 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 156.58 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | 0.0001 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 113.43 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | 0.0001 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | 9e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
254304 | AE2-114 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AE2-114 |  |  | 1
254305 | AE2-115 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY | AE2-115 |  |  | 1
941212 | AE2-115 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | 0.0001 |  |  |  | 0 |  | 1 | NEW | AE2-115 |  |  | 1
941202 | AE2-114 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | 0.0001 |  |  |  | 0 |  | 1 | NEW | AE2-114 |  |  | 1
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 2.69 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253900 | 15BVRVL1 | 22 | 215 | 44 | 781.7 | 898.5 | 898.5 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 899.3 |  |  | 0.0001 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241951 | AB1-105 OP | 345 | 202 | 58 | 0 | 850 | 0 |  |  | 8e-05 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 307.6 | 117.47 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | 9e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 280 | 106.93 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | 9e-05 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | 9e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Y2-050 |  |  | 1
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | 9e-05 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 26.1 | 16.36 |  |  | 9e-05 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 6e-05 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 6e-05 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | 6e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | Guernsey |  |  | 1
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 194.77 |  |  | 5e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | 5e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | 5e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 2.55 |  |  | 5e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1247 |  |  | 4e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
245305 | 05WOOSTER | 69 | 205 | 77 | 0 | 1 | 0.72 |  |  | 4e-05 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245304 | 05WOOSTER | 23 | 205 | 77 | 0 | 1 | 0.72 |  |  | 4e-05 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243158 | 05WOOSTE | 138 | 205 | 77 | 0 | 1 | 0.72 |  |  | 4e-05 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 7.55 |  |  | 2e-05 |  |  |  | 0 |  | 1 | NEW | Z1-035 |  |  | 1
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 1.13 |  |  | 2e-05 |  |  |  | 0 |  | 1 | CAPACITY | Z1-035 |  |  | 1
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 4.3 |  |  | -1e-05 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 243 | 92.8 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -4e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -4e-05 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -5e-05 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -5e-05 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 223.38 |  |  | -6e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 25 | 0.37 |  |  | -6e-05 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 44.3 |  |  | -7e-05 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
270106 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -8e-05 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 627.1 |  |  | -8e-05 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  |  |  | -0.0001
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 30.93 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 30.55 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 30.17 |  |  | -0.0001 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.0001 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  |  |  | -0.0001
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AC1-069 |  |  | 1
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AC1-068 |  |  | 1
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AC1-166 |  |  | 1
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.00011 |  |  |  | 0 |  | 1 | CAPACITY | AC1-165 |  |  | 1
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AC1-166 |  |  | 1
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AC1-165 |  |  | 1
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AC1-069 |  |  | 1
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.00011 |  |  |  | 0 |  | 1 | NEW | AC1-068 |  |  | 1
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
253317 | AC1-085 B_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 1
253314 | AC1-085 A_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.00012 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 1
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 29.6 |  |  | -0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 28.95 |  |  | -0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 28.68 |  |  | -0.00011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 19.51 |  |  | -0.00011 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 18.94 |  |  | -0.00011 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 9.4 |  |  | -0.00012 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 0.88 |  |  | -0.00019 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
907201 | AC2-103 E1 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.0002 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
907202 | AC2-103 E2 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.0002 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 1
252507 | AC2-088 C | 0.57 | 212 | 75 | 0 | 38.4 | 2.8 |  |  | -0.00021 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
932665 | AC2-088 E | 0.57 | 212 | 75 | 0 | 31.6 | 2.31 |  |  | -0.00021 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
241885 | AC2-103 C1 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.0002 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
241886 | AC2-103 C2 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.0002 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 1
252509 | AD1-136 C | 0.57 | 212 | 75 | 0 | 5.4 | 0.39 |  |  | -0.00021 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 1
935033 | AD1-136 E | 0.57 | 212 | 75 | 0 | 4.6 | 0.34 |  |  | -0.00021 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 1
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.5 | 3.02 |  |  | -0.00021 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.00021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.00021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.00021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  |  |  | -0.0002
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | -0.0002
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | -0.0002
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 6.79 |  |  | -0.00024 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 42.01 |  |  | -0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 108.1 | 41.28 |  |  | -0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 106.7 | 40.75 |  |  | -0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270186 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.00024 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 1
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 27.88 |  |  | -0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 70.9 | 27.08 |  |  | -0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.00025 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 1
270174 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 1
251832 | 08HLCRTG | 0.38 | 212 | 75 | 0 | 120 | 8.76 |  |  | -0.00026 |  |  |  | 0 |  | 1 | CAPACITY | AB1-014 |  |  | 1
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | V4-010 |  |  | 1
930062 | AB1-014 E | 0.38 | 212 | 75 | 0 | 77.5 | 5.66 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEW | AB1-014 |  |  | 1
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.00026 |  |  |  | 0 |  | 1 | CAPACITY | V4-010 |  |  | 1
253158 | 09INDI L | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.00027 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253127 | 09CEDRVL | 69 | 209 | 77 | 0 | 1.8 | 1.3 |  |  | -0.00026 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 345.1 | 131.79 |  |  | -0.00027 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 125.75 |  |  | -0.00028 |  |  |  | 0 |  | 1 | NEW | U2-072 |  |  | 1
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 162.6 | 62.1 |  |  | -0.00027 |  |  |  | 0.036 |  | 1 | CAPACITY | FREMONT |  |  | 1
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 159.1 | 60.76 |  |  | -0.00027 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 18.79 |  |  | -0.00028 |  |  |  | 0 |  | 1 | CAPACITY | U2-072 |  |  | 1
247454 | 05OGG STREET | 69 | 205 | 77 | 0 | 10 | 7.16 |  |  | -0.00028 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 896 |  |  | -0.00028 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 586 |  |  | -0.00029 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 734 |  |  | -0.00029 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
253160 | 09JCKCEN | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.00029 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
925135 | AB2-170 E | 0.55 | 205 | 75 | 0 | 80.6 | 0 |  |  | -0.0003 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
247549 | V3-028 C | 345 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.0003 |  |  |  | 0 |  | 1 | CAPACITY | V3-028 |  |  | 1
925133 | AB2-170 C | 0.55 | 205 | 75 | 0 | 49.4 | 0 |  |  | -0.0003 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 1
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 20.96 |  |  | -0.00031 |  |  |  | 0 |  | 1 | NEW | U1-059 |  |  | 1
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | -0.0003 |  |  |  | 0 |  | 1 | NEW | V3-028 |  |  | 1
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 7.71 |  |  | -0.00031 |  |  |  | 0 |  | 1 | NEW | W1-056 |  |  | 1
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 4.63 |  |  | -0.00031 |  |  |  | 0 |  | 1 | CAPACITY | U1-059 |  |  | 1
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.16 |  |  | -0.00031 |  |  |  | 0 |  | 1 | CAPACITY | W1-056 |  |  | 1
251828 | CLNTESP1 | 0 | 212 | 76 | 0 | 10 | 0 |  |  | -0.00033 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.00033 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 0 |  |  | -0.00035 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.00035 |  |  |  | 0.036 |  | 1 | NEW | AB1-107 |  |  | 1
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.00035 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 127.94 |  |  | -0.00035 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 124.58 |  |  | -0.00035 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.00035 |  |  |  | 0.036 |  | 1 | CAPACITY | OREGON |  |  | 1
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.00035 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 92.04 |  |  | -0.00035 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.00035 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.00035 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.00035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 41.94 |  |  | -0.00035 |  |  |  | 0.39467 |  | 1 | CAPACITY |  |  |  | 1
918421 | AA1-056 | 345 | 202 | 58 | 0 | 46 | 0 |  |  | -0.00034 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 101.27 |  |  | -0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 0.19 |  |  | -0.00034 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 0.15 |  |  | -0.00035 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
244357 | 05GRANGER EL | 34.5 | 205 | 2 | 0 | 3.2 | 0 |  |  | -0.00034 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0.11 |  |  | -0.00035 |  |  |  | 0 |  | 1 | NEW | V4-073 |  |  | 1
253303 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.07 |  |  | -0.00035 |  |  |  | 0 |  | 1 | CAPACITY | V4-073 |  |  | 1
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 2.26 |  |  | -0.00037 |  |  |  | 0 |  | 1 | NEW | AC2-067 |  |  | 1
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 1.93 |  |  | -0.00037 |  |  |  | 0 |  | 1 | CAPACITY | AC2-067 |  |  | 1
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 1.46 |  |  | -0.00036 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 10.04 |  |  | -0.00036 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.00036 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253197 | 09PIQUA3 | 69 | 209 | 77 | 0 | 38.3 | 2.77 |  |  | -0.00038 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 77.49 |  |  | -0.00041 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
253029 | 09GRNVIL | 138 | 209 | 77 | 0 | 4.5 | 3.26 |  |  | -0.0004 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251298 | 08CRITDN | 69 | 212 | 77 | 0 | 2.7 | 1.9 |  |  | -0.00041 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253363 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00042 |  |  |  | 0.05 |  | 1 | MTX | AC1-212 |  |  | 1
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 0.19 |  |  | -0.00042 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
253178 | 09MINSTR | 69 | 209 | 77 | 0 | 10 | 4.61 |  |  | -0.00042 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
AC1-212 | BATEXP_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0004
253362 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.28 |  |  | -0.00042 |  |  |  | 0 |  | 1 | CAPACITY | AC1-212 |  |  | 1
251542 | 08VERONA | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.00044 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251364 | 08LEBANO | 69 | 212 | 77 | 0 | 30.6 | 21.57 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253234 | 09VERSAL | 69 | 209 | 77 | 0 | 5.4 | 3.91 |  |  | -0.00046 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.00047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.00047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.2 | 45.52 |  |  | -0.00047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 8.4 |  |  | -0.00047 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 0.16 |  |  | -0.00047 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 272.1 | 103.92 |  |  | -0.00048 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-079 |  |  | 1
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 202.7 | 77.41 |  |  | -0.00048 |  |  |  | 0 |  | 1 | CAPACITY | Z1-079 |  |  | 1
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 19.29 |  |  | -0.00048 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251387 | 08MDDLTW | 69 | 212 | 77 | 0 | 22.5 | 16.62 |  |  | -0.00048 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 26.35 |  |  | -0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 11.46 |  |  | -0.00048 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 4.93 |  |  | -0.00048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253128 | 09CELINA | 69 | 209 | 77 | 0 | 4 | 2.89 |  |  | -0.00048 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 31.16 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.5 | 30.74 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 30.59 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 29.56 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251953 | 08MADSN2 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251954 | 08MADSN3 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251959 | 08MADSN8 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251955 | 08MADSN4 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251952 | 08MADSN1 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251958 | 08MADSN7 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251957 | 08MADSN6 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251956 | 08MADSN5 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.00049 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00049 |  |  |  | 0 |  | 1 | MTX | Y3-099 |  |  | 1
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00049 |  |  |  | 0 |  | 1 | MTX | Y3-100 |  |  | 1
250041 | 08HAMLTN | 138 | 212 | 77 | 0 | 2.2 | 1.55 |  |  | -0.0005 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
341584 | 2GRIFFIN | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | -0.00051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
251269 | 08BEAVR2 | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
913222 | Y1-054 E | 138 | 212 | 58 | 0 | 20 | 0 |  |  | -0.00051 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
251346 | 08IVYDL1 | 69 | 212 | 77 | 0 | 12.5 | 8.81 |  |  | -0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
250091 | 08RCHLE3 | 138 | 212 | 77 | 0 | 6.7 | 4.72 |  |  | -0.00051 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
342550 | 4BAVARIAN LF | 138 | 320 | 77 | 0 | 4.8 | 3.24 |  |  | -0.00053 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.00055 |  |  |  | 0 |  | 1 | NEW | R60 2 |  |  | 1
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.00055 |  |  |  | 0 |  | 1 | NEW | R60 1 |  |  | 1
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 84.83 | 40.87 |  |  | -0.00055 |  |  |  | 0 |  | 1 | NEW | R60 3 |  |  | 1
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 7.95 |  |  | -0.00055 |  |  |  | 0 |  | 1 | CAPACITY | R60 3 |  |  | 1
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.00055 |  |  |  | 0 |  | 1 | CAPACITY | R60 2 |  |  | 1
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.00055 |  |  |  | 0 |  | 1 | CAPACITY | R60 1 |  |  | 1
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.00054 |  |  |  | 0.0975 |  | 1 | MTX | Z1-065 |  |  | 1
249991 | 08BUFTN1 | 138 | 212 | 77 | 0 | 2.2 | 0 |  |  | -0.00055 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.0006 |  |  |  | 0 |  | 1 | NEW | V1-011 |  |  | 1
247607 | V1-011 GEN | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.0006 |  |  |  | 0 |  | 1 | CAPACITY | V1-011 |  |  | 1
243017 | 05HAVILAND1 | 138 | 205 | 77 | 0 | 4.5 | 3.22 |  |  | -0.0006 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 57.21 |  |  | -0.00062 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 57.17 |  |  | -0.00062 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149 | 56.9 |  |  | -0.00062 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 0.39 |  |  | -0.00063 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 0.37 |  |  | -0.00063 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 600 |  |  | -0.00064 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.00064 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.00064 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 76.1 | 36.67 |  |  | -0.00066 |  |  |  | 0 |  | 1 | NEW | R49 |  |  | 1
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 11.03 |  |  | -0.00066 |  |  |  | 0 |  | 1 | CAPACITY | R49 |  |  | 1
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 57.82 |  |  | -0.00067 |  |  |  | 0 |  | 1 | NEW | T131 |  |  | 1
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 31.8 |  |  | -0.00067 |  |  |  | 0 |  | 1 | NEW | AC1-173 |  |  | 1
247521 | T131 | 0.69 | 205 | 74 | 26.1 | 30 | 14.45 |  |  | -0.00067 |  |  |  | 0 |  | 1 | CAPACITY | T131 |  |  | 1
270191 | AC1-173 C | 0.65 | 205 | 74 | 0 | 9.9 | 4.77 |  |  | -0.00067 |  |  |  | 0 |  | 1 | CAPACITY | AC1-173 |  |  | 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.0007 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.0007 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.0007 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.0007 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.0007 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.0007 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
243362 | 05RANDOLPH1 | 138 | 205 | 77 | 0 | 4 | 3.06 |  |  | -0.00082 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
243415 | 05WWVSTA | 69 | 205 | 61 | 69.8 | 96 | 53.26 |  |  | -0.00082 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
246235 | 05BLUFFTON | 69 | 205 | 77 | 0 | 2 | 1.43 |  |  | -0.00083 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 46.25 |  |  | -0.00083 |  |  |  | 0 |  | 1 | NEW | S71 |  |  | 1
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 11.56 |  |  | -0.00083 |  |  |  | 0 |  | 1 | CAPACITY | S71 |  |  | 1
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.48 |  |  | -0.00083 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247529 | 05COVRT2 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.00084 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 2 |  |  | 1
247530 | 05COVRT3 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.00084 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247528 | 05COVRT1 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.00084 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247531 | 05COVRT4 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.00084 |  |  |  | 0 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.00084 |  |  |  | 0 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 114.1 | 131.2 | 50.11 |  |  | -0.00084 |  |  |  | 0 |  | 1 | CAPACITY | Covert 2 |  |  | 1
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 54.49 |  |  | -0.00084 |  |  |  | 0 |  | 1 | NEW | AC2-176 |  |  | 1
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.00085 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.00085 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270201 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 8.14 |  |  | -0.00084 |  |  |  | 0 |  | 1 | CAPACITY | AC2-176 |  |  | 1
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 22.88 |  |  | -0.00089 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 22.8 |  |  | -0.00089 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 22.19 |  |  | -0.00089 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 22.07 |  |  | -0.00089 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.02 |  |  | -0.0009 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.3 | 0.72 |  |  | -0.0009 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.0009 |  |  |  | 0 |  | 1 | CAPACITY | Z2-113 |  |  | 1
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.0009 |  |  |  | 0 |  | 1 | NEW | Z2-113 |  |  | 1
247604 | X1-042 | 12 | 205 | 64 | 0 | 3.8 | 2.55 |  |  | -0.0009 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.00091 |  |  |  | 0.036 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.00091 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 127.17 |  |  | -0.00091 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 1.75 |  |  | -0.00091 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 1014.5 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00093 |  |  |  | 0 |  | 1 | NEW | V3-007 |  |  | 1
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00093 |  |  |  | 0 |  | 1 | NEW | U2-090 |  |  | 1
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.00093 |  |  |  | 0 |  | 1 | CAPACITY | V3-007 |  |  | 1
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.00093 |  |  |  | 0 |  | 1 | CAPACITY | U2-090 |  |  | 1
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 3.33 |  |  | -0.00093 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 2.16 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247969 | Z2-116 E | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.00092 |  |  |  | 0 |  | 1 | NEW | Z2-116 |  |  | 1
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY | Z2-116 |  |  | 1
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1186 | 1186 |  |  | -0.00092 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 3.89 |  |  | -0.00095 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.6 | 1.44 |  |  | -0.00095 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
341200 | 2BROMLEYEK | 69 | 320 | 77 | 0 | 2 | 1.35 |  |  | -0.00094 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
246477 | 05NILES | 69 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.00094 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246476 | 05NILES | 34.5 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.00094 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243352 | 05NTRDAM | 138 | 205 | 77 | 0 | 57.6 | 41.21 |  |  | -0.00095 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247967 | 05OLIV SLR E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.00099 |  |  |  | 0 |  | 1 | NEW | OLIV SLR |  |  | 1
244415 | 05OLIV SLR C | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.00099 |  |  |  | 0 |  | 1 | CAPACITY | OLIV SLR |  |  | 1
243353 | 05OLIVE | 138 | 205 | 77 | 0 | 5 | 3.58 |  |  | -0.00099 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 95.86 |  |  | -0.001 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.001 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.001 |  |  |  | 0.036 |  | 1 | CAPACITY | X2-052 |  |  | 1
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.00101 |  |  |  | 0 |  | 1 | CAPACITY | Z2-115 |  |  | 1
247968 | Z2-115 E | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.00101 |  |  |  | 0 |  | 1 | NEW | Z2-115 |  |  | 1
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.00105 |  |  |  | 0 |  | 1 | NEW | U3-002 |  |  | 1
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 6.36 |  |  | -0.00105 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 6.17 |  |  | -0.00105 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.00106 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1356 |  |  | -0.00116 |  |  |  | 0 |  | 1 | CAPACITY | RKG1 |  |  | 1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1300 |  |  | -0.00116 |  |  |  | 0 |  | 1 | CAPACITY | RKG2 |  |  | 1
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 174.1 | 83.88 |  |  | -0.00117 |  |  |  | 0 |  | 1 | NEW | S06 |  |  | 1
930042 | AB1-006 E2 | 0.69 | 205 | 74 | 0 | 96.75 | 46.61 |  |  | -0.00117 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 88.2 | 42.49 |  |  | -0.00117 |  |  |  | 0 |  | 1 | NEW | T127 4 |  |  | 1
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 84.8 | 40.86 |  |  | -0.00117 |  |  |  | 0 |  | 1 | NEW | T126 2 |  |  | 1
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 84.7 | 40.81 |  |  | -0.00117 |  |  |  | 0 |  | 1 | NEW | T126 3 |  |  | 1
247943 | T-127 E | 0.69 | 205 | 74 | 0 | 79.8 | 38.45 |  |  | -0.00117 |  |  |  | 0 |  | 1 | NEW | T127 5 |  |  | 1
930041 | AB1-006 E1 | 0.69 | 205 | 74 | 0 | 77.25 | 37.22 |  |  | -0.00117 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 1
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 12.48 |  |  | -0.00117 |  |  |  | 0 |  | 1 | CAPACITY | S06 |  |  | 1
270180 | AB1-006 W1 | 0.65 | 205 | 74 | 0 | 22.75 | 10.96 |  |  | -0.00117 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 9.73 |  |  | -0.00117 |  |  |  | 0 |  | 1 | CAPACITY | T127 5 |  |  | 1
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 7.37 |  |  | -0.00117 |  |  |  | 0 |  | 1 | CAPACITY | T126 3 |  |  | 1
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 7.32 |  |  | -0.00117 |  |  |  | 0 |  | 1 | CAPACITY | T126 2 |  |  | 1
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 5.68 |  |  | -0.00117 |  |  |  | 0 |  | 1 | CAPACITY | T127 4 |  |  | 1
270181 | AB1-006 W2 | 0.69 | 205 | 74 | 0 | 3.25 | 1.57 |  |  | -0.00117 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 1
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00121 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00121 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00121 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 |  |  | -0.00121 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 62.67 |  |  | -0.00122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 61.87 |  |  | -0.00123 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 76.89 |  |  | -0.00125 |  |  |  | 0 |  | 1 | NEW | Q01 3 |  |  | 1
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 60.22 |  |  | -0.00125 |  |  |  | 0 |  | 1 | NEW | Q01 4 |  |  | 1
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 39.65 |  |  | -0.00125 |  |  |  | 0 |  | 1 | NEW | Q01 21 |  |  | 1
247903 | 05FR-22G E | 0.69 | 205 | 74 | 0 | 78.8 | 37.97 |  |  | -0.00125 |  |  |  | 0 |  | 1 | NEW | Q01 22 |  |  | 1
247900 | 05FR-11G E | 0.6 | 205 | 74 | 0 | 78.3 | 37.72 |  |  | -0.00125 |  |  |  | 0 |  | 1 | NEW | Q01 11 |  |  | 1
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 37.1 |  |  | -0.00125 |  |  |  | 0 |  | 1 | NEW | Q01 12 |  |  | 1
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 18.71 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 18.67 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 18.64 |  |  | -0.00125 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 14.02 |  |  | -0.00125 |  |  |  | 0 |  | 1 | CAPACITY | Q01 4 |  |  | 1
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 12.38 |  |  | -0.00125 |  |  |  | 0 |  | 1 | CAPACITY | Q01 11 |  |  | 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00125 |  |  |  | 0 |  | 1 | CAPACITY | Q01 22 |  |  | 1
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.00125 |  |  |  | 0 |  | 1 | CAPACITY | Q01 21 |  |  | 1
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.00125 |  |  |  | 0 |  | 1 | CAPACITY | Q01 3 |  |  | 1
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.00125 |  |  |  | 0 |  | 1 | CAPACITY | Q01 12 |  |  | 1
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0.41 |  |  | -0.00125 |  |  |  | 0 |  | 1 | NEW | X3-005 |  |  | 1
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 0.25 |  |  | -0.00125 |  |  |  | 0 |  | 1 | CAPACITY | X3-005 |  |  | 1
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | -0.00126 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 1.46 |  |  | -0.00128 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 67.45 |  |  | -0.00127 |  |  |  | 0 |  | 1 | NEW | S37 |  |  | 1
293519 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 67.45 |  |  | -0.00127 |  |  |  | 0 |  | 1 | NEW | S36 |  |  | 1
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 1.03 |  |  | -0.00128 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 20.47 |  |  | -0.00128 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00127 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00127 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00128 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00128 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | -0.00128 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | -0.00127 |  |  |  | 0 |  | 1 | CAPACITY | S36 |  |  | 1
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | -0.00127 |  |  |  | 0 |  | 1 | CAPACITY | S37 |  |  | 1
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 1183 |  |  | -0.00128 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 1154 |  |  | -0.00128 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274661 | LASCO STA;2U | 25 | 222 | 49 | 132 | 1134.8 | 1134.8 |  |  | -0.00129 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274660 | LASCO STA;1U | 25 | 222 | 49 | 135 | 1131.2 | 1131.2 |  |  | -0.00129 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274687 | WILL CNTY;4U | 20 | 222 | 15 | 49.4 | 510 | 510 |  |  | -0.00131 |  |  |  | 0 |  | 1 | CAPACITY | WILL4 |  |  | 1
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 289.95 |  |  | -0.00132 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet8 |  |  | 1
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 293.58 |  |  | -0.00132 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet7 |  |  | 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 160.3 | 184.3 | 70.39 |  |  | -0.00131 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 158.6 | 182.3 | 69.62 |  |  | -0.00131 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 46.55 |  |  | -0.00131 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 46.55 |  |  | -0.00131 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 209.23 |  |  | -0.00132 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet9 |  |  | 1
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 27.95 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00132 |  |  |  | 0.0975 |  | 1 | MTX | Z1-107 |  |  | 1
276617 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 5.88 |  |  | -0.00132 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276642 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | -0.00132 |  |  |  | 0 |  | 1 | CAPACITY | AC1-204 |  |  | 1
276640 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 213.08 |  |  | -0.00132 |  |  |  | 0.036 |  | 1 | CAPACITY | AC1-204 |  |  | 1
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 0 | 150 | 57.29 |  |  | -0.00132 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 73.43 |  |  | -0.00132 |  |  |  | 0 |  | 1 | NEW | P10 |  |  | 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 57.82 |  |  | -0.00132 |  |  |  | 0 |  | 1 | NEW | N15 |  |  | 1
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 13.2 |  |  | -0.00132 |  |  |  | 0 |  | 1 | CAPACITY | N15 |  |  | 1
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 4.91 |  |  | -0.00132 |  |  |  | 0 |  | 1 | CAPACITY | P10 |  |  | 1
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 69.62 |  |  | -0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 69.62 |  |  | -0.00133 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 46.55 |  |  | -0.00133 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 2 |  |  | 1
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 46.55 |  |  | -0.00133 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 1 |  |  | 1
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 80.3 | 30.67 |  |  | -0.00134 |  |  |  | 0.036 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
276618 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 6.71 |  |  | -0.00134 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
276660 | AB1-122 CT2 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | -0.00134 |  |  |  | 0 |  | 1 | CAPACITY | AB1-122 |  |  | 1
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 113.7 | 43.42 |  |  | -0.00135 |  |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
276658 | AB1-122 CT1 | 22.5 | 222 | 58 | 0 | 575 | 219.6 |  |  | -0.00136 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-122 |  |  | 1
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 167 | 63.78 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | -0.00135 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | -0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 58.05 |  |  | -0.00136 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.00137 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00137 |  |  |  | 0.05 |  | 1 | MTX | Z1-106 |  |  | 1
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00137 |  |  |  | 0.0975 |  | 1 | MTX | Z1-106 |  |  | 1
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | -0.00138 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 45.87 |  |  | -0.00138 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 131.6 | 63.4 |  |  | -0.00137 |  |  |  | 0 |  | 1 | NEW | O22 2 |  |  | 1
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 62.88 |  |  | -0.00137 |  |  |  | 0 |  | 1 | NEW | AA1-018 |  |  | 1
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 114.9 | 55.36 |  |  | -0.00137 |  |  |  | 0 |  | 1 | NEW | O22 1 |  |  | 1
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 16.91 |  |  | -0.00137 |  |  |  | 0 |  | 1 | CAPACITY | O22 2 |  |  | 1
270839 | OTTER CRK; R | 345 | 222 | 74 | 0 | 19.5 | 9.4 |  |  | -0.00137 |  |  |  | 0 |  | 1 | CAPACITY | AA1-018 |  |  | 1
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 8.86 |  |  | -0.00137 |  |  |  | 0 |  | 1 | CAPACITY | O22 1 |  |  | 1
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 244.23 |  |  | -0.00139 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK7 |  |  | 1
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | -0.00138 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | -0.00138 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 90.5 | 104 | 39.72 |  |  | -0.00139 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 88.4 | 101.6 | 38.8 |  |  | -0.00139 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 87.5 | 100.6 | 38.42 |  |  | -0.00139 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 24 | 27.6 | 10.54 |  |  | -0.00139 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 263.89 |  |  | -0.00139 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK8 |  |  | 1
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 38.5 |  |  | -0.00139 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.0014 |  |  |  | 0.0975 |  | 1 | MTX | Z1-108 |  |  | 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 10.1 | 6.78 |  |  | -0.0014 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1063 |  |  |  | -0.0014
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 63.01 |  |  | -0.0014 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | -0.0014 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | -0.0014 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 77.09 |  |  | -0.00142 |  |  |  | 0 |  | 1 | NEW | O50 |  |  | 1
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | -0.00142 |  |  |  | 0 |  | 1 | CAPACITY | O50 |  |  | 1
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 197.5 | 95.16 |  |  | -0.00143 |  |  |  | 0 |  | 1 | NEW | Q57 |  |  | 1
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | -0.00143 |  |  |  | 0 |  | 1 | CAPACITY | Q57 |  |  | 1
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00143 |  |  |  | 0.0975 |  | 1 | MTX | AA2-123 |  |  | 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | -0.00144 |  |  |  | 0 |  | 1 | NEW | O51 2 |  |  | 1
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | -0.00144 |  |  |  | 0 |  | 1 | NEW | O51 1 |  |  | 1
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | -0.00144 |  |  |  | 0 |  | 1 | CAPACITY | O51 1 |  |  | 1
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | -0.00144 |  |  |  | 0 |  | 1 | CAPACITY | O51 2 |  |  | 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 42.21 |  |  | -0.00145 |  |  |  | 0 |  | 1 | NEW | P26 |  |  | 1
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 56 | 26.98 |  |  | -0.00145 |  |  |  | 0 |  | 1 | NEW | Z1-073 |  |  | 1
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 22.6 |  |  | -0.00145 |  |  |  | 0 |  | 1 | NEW | WestBrooklyn |  |  | 1
272363 | ESS H440 ; R | 138 | 222 | 2 | 0 | 22 | 0 |  |  | -0.00145 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 10.98 |  |  | -0.00145 |  |  |  | 0 |  | 1 | NEW | Sublette |  |  | 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 10.55 |  |  | -0.00145 |  |  |  | 0 |  | 1 | CAPACITY | P26 |  |  | 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 14.4 | 6.94 |  |  | -0.00145 |  |  |  | 0 |  | 1 | CAPACITY | Z1-073 |  |  | 1
276602 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 3.42 |  |  | -0.00145 |  |  |  | 0 |  | 1 | CAPACITY | WestBrooklyn |  |  | 1
276603 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 1.54 |  |  | -0.00145 |  |  |  | 0 |  | 1 | CAPACITY | Sublette |  |  | 1
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 156.6 | 180 | 68.74 |  |  | -0.00147 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 155.8 | 179.1 | 68.4 |  |  | -0.00147 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 154.7 | 177.8 | 67.9 |  |  | -0.00147 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 4.3 |  |  | -0.00147 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | -0.00148 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | -0.00148 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 32.9 |  |  |  | -0.0015
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.3 | 6.25 |  |  | -0.00149 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
274656 | BYRON ;1U | 25 | 222 | 45 | 648.1 | 1168.5 | 1168.5 |  |  | -0.00148 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274657 | BYRON ;2U | 25 | 222 | 45 | 658.5 | 1141.5 | 1141.5 |  |  | -0.00148 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 83.83 |  |  | -0.0015 |  |  |  | 0 |  | 1 | NEW | Z2-087 |  |  | 1
924049 | AB2-047 E2 | 0.69 | 222 | 74 | 0 | 109.6 | 52.81 |  |  | -0.0015 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
924048 | AB2-047 E1 | 0.69 | 222 | 74 | 0 | 107.9 | 51.99 |  |  | -0.0015 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80.6 | 38.83 |  |  | -0.00149 |  |  |  | 0 |  | 1 | NEW | P46 |  |  | 1
270681 | BRIGHTSTK; R | 345 | 222 | 74 | 0 | 26 | 12.53 |  |  | -0.0015 |  |  |  | 0 |  | 1 | CAPACITY | Z2-087 |  |  | 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 9.35 |  |  | -0.00149 |  |  |  | 0 |  | 1 | CAPACITY | P46 |  |  | 1
276656 | AB2-047 C2 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | -0.0015 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
276655 | AB2-047 C1 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | -0.0015 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | -0.00152 |  |  |  | 0 |  | 1 | NEW | P36 2 |  |  | 1
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | -0.00152 |  |  |  | 0 |  | 1 | NEW | P36 1 |  |  | 1
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 32.12 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | -0.00152 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | -0.00152 |  |  |  | 0 |  | 1 | CAPACITY | P36 2 |  |  | 1
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | -0.00152 |  |  |  | 0 |  | 1 | CAPACITY | P36 1 |  |  | 1
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 28.52 |  |  | -0.00153 |  |  |  | 0 |  | 1 | NEW | O35 |  |  | 1
927209 | AC1-214 E2 | 0.69 | 222 | 74 | 0 | 55.15 | 26.57 |  |  | -0.00153 |  |  |  | 0 |  | 1 | NEW | AC1-214 2 |  |  | 1
916212 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 44.75 | 21.56 |  |  | -0.00153 |  |  |  | 0 |  | 1 | NEW | Z1-072 |  |  | 1
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 14.8 | 7.13 |  |  | -0.00153 |  |  |  | 0 |  | 1 | CAPACITY | O35 |  |  | 1
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 9.7 | 4.67 |  |  | -0.00153 |  |  |  | 0 |  | 1 | CAPACITY | Z1-072 |  |  | 1
276645 | AC1-214 C1 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | -0.00153 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 1 |  |  | 1
276646 | AC1-214 C2 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | -0.00153 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 2 |  |  | 1
927208 | AC1-214 E1 | 0.69 | 222 | 74 | 0 | 5.25 | 2.53 |  |  | -0.00153 |  |  |  | 0 |  | 1 | NEW | AC1-214 1 |  |  | 1
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 64.77 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 64.28 |  |  | -0.00155 |  |  |  | 0.036 |  | 1 | CAPACITY | NELSON |  |  | 1
293516 | O-009 E | 0.69 | 222 | 74 | 0 | 169.6 | 81.71 |  |  | -0.00155 |  |  |  | 0 |  | 1 | NEW | O09 |  |  | 1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 47.32 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 46.9 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 42.26 |  |  | -0.00155 |  |  |  | 0 |  | 1 | NEW | O29 1 |  |  | 1
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 23.17 |  |  | -0.00155 |  |  |  | 0 |  | 1 | NEW | O29 2 |  |  | 1
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 21.3 |  |  | -0.00155 |  |  |  | 0 |  | 1 | NEW | O29 3 |  |  | 1
274881 | WALNUT RG;1U | 0.69 | 222 | 74 | 0 | 42.4 | 20.43 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | O09 |  |  | 1
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 10.55 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | O29 1 |  |  | 1
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 5.78 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | O29 2 |  |  | 1
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 5.35 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | O29 3 |  |  | 1
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 137 | 66.01 |  |  | -0.00156 |  |  |  | 0 |  | 1 | NEW | L05_CE22 |  |  | 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | -0.00155 |  |  |  | 0 |  | 1 | NEW | P11 1 |  |  | 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | -0.00155 |  |  |  | 0 |  | 1 | NEW | P11 2 |  |  | 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | P11 2 |  |  | 1
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | -0.00155 |  |  |  | 0 |  | 1 | CAPACITY | P11 1 |  |  | 1
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 13 | 6.26 |  |  | -0.00156 |  |  |  | 0 |  | 1 | CAPACITY | L05_CE22 |  |  | 1
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 163.2 | 78.63 |  |  | -0.00157 |  |  |  | 0 |  | 1 | NEW | S27 |  |  | 1
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 162.2 | 78.15 |  |  | -0.00157 |  |  |  | 0 |  | 1 | NEW | S28 |  |  | 1
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 17.25 |  |  | -0.00157 |  |  |  | 0 |  | 1 | CAPACITY | S28 |  |  | 1
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 16.77 |  |  | -0.00157 |  |  |  | 0 |  | 1 | CAPACITY | S27 |  |  | 1
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 68.74 |  |  | -0.00164 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | -0.00164 |  |  |  | 0.036 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | -0.00164 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274663 | QUAD CITI;2U | 18 | 222 | 48 | 132 | 911.2 | 911.2 |  |  | -0.00165 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274662 | QUAD CITI;1U | 18 | 222 | 48 | 132 | 909.5 | 909.5 |  |  | -0.00165 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
276174 | W4-005 E | 0.69 | 222 | 74 | 0 | 260.4 | 125.46 |  |  | -0.00167 |  |  |  | 0 |  | 1 | NEW | W4-005 |  |  | 1
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 21.97 |  |  | -0.00167 |  |  |  | 0 |  | 1 | CAPACITY | W4-005 |  |  | 1
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 89.13 |  |  | -0.00171 |  |  |  | 0 |  | 1 | NEW | X2-022 |  |  | 1
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 31.32 |  |  | -0.00171 |  |  |  | 0.1042 |  | 1 | NEW | W2-048 |  |  | 1
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | -0.00179 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | -0.00179 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.002
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 59.6 |  |  |  | -0.0022
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 1348 |  |  |  | -0.0026
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0026
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 18 |  |  |  | -0.003
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0031
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0033
341329 | 2COLESBURG | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | -0.00794 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
936570 | AD2-072_C | 0.6 | 320 | 75 | 0 | 63.75 | 0 |  |  | -0.014 |  |  |  | 0 |  | 1 | CAPACITY | AD2-072 |  |  | 1
936576 | AD2-072_E | 0.6 | 320 | 75 | 0 | 31.25 | 0 |  |  | -0.014 |  |  |  | 0 |  | 1 | NEW | AD2-072 |  |  | 1
342442 | 2W GLASGOW | 69 | 320 | 77 | 0 | 1 | 0.67 |  |  | -0.04306 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
939134 | AE1-143 C | 0.64 | 320 | 75 | 0 | 64.14 | 4.68 |  |  | -0.0871 |  |  |  | 0 |  | 1 | CAPACITY | AE1-143 |  |  | 1
939135 | AE1-143 E | 0.64 | 320 | 75 | 0 | 31.86 | 2.33 |  |  | -0.0871 |  |  |  | 0 |  | 1 | NEW | AE1-143 |  |  | 1

## GD-W194
****** PJM Winter Generator Deliverability Detailed Report ****** PJM [TARA Ver 2101.1.0.0 64-bit - Mon Jun 21 18:04:01 2021]
FG Index [All Queue] | 194 | FG ID | 189 | Monitored Facility:274750 CRETE EC ;BP 345 255112 17STJOHN 345 1 / Contingency:765-L11215_-S_SRT-A[Single]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 80/20 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
1557 | 105.11 | 108.16 | AC | 919.72 | 591.42 | 0 | 105.02 | 20.42 | 1636.58 | 1684.1 | 0.008493 | 0 | 11936 | 0 | 8098.2 | 0.08582 | 3837.86 | 3837.86 | 0 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | FRMP | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited? | Ramping Limit
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.9308 | 1 | CAPACITY |  |  |  | 1
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.8664 | 1 | CAPACITY |  |  |  | 1
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.8064 | 1 | CAPACITY |  |  |  | 1
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 1183 | 1183 | EightyTwenty | 0.15472 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 1154 | 1154 | EightyTwenty | 0.15427 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 131.6 | 63.4 | 105.28 | EightyTwenty | 0.14817 | 6.2046 | 19.499 |  | 0 | 0.7506 | 1 | NEW | O22 2 |  |  | 0.8
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 114.9 | 55.36 | 91.92 | EightyTwenty | 0.14817 | 5.4172 | 17.0246 |  | 0 | 0.7506 | 1 | NEW | O22 1 |  |  | 0.8
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 16.91 | 28.08 | EightyTwenty | 0.14817 | 1.6549 | 5.2007 |  | 0 | 0.7506 | 1 | CAPACITY | O22 2 |  |  | 0.8
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 8.86 | 14.72 | EightyTwenty | 0.14817 | 0.8675 | 2.7263 |  | 0 | 0.7506 | 1 | CAPACITY | O22 1 |  |  | 0.8
274661 | LASCO STA;2U | 25 | 222 | 49 | 132 | 1134.8 | 1134.8 | 1134.8 | EightyTwenty | 0.14585 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274660 | LASCO STA;1U | 25 | 222 | 49 | 135 | 1131.2 | 1131.2 | 1131.2 | EightyTwenty | 0.14584 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274687 | WILL CNTY;4U | 20 | 222 | 15 | 49.4 | 510 | 510 | 510 | EightyTwenty | 0.14193 |  |  |  | 0 | 0.7506 | 1 | CAPACITY | WILL4 |  |  | 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 69.62 | 182.3 | EightyTwenty | 0.14051 | 15.8321 | 25.6143 |  | 0.036 | 0.7236 | 1 | CAPACITY | Kendall 2 |  |  | 1
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 69.62 | 182.3 | EightyTwenty | 0.14051 | 15.8321 | 25.6143 |  | 0.036 | 0.6976 | 1 | CAPACITY | Kendall 1 |  |  | 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 46.55 | 121.9 | EightyTwenty | 0.14051 | 10.5866 | 17.1277 |  | 0 | 0.7236 | 1 | CAPACITY | Kendall 2 |  |  | 1
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 46.55 | 121.9 | EightyTwenty | 0.14051 | 10.5866 | 17.1277 |  | 0 | 0.6976 | 1 | CAPACITY | Kendall 1 |  |  | 1
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 73.43 | 121.92 | EightyTwenty | 0.13923 | 6.7518 | 21.2185 |  | 0 | 0.6976 | 1 | NEW | P10 |  |  | 0.8
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 57.82 | 96 | EightyTwenty | 0.13923 | 5.3163 | 16.7075 |  | 0 | 0.6976 | 1 | NEW | N15 |  |  | 0.8
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 13.2 | 21.92 | EightyTwenty | 0.13923 | 1.2139 | 3.8149 |  | 0 | 0.6976 | 1 | CAPACITY | N15 |  |  | 0.8
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 4.91 | 8.16 | EightyTwenty | 0.13923 | 0.4519 | 1.4201 |  | 0 | 0.6976 | 1 | CAPACITY | P10 |  |  | 0.8
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 289.95 | 518 | EightyTwenty | 0.13919 | 31.742 | 72.1002 |  | 0.1042 | 0.6249 | 1 | CAPACITY | Joliet8 |  |  | 1
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 293.58 | 518 | EightyTwenty | 0.1391 | 31.2172 | 72.0541 |  | 0.1042 | 0.5598 | 1 | CAPACITY | Joliet7 |  |  | 1
276642 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 213.08 | 557.95 | EightyTwenty | 0.13774 | 47.5026 | 76.8533 |  | 0 | 0.5396 | 1 | CAPACITY | AC1-204 |  |  | 1
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.5023 | 1 | CAPACITY |  |  |  | 1
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.4675 | 1 | CAPACITY |  |  |  | 1
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.4352 | 1 | CAPACITY |  |  |  | 1
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.405 | 1 | CAPACITY |  |  |  | 1
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.377 | 1 | CAPACITY |  |  |  | 1
276640 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 213.08 | 557.95 | EightyTwenty | 0.13748 | 47.4136 | 76.7093 |  | 0.036 | 0.5396 | 1 | CAPACITY | AC1-204 |  |  | 1
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.3509 | 1 | CAPACITY |  |  |  | 1
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.3266 | 1 | CAPACITY |  |  |  | 1
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.304 | 1 | CAPACITY |  |  |  | 1
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.283 | 1 | CAPACITY |  |  |  | 1
276660 | AB1-122 CT2 | 22.5 | 222 | 58 | 0 | 575 | 219.6 | 575 | EightyTwenty | 0.13655 | 48.5314 | 78.5176 |  | 0 | 0.2728 | 1 | CAPACITY | AB1-122 |  |  | 1
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 167 | 63.78 | 167 | EightyTwenty | 0.13132 | 13.5553 | 21.9307 |  | 0.0692 | 0.2539 | 1 | CAPACITY |  |  |  | 1
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 167 | 63.78 | 167 | EightyTwenty | 0.13132 | 13.5553 | 21.9307 |  | 0.0692 | 0.2364 | 1 | CAPACITY |  |  |  | 1
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 58.05 | 152 | EightyTwenty | 0.13111 | 12.3181 | 19.9293 |  | 0.0692 | 0.22 | 1 | CAPACITY |  |  |  | 1
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 58.05 | 152 | EightyTwenty | 0.13111 | 12.3181 | 19.9293 |  | 0.0692 | 0.2048 | 1 | CAPACITY |  |  |  | 1
276658 | AB1-122 CT1 | 22.5 | 222 | 58 | 0 | 575 | 219.6 | 575 | EightyTwenty | 0.12575 | 44.691 | 72.3043 |  | 0.036 | 0.2728 | 1 | CAPACITY | AB1-122 |  |  | 1
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 32.9 |  | 32.9 | CLTF | 0.12226 | 4.0223 | 4.0223 | 0.2794
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  | 158.9 | CLTF | 0.08095 | 12.8624 | 12.8624 | 1.3495
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1063 |  | 1063 | LTF/CBM | 0.04958 | 52.7027 | 52.7027 | 9.028
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.0209 | 1.1556 | 1.1556 | -0.4697
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 1348 |  | 1348 | LTF/CBM | 0.01933 | 26.0567 | 26.0567 | 11.4485
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  | 175 | CLTF | 0.01763 | 3.086 | 3.086 | 1.4863
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.01298 | 0.7225 | 0.7225 | -0.4726
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.3 |  | 173.3 | CLTF | 0.01226 | 2.1237 | 2.1237 | -1.4714
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.01053 | 0.6082 | 0.6082 | -0.4905
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.0093 | 0.3256 | 0.3256 | -0.2973
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  | 140 | CLTF | 0.00679 | 0.9508 | 0.9508 | 1.189
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 18 |  | 18 | LTF/CBM | 0.00343 | 0.0617 | 0.0617 | 0.1529
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00294 | 0.147 | 0.147 | -0.4251
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00275 | 0.1367 | 0.1367 | -0.4221
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00111 | 0.0607 | 0.0607 | -0.4637
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 113.7 | 43.42 |  |  | 0.13062 |  |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | 0.13058 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.13058 |  |  |  | 0.0975 |  | 1 | MTX | Z1-106 |  |  | 1
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.13058 |  |  |  | 0.05 |  | 1 | MTX | Z1-106 |  |  | 1
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 244.23 |  |  | 0.13047 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK7 |  |  | 1
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 263.89 |  |  | 0.13012 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK8 |  |  | 1
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 38.5 |  |  | 0.13012 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 45.87 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276618 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 6.71 |  |  | 0.12969 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 160.3 | 184.3 | 70.39 |  |  | 0.12961 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 158.6 | 182.3 | 69.62 |  |  | 0.12961 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 46.55 |  |  | 0.12961 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 46.55 |  |  | 0.12961 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 88.4 | 101.6 | 38.8 |  |  | 0.12944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 87.5 | 100.6 | 38.42 |  |  | 0.12944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 24 | 27.6 | 10.54 |  |  | 0.12944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 90.5 | 104 | 39.72 |  |  | 0.12943 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.12921 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 63.01 |  |  | 0.12921 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.12921 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 80.3 | 30.67 |  |  | 0.12904 |  |  |  | 0.036 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.12854 |  |  |  | 0.0975 |  | 1 | MTX | Z1-108 |  |  | 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 10.1 | 6.78 |  |  | 0.12838 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 209.23 |  |  | 0.12706 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet9 |  |  | 1
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 77.09 |  |  | 0.12698 |  |  |  | 0 |  | 1 | NEW | O50 |  |  | 0.8
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.12698 |  |  |  | 0 |  | 1 | CAPACITY | O50 |  |  | 0.8
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.12657 |  |  |  | 0.0975 |  | 1 | MTX | Z1-107 |  |  | 1
276617 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 5.88 |  |  | 0.12657 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
293519 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.12651 |  |  |  | 0 |  | 1 | NEW | S36 |  |  | 0.8
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.12651 |  |  |  | 0 |  | 1 | NEW | S37 |  |  | 0.8
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.12651 |  |  |  | 0 |  | 1 | CAPACITY | S36 |  |  | 0.8
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.12651 |  |  |  | 0 |  | 1 | CAPACITY | S37 |  |  | 0.8
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.12586 |  |  |  | 0.0975 |  | 1 | MTX | AA2-123 |  |  | 1
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 197.5 | 95.16 |  |  | 0.12518 |  |  |  | 0 |  | 1 | NEW | Q57 |  |  | 0.8
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.12518 |  |  |  | 0 |  | 1 | CAPACITY | Q57 |  |  | 0.8
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 1.46 |  |  | 0.12335 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 1.03 |  |  | 0.12335 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
272363 | ESS H440 ; R | 138 | 222 | 2 | 0 | 22 | 0 |  |  | 0.12308 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 42.21 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | P26 |  |  | 0.8
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 56 | 26.98 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | Z1-073 |  |  | 0.8
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 22.6 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | WestBrooklyn |  |  | 0.8
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 10.98 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | Sublette |  |  | 0.8
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 10.55 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | P26 |  |  | 0.8
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 14.4 | 6.94 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | Z1-073 |  |  | 0.8
276602 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 3.42 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | WestBrooklyn |  |  | 0.8
276603 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 1.54 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | Sublette |  |  | 0.8
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 4.3 |  |  | 0.12209 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 156.6 | 180 | 68.74 |  |  | 0.12193 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 155.8 | 179.1 | 68.4 |  |  | 0.12193 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 154.7 | 177.8 | 67.9 |  |  | 0.12193 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 62.88 |  |  | 0.12155 |  |  |  | 0 |  | 1 | NEW | AA1-018 |  |  | 0.8
270839 | OTTER CRK; R | 345 | 222 | 74 | 0 | 19.5 | 9.4 |  |  | 0.12155 |  |  |  | 0 |  | 1 | CAPACITY | AA1-018 |  |  | 0.8
274656 | BYRON ;1U | 25 | 222 | 45 | 648.1 | 1168.5 | 1168.5 |  |  | 0.12122 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274657 | BYRON ;2U | 25 | 222 | 45 | 658.5 | 1141.5 | 1141.5 |  |  | 0.12122 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.3 | 6.25 |  |  | 0.12033 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80.6 | 38.83 |  |  | 0.12 |  |  |  | 0 |  | 1 | NEW | P46 |  |  | 0.8
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 9.35 |  |  | 0.12 |  |  |  | 0 |  | 1 | CAPACITY | P46 |  |  | 0.8
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.11924 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.11908 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.11732 |  |  |  | 0 |  | 1 | NEW | P36 2 |  |  | 0.8
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.11732 |  |  |  | 0 |  | 1 | NEW | P36 1 |  |  | 0.8
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 32.12 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.11732 |  |  |  | 0 |  | 1 | CAPACITY | P36 1 |  |  | 0.8
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.11732 |  |  |  | 0 |  | 1 | CAPACITY | P36 2 |  |  | 0.8
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11489 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11489 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 64.77 |  |  | 0.11475 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 64.28 |  |  | 0.11475 |  |  |  | 0.036 |  | 1 | CAPACITY | NELSON |  |  | 1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 47.32 |  |  | 0.11475 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 46.9 |  |  | 0.11475 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
293516 | O-009 E | 0.69 | 222 | 74 | 0 | 169.6 | 81.71 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O09 |  |  | 0.8
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 42.26 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O29 1 |  |  | 0.8
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 23.17 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O29 2 |  |  | 0.8
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 21.3 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O29 3 |  |  | 0.8
274881 | WALNUT RG;1U | 0.69 | 222 | 74 | 0 | 42.4 | 20.43 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O09 |  |  | 0.8
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 10.55 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O29 1 |  |  | 0.8
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 5.78 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O29 2 |  |  | 0.8
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 5.35 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O29 3 |  |  | 0.8
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 20.47 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 28.52 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | O35 |  |  | 0.8
927209 | AC1-214 E2 | 0.69 | 222 | 74 | 0 | 55.15 | 26.57 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | AC1-214 2 |  |  | 0.8
916212 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 44.75 | 21.56 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | Z1-072 |  |  | 0.8
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 14.8 | 7.13 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | O35 |  |  | 0.8
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 9.7 | 4.67 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | Z1-072 |  |  | 0.8
276645 | AC1-214 C1 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 1 |  |  | 0.8
276646 | AC1-214 C2 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 2 |  |  | 0.8
927208 | AC1-214 E1 | 0.69 | 222 | 74 | 0 | 5.25 | 2.53 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | AC1-214 1 |  |  | 0.8
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.10919 |  |  |  | 0 |  | 1 | NEW | P11 1 |  |  | 0.8
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.10919 |  |  |  | 0 |  | 1 | NEW | P11 2 |  |  | 0.8
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.10919 |  |  |  | 0 |  | 1 | CAPACITY | P11 1 |  |  | 0.8
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.10919 |  |  |  | 0 |  | 1 | CAPACITY | P11 2 |  |  | 0.8
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 137 | 66.01 |  |  | 0.10762 |  |  |  | 0 |  | 1 | NEW | L05_CE22 |  |  | 0.8
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 13 | 6.26 |  |  | 0.10762 |  |  |  | 0 |  | 1 | CAPACITY | L05_CE22 |  |  | 0.8
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 68.74 |  |  | 0.10647 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.10647 |  |  |  | 0.036 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.10647 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274663 | QUAD CITI;2U | 18 | 222 | 48 | 132 | 911.2 | 911.2 |  |  | 0.10644 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274662 | QUAD CITI;1U | 18 | 222 | 48 | 132 | 909.5 | 909.5 |  |  | 0.10637 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 18.71 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 18.67 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 18.64 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.09688 |  |  |  | 0 |  | 1 | NEW | O51 1 |  |  | 0.8
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.09688 |  |  |  | 0 |  | 1 | NEW | O51 2 |  |  | 0.8
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.09688 |  |  |  | 0 |  | 1 | CAPACITY | O51 2 |  |  | 0.8
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.09688 |  |  |  | 0 |  | 1 | CAPACITY | O51 1 |  |  | 0.8
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 83.83 |  |  | 0.09145 |  |  |  | 0 |  | 1 | NEW | Z2-087 |  |  | 0.8
924049 | AB2-047 E2 | 0.69 | 222 | 74 | 0 | 109.6 | 52.81 |  |  | 0.09145 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 0.8
924048 | AB2-047 E1 | 0.69 | 222 | 74 | 0 | 107.9 | 51.99 |  |  | 0.09145 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 0.8
270681 | BRIGHTSTK; R | 345 | 222 | 74 | 0 | 26 | 12.53 |  |  | 0.09145 |  |  |  | 0 |  | 1 | CAPACITY | Z2-087 |  |  | 0.8
276655 | AB2-047 C1 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.09145 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 0.8
276656 | AB2-047 C2 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.09145 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 0.8
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0.41 |  |  | 0.0897 |  |  |  | 0 |  | 1 | NEW | X3-005 |  |  | 0.1
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 0.25 |  |  | 0.0897 |  |  |  | 0 |  | 1 | CAPACITY | X3-005 |  |  | 0.1
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 163.2 | 78.63 |  |  | 0.08104 |  |  |  | 0 |  | 1 | NEW | S27 |  |  | 0.8
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 162.2 | 78.15 |  |  | 0.08104 |  |  |  | 0 |  | 1 | NEW | S28 |  |  | 0.8
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 17.25 |  |  | 0.08104 |  |  |  | 0 |  | 1 | CAPACITY | S28 |  |  | 0.8
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 16.77 |  |  | 0.08104 |  |  |  | 0 |  | 1 | CAPACITY | S27 |  |  | 0.8
276174 | W4-005 E | 0.69 | 222 | 74 | 0 | 260.4 | 125.46 |  |  | 0.06741 |  |  |  | 0 |  | 1 | NEW | W4-005 |  |  | 0.8
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 21.97 |  |  | 0.06741 |  |  |  | 0 |  | 1 | CAPACITY | W4-005 |  |  | 0.8
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 89.13 |  |  | 0.06612 |  |  |  | 0 |  | 1 | NEW | X2-022 |  |  | 0.8
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 31.32 |  |  | 0.06612 |  |  |  | 0.1042 |  | 1 | NEW | W2-048 |  |  | 0.8
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 61.87 |  |  | 0.06586 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.05944 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.05942 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 62.67 |  |  | 0.0536 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | 0.0205
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | 0.0205
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0025
342442 | 2W GLASGOW | 69 | 320 | 77 | 0 | 1 | 0.67 |  |  | -0.00289 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
939134 | AE1-143 C | 0.64 | 320 | 75 | 0 | 64.14 | 4.68 |  |  | -0.00755 |  |  |  | 0 |  | 1 | CAPACITY | AE1-143 |  |  | 0.1
939135 | AE1-143 E | 0.64 | 320 | 75 | 0 | 31.86 | 2.33 |  |  | -0.00755 |  |  |  | 0 |  | 1 | NEW | AE1-143 |  |  | 0.1
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 85.93 |  |  | -0.00846 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 44.3 |  |  | -0.00845 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
341329 | 2COLESBURG | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | -0.00859 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 682 |  |  |  | -0.009
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 38.84 |  |  | -0.00936 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
342070 | 2PINE GROVE | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | -0.01011 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
936570 | AD2-072_C | 0.6 | 320 | 75 | 0 | 63.75 | 0 |  |  | -0.01142 |  |  |  | 0 |  | 1 | CAPACITY | AD2-072 |  |  | 0.1
936576 | AD2-072_E | 0.6 | 320 | 75 | 0 | 31.25 | 0 |  |  | -0.01142 |  |  |  | 0 |  | 1 | NEW | AD2-072 |  |  | 0.1
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 94.5 |  |  |  | -0.0117
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 59.6 |  |  |  | -0.0119
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1300 |  |  | -0.012 |  |  |  | 0 |  | 1 | CAPACITY | RKG2 |  |  | 1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1356 |  |  | -0.012 |  |  |  | 0 |  | 1 | CAPACITY | RKG1 |  |  | 1
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | -0.01257 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | -0.01257 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01257 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 93.75 |  |  | -0.01349 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG2 |  |  | 1
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 125.1 | 93.15 |  |  | -0.01349 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG1 |  |  | 1
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 78.63 |  |  | -0.01349 |  |  |  | 0 |  | 1 | CAPACITY | CRG2 |  |  | 1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 104.7 | 77.96 |  |  | -0.01349 |  |  |  | 0 |  | 1 | CAPACITY | CRG1 |  |  | 1
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 610.3 |  |  | -0.01349 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 42.01 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 108.1 | 41.28 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 106.7 | 40.75 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 27.88 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 70.9 | 27.08 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316222 | AC1-221 C | 0.6 | 345 | 75 | 0 | 51.2 | 7.68 |  |  | -0.0137 |  |  |  | 0 |  | 1 | CAPACITY | AC1-221 |  |  | 0.1
316283 | AC2-100 C | 0.57 | 345 | 75 | 0 | 45.6 | 6.84 |  |  | -0.0137 |  |  |  | 0 |  | 1 | CAPACITY | AC2-100 |  |  | 0.1
932763 | AC2-100 E | 0.57 | 345 | 75 | 0 | 16.4 | 2.46 |  |  | -0.0137 |  |  |  | 0 |  | 1 | NEW | AC2-100 |  |  | 0.1
927255 | AC1-221 E | 0.6 | 345 | 75 | 0 | 14.6 | 2.19 |  |  | -0.0137 |  |  |  | 0 |  | 1 | NEW | AC1-221 |  |  | 0.1
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | -0.01382 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | -0.01382 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315131 | 1EDGECMA | 13.8 | 345 | 11 | 7.5 | 58 | 0 |  |  | -0.01408 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 9.9 |  |  | -0.01409 |  |  |  | 0 |  | 1 | CAPACITY | AB2-059 |  |  | 0.1
316049 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 8.4 |  |  | -0.01409 |  |  |  | 0 |  | 1 | CAPACITY | AB1-081 |  |  | 0.1
316263 | AC1-034 C | 0.55 | 345 | 75 | 0 | 42.75 | 6.41 |  |  | -0.01409 |  |  |  | 0 |  | 1 | CAPACITY | AC1-034 |  |  | 0.1
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 5.1 |  |  | -0.01409 |  |  |  | 0 |  | 1 | NEW | AB2-059 |  |  | 0.1
925595 | AC1-034 E | 0.55 | 345 | 75 | 0 | 32.25 | 4.84 |  |  | -0.01409 |  |  |  | 0 |  | 1 | NEW | AC1-034 |  |  | 0.1
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01409 |  |  |  | 0 |  | 1 | NEW | AB1-081 |  |  | 0.1
341200 | 2BROMLEYEK | 69 | 320 | 77 | 0 | 2 | 1.35 |  |  | -0.01413 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | -0.01426 |  |  |  | 0 |  | 1 | CAPACITY | Z2-088 |  |  | 0.1
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | -0.01426 |  |  |  | 0 |  | 1 | NEW | Z2-088 |  |  | 0.1
316319 | Z2-044 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | -0.01427 |  |  |  | 0 |  | 1 | CAPACITY | Z2-044 |  |  | 0.1
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0.54 |  |  | -0.01427 |  |  |  | 0 |  | 1 | NEW | Z2-044 |  |  | 0.1
316005 | AA1-067 C | 230 | 345 | 75 | 0 | 10.5 | 1.58 |  |  | -0.01445 |  |  |  | 0 |  | 1 | CAPACITY | AA1-067 |  |  | 0.1
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0.68 |  |  | -0.01445 |  |  |  | 0 |  | 1 | NEW | AA1-067 |  |  | 0.1
244012 | 05PINNACLE | 4 | 205 | 75 | 0 | 11 | 0.8 |  |  | -0.01455 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
316327 | AA2-057 C | 0.63 | 345 | 75 | 0 | 50 | 7.5 |  |  | -0.01457 |  |  |  | 0 |  | 1 | CAPACITY | AA2-057 |  |  | 0.1
919710 | AA2-057 E | 0.63 | 345 | 75 | 0 | 24.9 | 3.73 |  |  | -0.01457 |  |  |  | 0 |  | 1 | NEW | AA2-057 |  |  | 0.1
316210 | AC1-098 C | 0.6 | 345 | 75 | 0 | 37.6 | 5.64 |  |  | -0.01467 |  |  |  | 0 |  | 1 | CAPACITY | AC1-098 |  |  | 0.1
926206 | AC1-098 E | 0.6 | 345 | 75 | 0 | 22.4 | 3.36 |  |  | -0.01467 |  |  |  | 0 |  | 1 | NEW | AC1-098 |  |  | 0.1
316212 | AC1-099 C | 0.6 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | -0.01467 |  |  |  | 0 |  | 1 | CAPACITY | AC1-099 |  |  | 0.1
926214 | AC1-099 E | 0.6 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | -0.01467 |  |  |  | 0 |  | 1 | NEW | AC1-099 |  |  | 0.1
316274 | AC1-208 C | 0.38 | 345 | 75 | 0 | 55.4 | 8.31 |  |  | -0.01473 |  |  |  | 0 |  | 1 | CAPACITY | AC1-208 |  |  | 0.1
927146 | AC1-208 E | 0.38 | 345 | 75 | 0 | 24.5 | 0 |  |  | -0.01473 |  |  |  | 0 |  | 1 | NEW | AC1-208 |  |  | 0.1
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 15 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
TILTON | PJM->LTFIMP_TILTON |  |  | LTF |  | 63 |  |  |  | -0.015
316174 | AB2-169_C | 0.63 | 345 | 75 | 0 | 39 | 5.85 |  |  | -0.01498 |  |  |  | 0 |  | 1 | CAPACITY | AB2-169 |  |  | 0.1
925122 | AB2-169 E | 0.63 | 345 | 75 | 0 | 35 | 5.25 |  |  | -0.01498 |  |  |  | 0 |  | 1 | NEW | AB2-169 |  |  | 0.1
316248 | AF1-058 C | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01497 |  |  |  | 0 |  | 1 | CAPACITY | AF1-058 |  |  | 0.1
943902 | AF1-058 E | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01497 |  |  |  | 0 |  | 1 | NEW | AF1-058 |  |  | 0.1
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 45.6 |  |  | -0.01499 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 6.68 |  |  | -0.01501 |  |  |  | 0 |  | 1 | CAPACITY | AC1-054 |  |  | 0.1
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 3.08 |  |  | -0.01501 |  |  |  | 0 |  | 1 | NEW | AC1-054 |  |  | 0.1
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 5.18 |  |  | -0.01503 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 0.1
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 2.54 |  |  | -0.01503 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 0.1
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 74.1 | 55.58 |  |  | -0.01505 |  |  |  | 0.036 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 45.9 | 34.43 |  |  | -0.01505 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
270183 | AB2-010_C | 138 | 205 | 75 | 0 | 10 | 0.73 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 0.1
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 34.7 | 26.03 |  |  | -0.01505 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
270182 | AB2-011_C | 138 | 205 | 75 | 0 | 8 | 0.58 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 0.1
923772 | AB2-011_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 0.1
923762 | AB2-010_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 0.1
316003 | AC1-222 C | 0.6 | 345 | 75 | 0 | 38.8 | 5.82 |  |  | -0.01508 |  |  |  | 0 |  | 1 | CAPACITY | AC1-222 |  |  | 0.1
927264 | AC1-222 E | 0.6 | 345 | 75 | 0 | 25.9 | 3.88 |  |  | -0.01508 |  |  |  | 0 |  | 1 | NEW | AC1-222 |  |  | 0.1
316317 | KELFORD C | 115 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01511 |  |  |  | 0 |  | 1 | CAPACITY | Z2-043 |  |  | 0.1
917332 | KELFORD E | 115 | 345 | 75 | 0 | 7 | 1.05 |  |  | -0.01511 |  |  |  | 0 |  | 1 | NEW | Z2-043 |  |  | 0.1
316011 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 12.6 |  |  | -0.01519 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 0.1
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | -0.01519 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 0.1
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 50.3 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 48 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 8.22 |  |  | -0.01521 |  |  |  | 0 |  | 1 | CAPACITY | AA2-053 |  |  | 0.1
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 3.38 |  |  | -0.01521 |  |  |  | 0 |  | 1 | NEW | AA2-053 |  |  | 0.1
316238 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 0.1
316239 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 0.1
316237 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 0.1
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 0.1
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 0.1
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 0.1
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.01525 |  |  |  | 0 |  | 1 | NEW | AB2-043 |  |  | 0.1
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 2.84 |  |  | -0.01525 |  |  |  | 0 |  | 1 | CAPACITY | AB2-043 |  |  | 0.1
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 8.16 |  |  | -0.01527 |  |  |  | 0 |  | 1 | CAPACITY | AB2-060 |  |  | 0.1
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 3.84 |  |  | -0.01527 |  |  |  | 0 |  | 1 | NEW | AB2-060 |  |  | 0.1
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 37.51 |  |  | -0.01529 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
316243 | AE2-151 C | 115 | 345 | 75 | 0 | 6.5 | 0.98 |  |  | -0.01528 |  |  |  | 0 |  | 1 | CAPACITY | AE2-151 |  |  | 0.1
941542 | AE2-151 E | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | -0.01528 |  |  |  | 0 |  | 1 | NEW | AE2-151 |  |  | 0.1
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 67 | 10.05 |  |  | -0.01533 |  |  |  | 0 |  | 1 | CAPACITY | AA1-065 |  |  | 0.1
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01533 |  |  |  | 0 |  | 1 | NEW | AA1-065 |  |  | 0.1
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | -0.01534 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 0.1
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0.22 |  |  | -0.01534 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 0.1
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 7.64 |  |  | -0.01535 |  |  |  | 0 |  | 1 | CAPACITY | AA1-063A |  |  | 0.1
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01535 |  |  |  | 0 |  | 1 | NEW | AA1-063A |  |  | 0.1
923994 | AB2-040_E | 0.6 | 345 | 75 | 0 | 69.51 | 10.43 |  |  | -0.01538 |  |  |  | 0 |  | 1 | NEW | AB2-040 |  |  | 0.1
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 6.06 |  |  | -0.01538 |  |  |  | 0 |  | 1 | CAPACITY | AB1-173 |  |  | 0.1
316181 | AB2-040 GEN | 0.6 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01538 |  |  |  | 0 |  | 1 | CAPACITY | AB2-040 |  |  | 0.1
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | -0.01538 |  |  |  | 0 |  | 1 | NEW | AB1-173 |  |  | 0.1
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 6.3 |  |  | -0.01542 |  |  |  | 0 |  | 1 | CAPACITY | AB2-174 |  |  | 0.1
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 5.7 |  |  | -0.01542 |  |  |  | 0 |  | 1 | NEW | AB2-174 |  |  | 0.1
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 11 |  |  | -0.01545 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 5.74 |  |  | -0.01547 |  |  |  | 0 |  | 1 | CAPACITY | AC1-075 |  |  | 0.1
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 3.26 |  |  | -0.01547 |  |  |  | 0 |  | 1 | NEW | AC1-075 |  |  | 0.1
316205 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 1.92 |  |  | -0.01547 |  |  |  | 0 |  | 1 | CAPACITY | AC1-080 |  |  | 0.1
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 1.08 |  |  | -0.01547 |  |  |  | 0 |  | 1 | NEW | AC1-080 |  |  | 0.1
316318 | V4-068 C | 115 | 345 | 75 | 0 | 3.2 | 0.48 |  |  | -0.0155 |  |  |  | 0 |  | 1 | CAPACITY | V4-068 |  |  | 0.1
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.0155 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0.27 |  |  | -0.0155 |  |  |  | 0 |  | 1 | NEW | V4-068 |  |  | 0.1
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.2 | 441.2 |  |  | -0.01553 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 437.1 |  |  | -0.01553 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 1.39 |  |  | -0.01558 |  |  |  | 0 |  | 1 | NEW | AC1-036 |  |  | 0.1
316034 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 1.29 |  |  | -0.01558 |  |  |  | 0 |  | 1 | CAPACITY | AC1-036 |  |  | 0.1
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | -0.0156 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 0.1
270130 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0.56 |  |  | -0.0156 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 0.1
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | -0.01563 |  |  |  | 0 |  | 1 | NEW | AA2-088 |  |  | 0.1
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | -0.01563 |  |  |  | 0 |  | 1 | CAPACITY | AA2-088 |  |  | 0.1
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | -0.01569 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 1 |  |  | 0.1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | -0.01569 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 2 |  |  | 0.1
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | -0.01569 |  |  |  | 0 |  | 1 | NEW | AB2-100 1 |  |  | 0.1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | -0.01569 |  |  |  | 0 |  | 1 | NEW | AB2-100 2 |  |  | 0.1
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 8.4 |  |  | -0.01573 |  |  |  | 0 |  | 1 | CAPACITY | AA2-178 |  |  | 0.1
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01573 |  |  |  | 0 |  | 1 | NEW | AA2-178 |  |  | 0.1
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 422.31 |  |  | -0.01578 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | -0.01578 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | -0.01578 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | -0.01578 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 15.7 | 10.53 |  |  | -0.01586 |  |  |  | 0.1097 |  | 1 | CAPACITY | AMELIA LF_1-A |  |  | 1
313853 | 3PONTONDP | 115 | 345 | 65 | 0 | 4 | 0 |  |  | -0.01586 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53 | 53 |  |  | -0.01585 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 448.57 |  |  | -0.01587 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | -0.01587 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | -0.01587 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | -0.01587 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
314541 | 3WATKINS | 115 | 345 | 75 | 0 | 4 | 0.6 |  |  | -0.01587 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 7.5 |  |  | -0.01591 |  |  |  | 0 |  | 1 | CAPACITY | AB2-015 |  |  | 0.1
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 6.15 |  |  | -0.01591 |  |  |  | 0 |  | 1 | NEW | AB2-015 |  |  | 0.1
961092 | AF2-400 E | 115 | 345 | 75 | 0 | 4.43 | 0.66 |  |  | -0.01591 |  |  |  | 0 |  | 1 | NEW | af2-400 |  |  | 0.1
316300 | AF2-400 C | 115 | 345 | 75 | 0 | 2.71 | 0.41 |  |  | -0.01591 |  |  |  | 0 |  | 1 | CAPACITY | AF2-400 |  |  | 0.1
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 4.44 |  |  | -0.01593 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
316074 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 1.35 |  |  | -0.01596 |  |  |  | 0 |  | 1 | CAPACITY | AD1-157 |  |  | 0.1
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01596 |  |  |  | 0 |  | 1 | NEW | AD1-157 |  |  | 0.1
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.01598 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 52.4 |  |  | -0.01604 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 107.08 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 105.41 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 67.13 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 41.06 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 39.39 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 258.69 |  |  | -0.01606 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 0.8
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | -0.01606 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 0.8
251298 | 08CRITDN | 69 | 212 | 77 | 0 | 2.7 | 1.9 |  |  | -0.01606 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.2 | 27.3 |  |  | -0.01608 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.0161 |  |  |  | 0 |  | 1 | NEW | AC1-145 |  |  | 0.1
925665 | AC1-042 E | 0.4 | 345 | 75 | 0 | 26.04 | 3.91 |  |  | -0.0161 |  |  |  | 0 |  | 1 | NEW | AC1-042 |  |  | 0.1
316217 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 2.85 |  |  | -0.0161 |  |  |  | 0 |  | 1 | CAPACITY | AC1-145 |  |  | 0.1
316197 | AC1-042 C | 0.4 | 345 | 75 | 0 | 15.96 | 2.39 |  |  | -0.0161 |  |  |  | 0 |  | 1 | CAPACITY | AC1-042 |  |  | 0.1
316315 | AB2-025 C | 230 | 345 | 75 | 0 | 13.65 | 2.05 |  |  | -0.01619 |  |  |  | 0 |  | 1 | CAPACITY | AB2-025 |  |  | 0.1
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | -0.01619 |  |  |  | 0 |  | 1 | NEW | AB2-025 |  |  | 0.1
901082 | W1-029 E | 230 | 345 | 74 | 0 | 169 | 167.31 |  |  | -0.01624 |  |  |  | 0 |  | 1 | NEW | W1-029 |  |  | 0.8
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | -0.01624 |  |  |  | 0 |  | 1 | CAPACITY | W1-029 |  |  | 0.8
316321 | Z2-027 C | 230 | 345 | 75 | 0 | 13.8 | 2.07 |  |  | -0.0163 |  |  |  | 0 |  | 1 | CAPACITY | Z2-027 |  |  | 0.1
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.0163 |  |  |  | 0 |  | 1 | NEW | Z2-027 |  |  | 0.1
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 30.18 |  |  | -0.01631 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 0.8
270111 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 4.51 |  |  | -0.01631 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 0.8
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 12.2 | 6.77 |  |  | -0.01632 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.01632 |  |  |  | 0.0789 |  | 1 | ENERGY |  |  |  | 1
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.1 | 5.05 |  |  | -0.01632 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.01632 |  |  |  | 0 |  | 1 | MTX | AD2-205 |  |  | 1
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 1.95 |  |  | -0.01634 |  |  |  | 0 |  | 1 | CAPACITY | AB2-022 |  |  | 0.1
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 1.86 |  |  | -0.01634 |  |  |  | 0 |  | 1 | NEW | Y1-086 |  |  | 0.1
316320 | Y1-086 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | -0.01634 |  |  |  | 0 |  | 1 | CAPACITY | Y1-086 |  |  | 0.1
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 1.05 |  |  | -0.01634 |  |  |  | 0 |  | 1 | NEW | AB2-022 |  |  | 0.1
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 10.06 |  |  | -0.01643 |  |  |  | 0.44065 |  | 1 | CAPACITY |  |  |  | 1
316305 | AF2-043 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AF2-043 |  |  | 0.1
316244 | AE2-225 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AE2-225 |  |  | 0.1
316246 | AF1-032 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AF1-032 |  |  | 0.1
316245 | AE2-229 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AE2-229 |  |  | 0.1
957492 | AF2-043 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AF2-043 |  |  | 0.1
942132 | AE2-225 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AE2-225 |  |  | 0.1
942172 | AE2-229 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AE2-229 |  |  | 0.1
943612 | AF1-032 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AF1-032 |  |  | 0.1
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 11.81 |  |  | -0.01646 |  |  |  | 0 |  | 1 | CAPACITY | AA1-139 |  |  | 0.1
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | -0.01646 |  |  |  | 0 |  | 1 | NEW | AA1-139 |  |  | 0.1
932596 | AC2-079 E | 0.64 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | -0.01649 |  |  |  | 0 |  | 1 | NEW | AC2-079 |  |  | 0.1
316311 | AC2-079 C | 0.64 | 345 | 75 | 0 | 32.3 | 4.84 |  |  | -0.01649 |  |  |  | 0 |  | 1 | CAPACITY | AC2-079 |  |  | 0.1
270173 | AC1-122_C | 0.6 | 205 | 75 | 0 | 54.4 | 3.97 |  |  | -0.01652 |  |  |  | 0 |  | 1 | CAPACITY | AC1-122 |  |  | 0.1
926516 | AC1-122_E | 0.6 | 205 | 75 | 0 | 21.5 | 1.57 |  |  | -0.01652 |  |  |  | 0 |  | 1 | NEW | AC1-122 |  |  | 0.1
316150 | AD2-215 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | -0.01653 |  |  |  | 0 |  | 1 | CAPACITY | AD2-215 |  |  | 0.1
316072 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 1.46 |  |  | -0.01653 |  |  |  | 0 |  | 1 | CAPACITY | AD1-144 |  |  | 0.1
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | -0.01653 |  |  |  | 0 |  | 1 | NEW | AD1-144 |  |  | 0.1
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | -0.01653 |  |  |  | 0 |  | 1 | NEW | AD2-215 |  |  | 0.1
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 27.95 |  |  | -0.01653 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316185 | AD1-033 C | 0.6 | 345 | 75 | 0 | 42 | 6.3 |  |  | -0.01654 |  |  |  | 0 |  | 1 | CAPACITY | AD1-033 |  |  | 0.1
934065 | AD1-033 E | 0.6 | 345 | 75 | 0 | 28 | 4.2 |  |  | -0.01654 |  |  |  | 0 |  | 1 | NEW | AD1-033 |  |  | 0.1
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.01653 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.01653 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316057 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | -0.01653 |  |  |  | 0 |  | 1 | CAPACITY | AC2-196 |  |  | 0.1
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 1 |  |  | -0.01653 |  |  |  | 0 |  | 1 | NEW | AC2-196 |  |  | 0.1
316316 | AC1-027 C | 115 | 345 | 75 | 0 | 11.2 | 1.68 |  |  | -0.01655 |  |  |  | 0 |  | 1 | CAPACITY | AC1-027 |  |  | 0.1
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | -0.01655 |  |  |  | 0 |  | 1 | NEW | AC1-027 |  |  | 0.1
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 10.4 |  |  | -0.01655 |  |  |  | 0 |  | 1 | NEW | Z1-068 |  |  | 0.8
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.49 |  |  | -0.01655 |  |  |  | 0 |  | 1 | CAPACITY | Z1-068 |  |  | 0.8
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 83.11 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 82.06 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 80.64 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315099 | 1CHESPKB | 13.8 | 345 | 20 | 0 | 24.7 | 0 |  |  | -0.01658 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 0.45 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316036 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | -0.01658 |  |  |  | 0 |  | 1 | CAPACITY | AC1-147 |  |  | 0.1
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | -0.01658 |  |  |  | 0 |  | 1 | NEW | AC1-147 |  |  | 0.1
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 7.56 |  |  | -0.01657 |  |  |  | 0.1097 |  | 1 | CAPACITY | VIRGINIA BEACH LF_A |  |  | 1
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 11.9 |  |  | -0.01657 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 12.9 |  |  | -0.01657 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 15.2 |  |  | -0.01657 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251542 | 08VERONA | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.0166 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 2.22 |  |  | -0.01661 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.01664 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 0.1
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 2.85 |  |  | -0.01664 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 0.1
316294 | AC1-161 C | 0.44 | 345 | 75 | 0 | 168.2 | 25.23 |  |  | -0.01667 |  |  |  | 0 |  | 1 | CAPACITY | AC1-161 |  |  | 0.1
926755 | AC1-161 E | 0.44 | 345 | 75 | 0 | 71.8 | 0 |  |  | -0.01667 |  |  |  | 0 |  | 1 | NEW | AC1-161 |  |  | 0.1
316236 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.0167 |  |  |  | 0 |  | 1 | CAPACITY | AE1-162 |  |  | 0.1
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.0167 |  |  |  | 0 |  | 1 | NEW | AE1-162 |  |  | 0.1
932586 | AC2-078 E | 0.64 | 345 | 75 | 0 | 37.2 | 5.58 |  |  | -0.0167 |  |  |  | 0 |  | 1 | NEW | AC2-078 |  |  | 0.1
316289 | AC2-078 C | 0.64 | 345 | 75 | 0 | 22.8 | 3.42 |  |  | -0.0167 |  |  |  | 0 |  | 1 | CAPACITY | AC2-078 |  |  | 0.1
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 2.75 |  |  | -0.01671 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 0.89 |  |  | -0.01677 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 65.18 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 65.11 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 844.6 |  |  | -0.01677 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316242 | AE2-079 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY | AE2-079 |  |  | 0.1
316241 | AE2-078 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY | AE2-078 |  |  | 0.1
316247 | AF1-033 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY | AF1-033 |  |  | 0.1
943622 | AF1-033 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01679 |  |  |  | 0 |  | 1 | NEW | AF1-033 |  |  | 0.1
940902 | AE2-079 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01679 |  |  |  | 0 |  | 1 | NEW | AE2-079 |  |  | 0.1
940892 | AE2-078 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01679 |  |  |  | 0 |  | 1 | NEW | AE2-078 |  |  | 0.1
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 843.5 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
341584 | 2GRIFFIN | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | -0.01684 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
270205 | AE1-176 | 138 | 205 | 60 | 0 | 2.4 | 1.33 |  |  | -0.01685 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 4.5 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 10.77 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY | AB2-134 |  |  | 0.1
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 10.59 |  |  | -0.01688 |  |  |  | 0 |  | 1 | NEW | AB2-134 |  |  | 0.1
316051 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY | AC2-071 |  |  | 0.1
316322 | AB2-045 C | 230 | 345 | 75 | 0 | 11.43 | 1.72 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY | AB2-045 |  |  | 0.1
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01688 |  |  |  | 0 |  | 1 | NEW | AC2-071 |  |  | 0.1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | -0.01688 |  |  |  | 0 |  | 1 | NEW | AB2-045 |  |  | 0.1
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 787.1 | 23.61 |  |  | -0.01689 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | -0.01691 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 0.1
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 4.56 |  |  | -0.01691 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 0.1
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 6.71 |  |  | -0.01691 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 16.8 |  |  | -0.01691 |  |  |  | 0 |  | 1 | CAPACITY | AB2-190 |  |  | 0.1
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 7.2 |  |  | -0.01691 |  |  |  | 0 |  | 1 | NEW | AB2-190 |  |  | 0.1
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | -0.01693 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | -0.01693 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
316301 | AE2-228 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | -0.01699 |  |  |  | 0 |  | 1 | CAPACITY | AE2-228 |  |  | 0.1
942162 | AE2-228 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | -0.01699 |  |  |  | 0 |  | 1 | NEW | AE2-228 |  |  | 0.1
316240 | AF1-291 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.017 |  |  |  | 0 |  | 1 | CAPACITY | AF1-291 |  |  | 0.1
946262 | AF1-291 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.017 |  |  |  | 0 |  | 1 | NEW | AF1-291 |  |  | 0.1
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.01703 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 94.51 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | -0.01703 |  |  |  | 0.036 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
342550 | 4BAVARIAN LF | 138 | 320 | 77 | 0 | 4.8 | 3.24 |  |  | -0.01703 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 52.8 | 52.8 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316159 | AE1-175 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01704 |  |  |  | 0 |  | 1 | CAPACITY | AE1-175 |  |  | 0.1
316160 | AE1-175 E | 230 | 345 | 75 | 0 | 6.6 | 0.99 |  |  | -0.01704 |  |  |  | 0 |  | 1 | NEW | AE1-175 |  |  | 0.1
242587 | 05CELAN | 138 | 205 | 77 | 0 | 81.6 | 58.39 |  |  | -0.01711 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 98.04 |  |  | -0.01721 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 96.46 |  |  | -0.01721 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 49.66 |  |  | -0.01721 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 45.01 |  |  | -0.01721 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316280 | AD1-041 C | 0.55 | 345 | 75 | 0 | 30 | 4.5 |  |  | -0.01722 |  |  |  | 0 |  | 1 | CAPACITY | AD1-041 |  |  | 0.1
934146 | AD1-041 E | 0.55 | 345 | 75 | 0 | 20 | 3 |  |  | -0.01722 |  |  |  | 0 |  | 1 | NEW | AD1-041 |  |  | 0.1
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 1.97 |  |  | -0.01721 |  |  |  | 0 |  | 1 | CAPACITY | AD2-030 |  |  | 0.1
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01721 |  |  |  | 0 |  | 1 | NEW | AD2-030 |  |  | 0.1
316201 | AC1-065 C | 0.39 | 345 | 75 | 0 | 49.4 | 7.41 |  |  | -0.01723 |  |  |  | 0 |  | 1 | CAPACITY | AC1-065 |  |  | 0.1
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.01723 |  |  |  | 0 |  | 1 | NEW | AC1-065 |  |  | 0.1
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 20 |  |  | -0.01723 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316059 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | -0.01724 |  |  |  | 0 |  | 1 | CAPACITY | AD1-063 |  |  | 0.1
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.1 | 10.8 |  |  | -0.01724 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHARLES CITY_LF |  |  | 1
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01724 |  |  |  | 0 |  | 1 | NEW | AD1-063 |  |  | 0.1
313053 | 6PAPERMILL | 230 | 345 | 77 | 12 | 37 | 0 |  |  | -0.01725 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
316314 | AB2-024 C | 230 | 345 | 75 | 0 | 11.13 | 1.67 |  |  | -0.01725 |  |  |  | 0 |  | 1 | CAPACITY | AB2-024 |  |  | 0.1
315086 | 1SPRUNCD | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | -0.01726 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315085 | 1SPRUNCC | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | -0.01726 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | -0.01725 |  |  |  | 0 |  | 1 | NEW | AB2-024 |  |  | 0.1
316304 | AE2-227 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | -0.01727 |  |  |  | 0 |  | 1 | CAPACITY | AE2-227 |  |  | 0.1
942152 | AE2-227 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | -0.01727 |  |  |  | 0 |  | 1 | NEW | AE2-227 |  |  | 0.1
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 9.99 |  |  | -0.01727 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHESTERFIELD LF_A |  |  | 1
316169 | AC1-164 GEN | 0.44 | 345 | 75 | 192.1 | 220.8 | 33.12 |  |  | -0.01729 |  |  |  | 0 |  | 1 | CAPACITY | AC1-164 |  |  | 0.1
926785 | AC1-164_E | 0.44 | 345 | 75 | 91 | 104.6 | 15.69 |  |  | -0.01729 |  |  |  | 0 |  | 1 | NEW | AC1-164 |  |  | 0.1
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 185.28 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | -0.01731 |  |  |  | 0.036 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
AF2-085 | BATEXP_AF2-085->PJM |  |  | LTF |  | 20 |  |  |  | -0.0173
316313 | AB2-026 C | 230 | 345 | 75 | 0 | 13.07 | 1.96 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | AB2-026 |  |  | 0.1
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 12.7 | 1.9 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | AC2-137 |  |  | 0.1
316258 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | AE1-075 |  |  | 0.1
316303 | AF2-085 | 230 | 345 | 76 | 0 | 20 | 13.41 |  |  | -0.01732 |  |  |  | 0.05 |  | 1 | CAPACITY |  |  |  | 1
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | -0.01731 |  |  |  | 0 |  | 1 | NEW | AC2-137 |  |  | 0.1
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | -0.01731 |  |  |  | 0 |  | 1 | NEW | AB2-026 |  |  | 0.1
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0.88 |  |  | -0.01731 |  |  |  | 0 |  | 1 | NEW | AE1-075 |  |  | 0.1
316233 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01732 |  |  |  | 0 |  | 1 | CAPACITY | AE1-074 |  |  | 0.1
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01732 |  |  |  | 0 |  | 1 | NEW | AE1-074 |  |  | 0.1
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 64.51 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 64.43 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 64.21 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 64.14 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 6.2 |  |  | -0.01736 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.01737 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.01737 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.01737 |  |  |  | 0.036 |  | 1 | NEW | AC1-107 |  |  | 1
316312 | AB1-027 C | 230 | 345 | 75 | 0 | 17.5 | 2.63 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AB1-027 |  |  | 0.1
316004 | AC1-112 C | 230 | 345 | 75 | 0 | 10.9 | 1.63 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AC1-112 |  |  | 0.1
316050 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 1.38 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AC2-070 |  |  | 0.1
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 7.5 | 1.13 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AB1-027 |  |  | 0.1
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0.92 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AC1-112 |  |  | 0.1
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0.57 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AC2-070 |  |  | 0.1
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 0.75 |  |  | -0.01742 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 0.72 |  |  | -0.01742 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AC2-138 |  |  | 0.1
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AC2-138 |  |  | 0.1
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 7.38 |  |  | -0.01744 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 4 |  |  | -0.0175 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316223 | AC1-118 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01759 |  |  |  | 0 |  | 1 | CAPACITY | AC1-118 |  |  | 0.1
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01759 |  |  |  | 0 |  | 1 | NEW | AC1-118 |  |  | 0.1
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 165.2 | 123.92 |  |  | -0.01771 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 165.1 | 123.84 |  |  | -0.01771 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 126.7 | 95.04 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 124.8 | 93.61 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | -0.01771 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | -0.01771 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 127.52 |  |  | -0.01771 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316234 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01772 |  |  |  | 0 |  | 1 | CAPACITY | AE1-124 |  |  | 0.1
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01772 |  |  |  | 0 |  | 1 | NEW | AE1-124 |  |  | 0.1
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 1.17 |  |  | -0.0178 |  |  |  | 0 |  | 1 | NEW | AC1-116 |  |  | 0.1
316035 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 0.7 |  |  | -0.0178 |  |  |  | 0 |  | 1 | CAPACITY | AC1-116 |  |  | 0.1
314860 | 4E MILL | 138 | 345 | 77 | 0 | 50 | 0 |  |  | -0.01798 |  |  |  | 0 |  | 1 | NEWENERGY | Covington |  |  | 1
314859 | 4WSTVACO | 138 | 345 | 2 | 0 | 40.5 | 0 |  |  | -0.01798 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
909222 | X2-060 E | 138 | 345 | 64 | 0 | 30 | 0 |  |  | -0.01798 |  |  |  | 0 |  | 1 | ENERGY | Covington |  |  | 1
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 0.76 |  |  | -0.01798 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 0.75 |  |  | -0.01798 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
918234 | AA1-038_E | 0.69 | 345 | 74 | 0 | 66.7 | 66.03 |  |  | -0.01798 |  |  |  | 0 |  | 1 | NEW | AA1-038 |  |  | 0.8
315616 | AA1-038_C | 0.69 | 345 | 74 | 0 | 9.9 | 9.8 |  |  | -0.01798 |  |  |  | 0 |  | 1 | CAPACITY | AA1-038 |  |  | 0.8
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 5.5 |  |  | -0.01798 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 301.17 |  |  | -0.01801 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | -0.01801 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | -0.01801 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | -0.01801 |  |  |  | 0.036 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
316299 | AC2-112 C | 0.6 | 345 | 75 | 0 | 103.1 | 15.47 |  |  | -0.01806 |  |  |  | 0 |  | 1 | CAPACITY | AC2-112 |  |  | 0.1
932855 | AC2-112 E | 0.6 | 345 | 75 | 0 | 46.9 | 0 |  |  | -0.01806 |  |  |  | 0 |  | 1 | NEW | AC2-112 |  |  | 0.1
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 8.7 |  |  | -0.01807 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 223.38 |  |  | -0.01808 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 502.3 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 503.8 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 502.2 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 502.8 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 120.47 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 120.09 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 119.87 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 0.39 |  |  | -0.01821 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 0.37 |  |  | -0.01821 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 948.5 |  |  | -0.01823 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 948.9 |  |  | -0.01823 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316192 | AB2-158 C | 230 | 345 | 75 | 0 | 71 | 10.65 |  |  | -0.01828 |  |  |  | 0 |  | 1 | CAPACITY | AB2-158 |  |  | 0.1
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 4.08 |  |  | -0.01828 |  |  |  | 0 |  | 1 | NEW | AB2-158 |  |  | 0.1
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 118.52 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 57.83 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | -0.01831 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | -0.01831 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | -0.01831 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | -0.01831 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
249991 | 08BUFTN1 | 138 | 212 | 77 | 0 | 2.2 | 0 |  |  | -0.01833 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
342031 | 2PACTOLUS | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | -0.01836 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 194.77 |  |  | -0.01841 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | -0.01841 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | -0.01841 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 2 |  |  | -0.01843 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316044 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | -0.01848 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 1 |  |  | 0.1
316045 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | -0.01848 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 2 |  |  | 0.1
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | -0.01848 |  |  |  | 0 |  | 1 | NEW | AC1-158 1 |  |  | 0.1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | -0.01848 |  |  |  | 0 |  | 1 | NEW | AC1-158 2 |  |  | 0.1
926004 | AC1-076_E | 0.6 | 345 | 75 | 0 | 39.42 | 5.91 |  |  | -0.0185 |  |  |  | 0 |  | 1 | NEW | AC1-076 |  |  | 0.1
316164 | AC1-076_C | 0.6 | 345 | 75 | 0 | 23.8 | 3.57 |  |  | -0.0185 |  |  |  | 0 |  | 1 | CAPACITY | AC1-076 |  |  | 0.1
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | -0.01849 |  |  |  | 0 |  | 1 | CAPACITY | AE1-099 |  |  | 0.1
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | -0.01849 |  |  |  | 0 |  | 1 | CAPACITY | AE1-098 |  |  | 0.1
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | -0.01849 |  |  |  | 0 |  | 1 | NEW | AE1-099 |  |  | 0.1
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | -0.01849 |  |  |  | 0 |  | 1 | NEW | AE1-098 |  |  | 0.1
316254 | AC1-120 C | 0.6 | 345 | 75 | 0 | 39.6 | 5.94 |  |  | -0.01854 |  |  |  | 0 |  | 1 | CAPACITY | AC1-120 |  |  | 0.1
926486 | AC1-120 E | 0.6 | 345 | 75 | 0 | 20.4 | 3.06 |  |  | -0.01854 |  |  |  | 0 |  | 1 | NEW | AC1-120 |  |  | 0.1
316170 | AC1-121 C | 0.6 | 345 | 75 | 0 | 13.6 | 2.04 |  |  | -0.01854 |  |  |  | 0 |  | 1 | CAPACITY | AC1-121 |  |  | 0.1
926502 | AC1-121 E | 0.6 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | -0.01854 |  |  |  | 0 |  | 1 | NEW | AC1-121 |  |  | 0.1
925672 | AC1-043 E | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | -0.01857 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 0.1
316257 | AC1-043 C | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | -0.01857 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 0.1
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 1.07 | 0.16 |  |  | -0.01858 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
961102 | AF2-401 E | 115 | 345 | 75 | 0 | 5.8 | 0.87 |  |  | -0.01861 |  |  |  | 0 |  | 1 | NEW | AF2-401 |  |  | 0.1
316302 | AF2-401 C | 115 | 345 | 75 | 0 | 3.52 | 0.53 |  |  | -0.01861 |  |  |  | 0 |  | 1 | CAPACITY | AF2-401 |  |  | 0.1
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 1.46 |  |  | -0.01863 |  |  |  | 0 |  | 1 | NEW | AD1-085 |  |  | 0.1
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 0.9 |  |  | -0.01863 |  |  |  | 0 |  | 1 | CAPACITY | AD1-085 |  |  | 0.1
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 0.72 |  |  | -0.01863 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.44 |  |  | -0.01863 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 2.4 | 1.61 |  |  | -0.01865 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316267 | AC1-143 C | 0.38 | 345 | 75 | 0 | 41.2 | 6.18 |  |  | -0.01869 |  |  |  | 0 |  | 1 | CAPACITY | AC1-143 |  |  | 0.1
926615 | AC1-143 E | 0.38 | 345 | 75 | 0 | 18.8 | 2.82 |  |  | -0.01869 |  |  |  | 0 |  | 1 | NEW | AC1-143 |  |  | 0.1
316054 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | -0.01869 |  |  |  | 0 |  | 1 | CAPACITY | AC2-074 |  |  | 0.1
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0.79 |  |  | -0.01869 |  |  |  | 0 |  | 1 | NEW | AC2-074 |  |  | 0.1
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 1.83 |  |  | -0.01873 |  |  |  | 0 |  | 1 | NEW | AB2-029 |  |  | 0.1
316006 | AB2-029 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | -0.01873 |  |  |  | 0 |  | 1 | CAPACITY | AB2-029 |  |  | 0.1
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 170 | 127.52 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | -0.01877 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | -0.01877 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 120.39 |  |  | -0.01877 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 113.79 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.1 | 113.34 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 112.29 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.01884 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.01884 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.01884 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251269 | 08BEAVR2 | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.01886 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 188.28 |  |  | -0.01887 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | -0.01887 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | -0.01887 |  |  |  | 0.036 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 1.07 |  |  | -0.01887 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 1.07 |  |  | -0.01887 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.01891 |  |  |  | 0.0975 |  | 1 | MTX | Z1-065 |  |  | 1
316052 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01895 |  |  |  | 0 |  | 1 | CAPACITY | AC2-072 |  |  | 0.1
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01895 |  |  |  | 0 |  | 1 | NEW | AC2-072 |  |  | 0.1
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
913222 | Y1-054 E | 138 | 212 | 58 | 0 | 20 | 0 |  |  | -0.01896 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
314088 | 6VANDORN | 230 | 345 | 1 | 7 | 21 | 14.08 |  |  | -0.01896 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
250091 | 08RCHLE3 | 138 | 212 | 77 | 0 | 6.7 | 4.72 |  |  | -0.01896 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 734 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 586 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | -0.01897 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251346 | 08IVYDL1 | 69 | 212 | 77 | 0 | 12.5 | 8.81 |  |  | -0.01903 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.01915 |  |  |  | 0 |  | 1 | MTX | Y3-100 |  |  | 1
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.01915 |  |  |  | 0 |  | 1 | MTX | Y3-099 |  |  | 1
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 227.1 |  |  | -0.01918 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  |  |  | -0.0192
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 229.53 |  |  | -0.0192 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | -0.0192 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-039 |  |  | 1
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | -0.0192 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 44.38 |  |  | -0.01924 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
250041 | 08HAMLTN | 138 | 212 | 77 | 0 | 2.2 | 1.55 |  |  | -0.01925 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 600 |  |  | -0.01927 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 6.79 |  |  | -0.01928 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 0.1
270186 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.01928 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 0.1
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 327.3 | 176.05 |  |  | -0.01929 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | -0.01929 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | -0.01929 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-035 |  |  | 1
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 43.03 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | -0.01931 |  |  |  | 0.036 |  | 1 | CAPACITY | PANDA |  |  | 1
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
226704 | AOCX4-046 E | 13.8 | 233 | 58 | 0 | 19.5 | 0 |  |  | -0.01931 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | -0.01931 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226924 | AE1-015 E | 69 | 233 | 75 | 0 | 0.75 | 0.07 |  |  | -0.01931 |  |  |  | 0 |  | 1 | NEW | AE1-015 |  |  | 0.1
226923 | AE1-015 C | 69 | 233 | 75 | 0 | 0.57 | 0.05 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | AE1-015 |  |  | 0.1
226922 | AE1-013 E | 69 | 233 | 75 | 0 | 0.5 | 0.05 |  |  | -0.01931 |  |  |  | 0 |  | 1 | NEW | AE1-013 |  |  | 0.1
226921 | AE1-013 C | 69 | 233 | 75 | 0 | 0.38 | 0.04 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | AE1-013 |  |  | 0.1
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.01933 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.01933 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 395.08 |  |  | -0.01936 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | -0.01936 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | -0.01936 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | -0.01936 |  |  |  | 0.036 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -0.01938 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 182.23 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | -0.01938 |  |  |  | 0.036 |  | 1 | CAPACITY | WALDORF |  |  | 1
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 1.86 |  |  | -0.01939 |  |  |  | 0 |  | 1 | NEW | AC2-101 |  |  | 0.1
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 1.58 |  |  | -0.01939 |  |  |  | 0 |  | 1 | NEW | AC2-120 |  |  | 0.1
227282 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 1.14 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY | AC2-101 |  |  | 0.1
227280 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 0.97 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY | AC2-120 |  |  | 0.1
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 613.3 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 619.4 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 11.01 |  |  | -0.0194 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 10.83 |  |  | -0.0194 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227024 | SMECOCT | 13.8 | 238 | 57 | 0 | 80.2 | 43.14 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 13.12 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 9.68 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | -0.01941 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.39 |  |  | -0.01941 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 3.05 |  |  | -0.01943 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0.16 |  |  | -0.01943 |  |  |  | 0 |  | 1 | NEW | AB2-157 |  |  | 0.1
226910 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.07 |  |  | -0.01943 |  |  |  | 0 |  | 1 | CAPACITY | AB2-157 |  |  | 0.1
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.91 |  |  | -0.01942 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247225 | 05FTHLG2 | 18 | 205 | 57 | 151.2 | 173.8 | 66.38 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247224 | 05FTHLG1 | 18 | 205 | 57 | 151.1 | 173.7 | 66.34 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247231 | 05RIVRG2 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247232 | 05RIVRG3 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 866 |  |  | -0.01945 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 841.8 |  |  | -0.01945 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | -0.01947 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 0.1
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | -0.01947 |  |  |  | 0 |  | 1 | NEW | Z2-030 |  |  | 0.1
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | -0.01947 |  |  |  | 0 |  | 1 | CAPACITY | Z2-030 |  |  | 0.1
237077 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | -0.01947 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 0.1
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 0.76 |  |  | -0.01947 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | -0.01949 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | -0.01949 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 0.33 |  |  | -0.01948 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 52 |  |  | -0.01949 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226920 | AE1-012 E | 115 | 233 | 75 | 0 | 0.34 | 0.03 |  |  | -0.01949 |  |  |  | 0 |  | 1 | NEW | AE1-012 |  |  | 0.1
226919 | AE1-012 C | 115 | 233 | 75 | 0 | 0.22 | 0.02 |  |  | -0.01949 |  |  |  | 0 |  | 1 | CAPACITY | AE1-012 |  |  | 0.1
252507 | AC2-088 C | 0.57 | 212 | 75 | 0 | 38.4 | 2.8 |  |  | -0.01952 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 0.1
932665 | AC2-088 E | 0.57 | 212 | 75 | 0 | 31.6 | 2.31 |  |  | -0.01952 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 0.1
252509 | AD1-136 C | 0.57 | 212 | 75 | 0 | 5.4 | 0.39 |  |  | -0.01952 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 0.1
935033 | AD1-136 E | 0.57 | 212 | 75 | 0 | 4.6 | 0.34 |  |  | -0.01952 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 0.1
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.5 | 3.02 |  |  | -0.01952 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | -0.01953 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 29.06 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76 | 29.02 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 28.99 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 28.91 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 28.87 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 28.8 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251364 | 08LEBANO | 69 | 212 | 77 | 0 | 30.6 | 21.57 |  |  | -0.01955 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 1.87 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251832 | 08HLCRTG | 0.38 | 212 | 75 | 0 | 120 | 8.76 |  |  | -0.01958 |  |  |  | 0 |  | 1 | CAPACITY | AB1-014 |  |  | 0.1
930062 | AB1-014 E | 0.38 | 212 | 75 | 0 | 77.5 | 5.66 |  |  | -0.01958 |  |  |  | 0 |  | 1 | NEW | AB1-014 |  |  | 0.1
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.87 |  |  | -0.01958 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 19.29 |  |  | -0.01959 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251387 | 08MDDLTW | 69 | 212 | 77 | 0 | 22.5 | 16.62 |  |  | -0.01959 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 26.35 |  |  | -0.0196 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 11.46 |  |  | -0.0196 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 4.93 |  |  | -0.0196 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223967 | METZ E69 | 69 | 233 | 56 | 0 | 20 | 0 |  |  | -0.01961 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226895 | WOAKV2-037 E | 69 | 233 | 29 | 0 | 4.5 | 0 |  |  | -0.01961 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 31.16 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.5 | 30.74 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 30.59 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 29.56 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251952 | 08MADSN1 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251953 | 08MADSN2 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251954 | 08MADSN3 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251955 | 08MADSN4 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251959 | 08MADSN8 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251957 | 08MADSN6 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251958 | 08MADSN7 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251956 | 08MADSN5 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 3.62 |  |  | -0.01964 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 0.1
237026 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 2.22 |  |  | -0.01964 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 0.1
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.64 |  |  | -0.01964 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 272.1 | 103.92 |  |  | -0.01965 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-079 |  |  | 1
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 202.7 | 77.41 |  |  | -0.01965 |  |  |  | 0 |  | 1 | CAPACITY | Z1-079 |  |  | 1
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 54.8 | 40.8 |  |  | -0.01966 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251828 | CLNTESP1 | 0 | 212 | 76 | 0 | 10 | 0 |  |  | -0.01971 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 113.58 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.1 | 113.46 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | -0.01974 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | -0.01974 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | -0.01976 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 1.44 |  |  | -0.01976 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
923213 | AB1-125_E | 0.6 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | -0.01977 |  |  |  | 0 |  | 1 | NEW | AB1-125 |  |  | 0.1
237006 | AB1-125_C | 0.6 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | -0.01977 |  |  |  | 0 |  | 1 | CAPACITY | AB1-125 |  |  | 0.1
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 41.19 |  |  | -0.0198 |  |  |  | 0 |  | 1 | NEW | M24 |  |  | 0.8
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.0198 |  |  |  | 0.0975 |  | 1 | MTX | M24 BAT |  |  | 1
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 21.15 |  |  | -0.0198 |  |  |  | 0 |  | 1 | NEW | AB1-150 |  |  | 0.8
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 7.23 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY | M24 |  |  | 0.8
237033 | AB1-150 C | 138 | 201 | 74 | 0 | 7.3 | 3.52 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY | AB1-150 |  |  | 0.8
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 7.34 |  |  | -0.0198 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 638.9 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 642.7 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247622 | Y3-025 | 69 | 205 | 64 | 0 | 3.18 | 0 |  |  | -0.01982 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.14 |  |  | -0.01982 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 68.9 |  |  | -0.01982 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 289.09 |  |  | -0.01982 |  |  |  | 0.1042 |  | 1 | CAPACITY | Wagner3 |  |  | 1
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | -0.01982 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 7.15 |  |  | -0.01982 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | -0.01985 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | -0.01986 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 57 |  |  | -0.01986 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.2 | 16.24 |  |  | -0.01986 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 29.8 | 16.03 |  |  | -0.01986 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 108.79 |  |  | -0.01987 |  |  |  | 0 |  | 1 | NEW | K11 |  |  | 0.8
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 18.41 |  |  | -0.01987 |  |  |  | 0 |  | 1 | CAPACITY | K11 |  |  | 0.8
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.01988 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 0.1
237025 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.01988 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 0.1
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0.44 |  |  | -0.01987 |  |  |  | 0 |  | 1 | NEW | AB1-096 |  |  | 0.1
237030 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 0.23 |  |  | -0.01987 |  |  |  | 0 |  | 1 | CAPACITY | AB1-096 |  |  | 0.1
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 81.18 |  |  | -0.01987 |  |  |  | 0 |  | 1 | NEW | T157 |  |  | 0.8
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 20.3 |  |  | -0.01987 |  |  |  | 0 |  | 1 | CAPACITY | T157 |  |  | 0.8
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 0.36 |  |  | -0.01989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0.63 |  |  | -0.0199 |  |  |  | 0 |  | 1 | NEW | W1-116 |  |  | 0.1
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 0.39 |  |  | -0.0199 |  |  |  | 0 |  | 1 | CAPACITY | W1-116 |  |  | 0.1
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.0199 |  |  |  | 0 |  | 1 | MTX | AB1-055 |  |  | 1
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 553 |  |  | -0.01989 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM2 |  |  | 1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 522.9 |  |  | -0.01989 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 548.2 |  |  | -0.0199 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM1 |  |  | 1
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 36.56 |  |  | -0.0199 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
237003 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0.76 |  |  | -0.01991 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 0.1
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | -0.01991 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 0.1
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | -0.01991 |  |  |  | 0 |  | 1 | CAPACITY | AA1-109 |  |  | 0.1
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | -0.01991 |  |  |  | 0 |  | 1 | NEW | AA1-109 |  |  | 0.1
220904 | CRANE G2 | 20 | 232 | 12 | 0 | 14 | 0 |  |  | -0.01991 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 0.1
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 0.1
253314 | AC1-085 A_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 0.8
253317 | AC1-085 B_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 0.8
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.61 |  |  | -0.01996 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 139.8 | 75.19 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 61.1 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 55.94 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 27.97 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | W4-102 |  |  | 0.1
223402 | AF1-300 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | AF1-300 |  |  | 0.1
223401 | AF1-299 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | AF1-299 |  |  | 0.1
946352 | AF1-299 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AF1-299 |  |  | 0.1
946362 | AF1-300 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AF1-300 |  |  | 0.1
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | W4-102 |  |  | 0.1
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.4 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 0.1
237024 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0.51 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 0.1
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0.24 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AA1-095 |  |  | 0.1
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 0.21 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | AA1-095 |  |  | 0.1
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 8.21 |  |  | -0.01999 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0.73 |  |  | -0.02001 |  |  |  | 0 |  | 1 | NEW | AB2-097 |  |  | 0.1
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02 |  |  |  | 0 |  | 1 | CAPACITY | AA1-092 |  |  | 0.1
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0.29 |  |  | -0.02 |  |  |  | 0 |  | 1 | NEW | AA1-092 |  |  | 0.1
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02003 |  |  |  | 0 |  | 1 | NEW | AA2-072 |  |  | 0.1
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0.46 |  |  | -0.02003 |  |  |  | 0 |  | 1 | NEW | AC2-136 |  |  | 0.1
237034 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 0.4 |  |  | -0.02003 |  |  |  | 0 |  | 1 | CAPACITY | AC2-136 |  |  | 0.1
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 10.07 |  |  | -0.02005 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | -0.02005 |  |  |  | 0 |  | 1 | NEW | AD1-060 |  |  | 0.1
237080 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | -0.02005 |  |  |  | 0 |  | 1 | CAPACITY | AD1-060 |  |  | 0.1
237037 | AE1-188 C | 34.5 | 201 | 75 | 0 | 20.5 | 1.5 |  |  | -0.02008 |  |  |  | 0 |  | 1 | CAPACITY | AE1-188 |  |  | 0.1
237038 | AE2-054 C | 34.5 | 201 | 75 | 0 | 12 | 0.88 |  |  | -0.02007 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 0.1
939592 | AE1-188 E | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | -0.02008 |  |  |  | 0 |  | 1 | NEW | AE1-188 |  |  | 0.1
940672 | AE2-054 E | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02007 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 0.1
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 800 |  |  | -0.02008 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02009 |  |  |  | 0 |  | 1 | NEW | AB1-128 |  |  | 0.1
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02009 |  |  |  | 0 |  | 1 | NEW | AB1-127 |  |  | 0.1
235043 | AF1-166 C | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | -0.02009 |  |  |  | 0 |  | 1 | CAPACITY | AF1-166 |  |  | 0.1
237001 | AB1-127 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.02009 |  |  |  | 0 |  | 1 | CAPACITY | AB1-127 |  |  | 0.1
237002 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.02009 |  |  |  | 0 |  | 1 | CAPACITY | AB1-128 |  |  | 0.1
945012 | AF1-166 E | 34.5 | 201 | 75 | 0 | 6.4 | 0.47 |  |  | -0.02009 |  |  |  | 0 |  | 1 | NEW | AF1-166 |  |  | 0.1
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | -0.02011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | -0.02011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1330 |  |  | -0.02011 |  |  |  | 0 |  | 1 | CAPACITY | AMG3 |  |  | 1
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 800 |  |  | -0.02011 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 19.81 |  |  | -0.02016 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 2.01 |  |  | -0.02018 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 0.1
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 1.23 |  |  | -0.02018 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 0.1
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 93.64 |  |  | -0.02022 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208904 | HOLT 696 | 13.2 | 229 | 60 | 16 | 58.4 | 41.06 |  |  | -0.02022 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208903 | HOLT 695 | 13.2 | 229 | 60 | 19 | 53.2 | 37.4 |  |  | -0.02022 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 0.45 |  |  | -0.02022 |  |  |  | 0 |  | 1 | CAPACITY | V4-027 |  |  | 0.1
208254 | AF2-280 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02022 |  |  |  | 0 |  | 1 | NEW | AF2-280 |  |  | 0.1
208474 | KINZ 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02022 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208253 | AF2-280 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02022 |  |  |  | 0 |  | 1 | MTX | AF2-280 |  |  | 1
916007 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 0.1 | 0.06 |  |  | -0.02022 |  |  |  | 0 |  | 1 | NEW | V4-027 |  |  | 0.1
208769 | SISO | 12.5 | 229 | 2 | 2.5 | 1.6 | 0 |  |  | -0.02029 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
208876 | WLAN | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02029 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 80.49 |  |  | -0.0203 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 68.19 |  |  | -0.0203 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 53.78 |  |  | -0.0203 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 45.34 |  |  | -0.0203 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 44.99 |  |  | -0.0203 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
209030 | FRFA O01 | 12.5 | 229 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02031 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
208527 | AF2-279 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02031 |  |  |  | 0 |  | 1 | NEW | AF2-279 |  |  | 0.1
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 2 | 1.22 |  |  | -0.02031 |  |  |  | 0 |  | 1 | NEW | V3-051 |  |  | 0.8
208526 | AF2-279 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02031 |  |  |  | 0 |  | 1 | MTX | AF2-279 |  |  | 1
205916 | AD1-020_C | 0.6 | 227 | 75 | 0 | 54 | 4.99 |  |  | -0.02033 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 0.1
205917 | AD1-020 ES | 0.55 | 227 | 75 | 0 | 21.5 | 1.99 |  |  | -0.02033 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 0.1
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 20.5 | 11.03 |  |  | -0.02033 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205922 | AF2-268 E | 115 | 227 | 75 | 0 | 2 | 0.19 |  |  | -0.02033 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 205.47 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | -0.02033 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 103.81 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | -0.02033 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA |  |  | 1
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1288.2 |  |  | -0.02034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1307 |  |  | -0.02034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 247.42 |  |  | -0.02035 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | -0.02035 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | -0.02035 |  |  |  | 0.036 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200055 | ROCKSP 4 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200054 | ROCKSP 3 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200052 | ROCKSP 1 | 18 | 235 | 57 | 145.7 | 167.5 | 90.09 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200053 | ROCKSP 2 | 18 | 235 | 57 | 144.9 | 166.5 | 89.56 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 64 | 34.42 |  |  | -0.02034 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 67.49 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 33.74 |  |  | -0.02036 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 171.69 |  |  | -0.02037 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | -0.02037 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | -0.02037 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 89.82 |  |  | -0.02037 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 20.6 | 11.08 |  |  | -0.02037 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 40.5 | 21.78 |  |  | -0.02038 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.02038 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 33.02 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY | P.H. GLATFELTER_IPP |  |  | 1
205920 | AF2-101 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY | AF2-101 |  |  | 0.1
958072 | AF2-101 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02039 |  |  |  | 0 |  | 1 | NEW | AF2-101 |  |  | 0.1
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 41.2 | 22.16 |  |  | -0.02039 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0.77 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | W1-045 |  |  | 0.1
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.1 | 0.47 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | W1-045 |  |  | 0.1
204555 | 27QUEEN ST | 115 | 227 | 75 | 0 | 5 | 0.46 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
205921 | AF2-151 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY | AF2-151 |  |  | 0.1
958602 | AF2-151 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02039 |  |  |  | 0 |  | 1 | NEW | AF2-151 |  |  | 0.1
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.77 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | -0.02041 |  |  |  | 0.036 |  | 1 | NEW | Garrison |  |  | 1
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 2.83 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 103.81 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 102.2 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 8.6 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AA1-102 |  |  | 0.1
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 111.97 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AB1-056 |  |  | 0.8
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 1.28 |  |  | -0.0204 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.0204 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 62.5 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 5.27 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AA1-102 |  |  | 0.1
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232915 | OH NUG4 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 0.82 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233935 | AB2-179 C | 0.38 | 235 | 75 | 0 | 37.6 | 3.48 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-179 |  |  | 0.1
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 38.35 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
924802 | AB2-133 E | 69 | 235 | 75 | 0 | 31.2 | 2.89 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-133 |  |  | 0.1
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 30.66 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 29.58 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233906 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 39.32 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AB1-056 |  |  | 0.8
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 388.63 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 26.36 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233939 | AB2-133 C | 69 | 235 | 75 | 0 | 24.6 | 2.28 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-133 |  |  | 0.1
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 25.82 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232901 | NORTHST | 69 | 235 | 56 | 5 | 45 | 24.2 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 16.08 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233930 | AB2-032 GEN | 0.6 | 235 | 75 | 0 | 13.6 | 1.26 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-032 |  |  | 0.1
232905 | CHERITON_25 | 24.9 | 235 | 65 | 0 | 12.5 | 0.23 |  |  | -0.02041 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB1-142 |  |  | 0.1
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB1-141 |  |  | 0.1
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-003 |  |  | 0.1
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-004 |  |  | 0.1
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-005 |  |  | 0.1
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-006 |  |  | 0.1
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-179 |  |  | 0.1
923925 | AB2-153 E | 0.6 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-153 |  |  | 0.1
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | X3-008 |  |  | 0.1
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-004 |  |  | 0.1
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-005 |  |  | 0.1
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-006 |  |  | 0.1
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-003 |  |  | 0.1
917082 | Z2-012 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Z2-012 |  |  | 0.1
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0.86 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Y3-058 |  |  | 0.1
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 9.57 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 8.9 | 0.82 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Y3-058 |  |  | 0.1
232920 | IR10 | 13.2 | 235 | 55 | 14 | 16.1 | 8.66 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233933 | AB2-153 GEN | 0.6 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-153 |  |  | 0.1
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | X3-008 |  |  | 0.1
233901 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Z2-012 |  |  | 0.1
232919 | VN10 | 13.2 | 235 | 55 | 0 | 14.3 | 7.69 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923928 | AB2-032 E | 0.6 | 235 | 75 | 0 | 6.4 | 0.59 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-032 |  |  | 0.1
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB1-142 |  |  | 0.1
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB1-141 |  |  | 0.1
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0.57 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | Y1-079 |  |  | 0.1
925262 | AB2-180 E | 0.38 | 235 | 75 | 0 | 6 | 0.56 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AB2-180 |  |  | 0.1
233942 | AB2-180 C | 0.38 | 235 | 75 | 0 | 14 | 8.72 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AB2-180 |  |  | 0.1
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 0.39 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AB1-137 |  |  | 0.1
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 6.23 |  |  | -0.02041 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0.37 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | X1-032 |  |  | 0.1
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Z2-076 |  |  | 0.1
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Z2-077 |  |  | 0.1
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 20.25 |  |  | -0.0204 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 0.35 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Y1-079 |  |  | 0.1
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0.34 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | X3-066 |  |  | 0.1
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 3.08 | 0.28 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | X3-066 |  |  | 0.1
960882 | AF2-379 E | 69 | 235 | 75 | 0 | 2.26 | 0.21 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AF2-379 |  |  | 0.1
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0.19 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Y1-080 |  |  | 0.1
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Z2-077 |  |  | 0.1
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Z2-076 |  |  | 0.1
205930 | AF2-099 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AF2-099 |  |  | 0.1
205931 | AF2-100 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AF2-100 |  |  | 0.1
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AB1-137 |  |  | 0.1
233940 | AF2-379 C | 69 | 235 | 75 | 0 | 1.64 | 0.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AF2-379 |  |  | 0.1
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 0.12 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Y1-080 |  |  | 0.1
958052 | AF2-099 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AF2-099 |  |  | 0.1
958062 | AF2-100 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AF2-100 |  |  | 0.1
233900 | O-025 C | 25 | 235 | 64 | 0 | 6 | 5.11 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 14.34 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.23 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.55 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.21 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 30 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.02041 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 12.37 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 12.32 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 164.17 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 9.25 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 7.64 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 81.14 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 8.32 |  |  | -0.02042 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 99.67 |  |  | -0.02042 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 13.36 |  |  | -0.02043 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
213893 | PHLISST1 | 20 | 230 | 58 | 232.3 | 267 | 143.61 |  |  | -0.02043 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | -0.02043 |  |  |  | 0.036 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | -0.02043 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | -0.02043 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1178.3 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 1145.8 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 1138.9 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | -0.02044 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | -0.02044 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 222.4 | 119.62 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | -0.02044 |  |  |  | 0.036 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 20.98 |  |  | -0.02044 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 18.29 |  |  | -0.02044 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.02045 |  |  |  | 0.1097 |  | 1 | ENERGY |  |  |  | 1
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | -0.02045 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208885 | WNHO | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | -0.02045 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208697 | PRIN B34 | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | -0.02045 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 87.67 |  |  | -0.02045 |  |  |  | 0.036 |  | 1 | CAPACITY | GRAYS FERRY |  |  | 1
228203 | P06 | 13.8 | 234 | 57 | 78 | 89.7 | 48.25 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 45.99 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 45.13 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 34.26 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 57.7 | 31.03 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 57.6 | 30.98 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 30.66 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 29.85 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.1 | 39.2 | 21.08 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 20.22 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | -0.02045 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 226.44 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 206.63 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | -0.02045 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | -0.02045 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
228357 | V2-046E | 12.9 | 234 | 75 | 0 | 12.9 | 1.19 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V2-046 |  |  | 0.1
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.1 | 12.43 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228471 | VALERO1 | 13.8 | 234 | 58 | 19.1 | 22 | 11.83 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | Valero |  |  | 1
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 0.72 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V2-046 |  |  | 0.1
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V4-054 |  |  | 0.1
228473 | VALERO3 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228484 | VALERO4 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228472 | VALERO2 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V4-054 |  |  | 0.1
228712 | V2-041E | 13.2 | 234 | 75 | 0 | 2.48 | 0.23 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V2-041 |  |  | 0.1
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V2-041 |  |  | 0.1
228721 | V2-035E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V2-035 |  |  | 0.1
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.07 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V2-035 |  |  | 0.1
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 3 | 2.55 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 75 |  |  | -0.02045 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 181.64 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | Q90 |  |  | 1
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 43.08 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
227801 | ONTC&DCT | 13.8 | 234 | 75 | 33.6 | 38.6 | 3.57 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 35.07 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | -0.02047 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | -0.02047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | -0.02047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 22.59 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | -0.02046 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 16.14 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | -0.02046 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 16.18 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | -0.02046 |  |  |  | 0.30476 |  | 1 | ENERGY |  |  |  | 1
219913 | AD2-042 E | 26.4 | 231 | 75 | 0 | 8.2 | 0.76 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AD2-042 |  |  | 0.1
924052 | AB2-049 E | 69 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AB2-049 |  |  | 0.1
219915 | AD2-027 E | 26.4 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AD2-027 |  |  | 0.1
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0.56 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | W2-030 |  |  | 0.1
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0.53 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | W1-130 |  |  | 0.1
219912 | AD2-042 C | 26.4 | 231 | 75 | 0 | 5 | 0.46 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AD2-042 |  |  | 0.1
214030 | WAYNEJCT | 13.8 | 230 | 29 | 0 | 8.8 | 4.73 |  |  | -0.02046 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.2 | 7.55 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 0.1
219914 | AD2-027 C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AD2-027 |  |  | 0.1
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 0.34 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | W2-030 |  |  | 0.1
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | W1-130 |  |  | 0.1
219765 | PARADISE E | 13 | 231 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | U4-036 |  |  | 0.1
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | Y2-081 |  |  | 0.1
230408 | AD2-065 E | 12.9 | 234 | 75 | 0 | 3.03 | 0.28 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AD2-065 |  |  | 0.1
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0.28 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | X3-075 |  |  | 0.1
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Y2-081 |  |  | 0.1
230414 | AF1-041 E | 69 | 234 | 75 | 0 | 2.4 | 0.22 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AF1-041 |  |  | 0.1
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0.22 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | Y3-087 |  |  | 0.1
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 0.21 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Y3-087 |  |  | 0.1
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | MTX | X2-013 |  |  | 1
219904 | AC1-010 C | 26.4 | 231 | 75 | 0 | 2.2 | 0.2 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 0.1
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | U4-036 |  |  | 0.1
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0.16 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | W2-071 |  |  | 0.1
227928 | V4-067E | 12.9 | 234 | 75 | 0 | 1.6 | 0.15 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V4-067 |  |  | 0.1
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.55 | 0.14 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AC1-030 |  |  | 0.1
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0.13 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AB1-001 |  |  | 0.1
219921 | AF1-264 | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | X3-075 |  |  | 0.1
230410 | AE1-218 E O1 | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AE1-218 |  |  | 0.1
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AB2-122 |  |  | 0.1
230415 | AB2-049 C | 69 | 234 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AB2-049 |  |  | 0.1
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.02047 |  |  |  | 0 |  | 1 | MTX | Z1-082 |  |  | 1
230407 | AD2-065_C | 12.9 | 234 | 75 | 0 | 1.08 | 0.1 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AD2-065 |  |  | 0.1
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.1 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | W2-071 |  |  | 0.1
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.09 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V4-067 |  |  | 0.1
219907 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AC1-030 |  |  | 0.1
219138 | THOSOLAR E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.08 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AB1-001 |  |  | 0.1
230403 | AB1-116 E | 12.9 | 234 | 28 | 0 | 0.78 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228733 | AB1-119 E | 12.9 | 234 | 28 | 0 | 0.73 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
230409 | AE1-218 C O1 | 12.9 | 234 | 75 | 0 | 0.8 | 0.07 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AE1-218 |  |  | 0.1
930243 | AB1-063_E | 69 | 231 | 0 | 0 | 0 | -0.7 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.65 | 3.95 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
230413 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.06 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AB2-122 |  |  | 0.1
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | Y1-075 |  |  | 0.1
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0.05 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | X1-071 |  |  | 0.1
228014 | PVILLEG | 0.48 | 234 | 65 | 0 | 1.3 | 0.77 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219137 | THOSOLAR C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
219917 | AB1-063 E | 69 | 231 | 75 | 0 | 0.4 | 0.04 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | Y1-075 |  |  | 0.1
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.03 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | X1-071 |  |  | 0.1
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.7 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.43 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 28 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 1122.1 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 1119.7 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 256.8 | 138.13 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 137.8 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | -0.02048 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | -0.02048 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | -0.02048 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 25.82 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 345.42 |  |  | -0.02047 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris2 |  |  | 1
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213798 | MERCK 3 | 13.8 | 230 | 29 | 13 | 42 | 22.59 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 291.92 |  |  | -0.02047 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris1 |  |  | 1
213797 | MERCK 2 | 13.8 | 230 | 29 | 4 | 32 | 17.21 |  |  | -0.02048 |  |  |  | 0.1042 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | W3-080 |  |  | 0.1
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0.63 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | W2-056 |  |  | 0.1
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | W4-103 |  |  | 0.1
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | W2-102 |  |  | 0.1
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 0.39 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | W2-056 |  |  | 0.1
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.02048 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Y3-026 |  |  | 0.1
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | Y3-026 |  |  | 0.1
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 0.34 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | W3-080 |  |  | 0.1
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 3.56 | 0.33 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | W4-103 |  |  | 0.1
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | W2-102 |  |  | 0.1
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0.21 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AC1-017 |  |  | 0.1
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0.2 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | X1-070 |  |  | 0.1
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AB1-025 S |  |  | 0.1
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AB1-025 N |  |  | 0.1
208580 | MGTN 2 | 12.5 | 229 | 77 | 0 | 4.8 | 2.98 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | V4-005 |  |  | 0.1
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 2.75 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219906 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AC1-017 |  |  | 0.1
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 S |  |  | 0.1
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 N |  |  | 0.1
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | T20 |  |  | 0.1
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | X1-070 |  |  | 0.1
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | V4-005 |  |  | 0.1
219685 | NATIONAL_GYP | 26 | 231 | 77 | 0 | 2.8 | 1.89 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
916010 | T20SOLAR E | 0.5 | 230 | 75 | 0 | 2 | 1.22 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | T20 |  |  | 0.1
219922 | AF1-261 | 26.4 | 231 | 75 | 0 | 0.9 | 0.61 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 0.1
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 749 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W2-082 |  |  | 0.1
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W4-025 |  |  | 0.1
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W2-019 |  |  | 0.1
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-129 |  |  | 0.1
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W2-082 |  |  | 0.1
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | X4-015 |  |  | 0.1
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 0.24 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W4-025 |  |  | 0.1
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 0.21 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W2-019 |  |  | 0.1
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-129 |  |  | 0.1
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | X4-015 |  |  | 0.1
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 260.87 |  |  | -0.02049 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
204662 | 27AES GEN1 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | -0.0205 |  |  |  | 0.036 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204663 | 27AES GEN2 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204664 | 27AES GEN3 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.0205 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.0205 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 76.9 | 88.4 | 47.55 |  |  | -0.0205 |  |  |  | 0.036 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
207179 | 28SIXFLAGS | 34.5 | 228 | 77 | 0 | 17 | 0 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 18.29 |  |  | -0.02049 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 32.1 | 17.27 |  |  | -0.0205 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 16.67 |  |  | -0.02049 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
939122 | AE1-142 E O1 | 34.5 | 228 | 75 | 0 | 11.8 | 1.09 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AE1-142 |  |  | 0.1
218780 | PRINCENTON_U | 26 | 231 | 77 | 0 | 31.56 | 21.27 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
207459 | AE1-142 C O1 | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AE1-142 |  |  | 0.1
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0.75 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | Z2-102 |  |  | 0.1
923293 | AB1-138 E | 0.36 | 228 | 75 | 0 | 6 | 0.56 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AB1-138 |  |  | 0.1
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-120 |  |  | 0.1
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-119 |  |  | 0.1
207450 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 0.46 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | Z2-102 |  |  | 0.1
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0.45 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | Z1-096 |  |  | 0.1
206280 | 28LAKEHURS | 34.5 | 228 | 55 | 0 | 13.7 | 10.22 |  |  | -0.0205 |  |  |  | 0.17131 |  | 1 | CAPACITY |  |  |  | 1
207445 | AB1-138 C | 0.38 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AB1-138 |  |  | 0.1
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-119 |  |  | 0.1
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-120 |  |  | 0.1
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | X1-085 |  |  | 0.1
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 0.28 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | Z1-096 |  |  | 0.1
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0.23 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-121 Z |  |  | 0.1
219728 | YARDVSOLFA E | 13.2 | 231 | 75 | 0 | 2.42 | 0.22 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.02049 |  |  |  | 0 |  | 1 | MTX | AA1-060 |  |  | 1
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | X1-085 |  |  | 0.1
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Y |  |  | 0.1
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Z |  |  | 0.1
219727 | YARDVSOLFA C | 13.2 | 231 | 75 | 0 | 1.48 | 0.14 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
219622 | TRENT_BIOGAS | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-121 Y |  |  | 0.1
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 30 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 43.9 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 134.03 |  |  | -0.02051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.02051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.02051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.02051 |  |  |  | 0.0975 |  | 1 | MTX | AA1-100 |  |  | 1
207454 | AA2-184 E | 34.5 | 228 | 75 | 0 | 11.6 | 1.07 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | BenMoreell |  |  | 0.1
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0.98 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | X1-037 |  |  | 0.1
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-124 |  |  | 0.1
207464 | AF1-023 | 34.5 | 228 | 75 | 0 | 8.4 | 0.78 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | BenMoreell |  |  | 0.1
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AC1-207 |  |  | 0.1
207451 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -0.0205 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0.52 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W2-078 |  |  | 0.1
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-113 |  |  | 0.1
207420 | AC1-207 TAP | 34.5 | 228 | 75 | 0 | 4.9 | 0.45 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-207 |  |  | 0.1
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | W3-079 |  |  | 0.1
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 0.39 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | X1-037 |  |  | 0.1
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0.36 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 3 |  |  | 0.1
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-124 |  |  | 0.1
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | W3-079 |  |  | 0.1
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | Y2-051 |  |  | 0.1
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W2-078 |  |  | 0.1
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 3.23 |  |  | -0.0205 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205925 | AF2-428 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-428 |  |  | 0.1
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 0.26 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-113 |  |  | 0.1
901032 | W1-024E OP1 | 34.5 | 228 | 75 | 0 | 2.5 | 0.23 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-024 |  |  | 0.1
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 0.22 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 3 |  |  | 0.1
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0.22 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 4 |  |  | 0.1
219679 | NRGCENTER E | 13.2 | 231 | 55 | 0 | 2 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | X4-031 |  |  | 0.1
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | Y2-051 |  |  | 0.1
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | W1-032 |  |  | 0.1
940922 | AE2-081 E | 34.5 | 228 | 75 | 0 | 1.75 | 0.16 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AE2-081 |  |  | 0.1
207460 | AE2-056 C | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AE2-056 |  |  | 0.1
207463 | AE2-081 C | 34.5 | 228 | 75 | 0 | 1.57 | 0.14 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AE2-081 |  |  | 0.1
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-024 |  |  | 0.1
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 4 |  |  | 0.1
940692 | AE2-056 E | 34.5 | 228 | 75 | 0 | 1.4 | 0.13 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AE2-056 |  |  | 0.1
219650 | TRENT_COLLEG | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.0205 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | W1-032 |  |  | 0.1
219818 | TRENTONSOL E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 5 | 4.26 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0.07 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 0.1
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0.06 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 0.1
219817 | TRENTONSOL C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
940702 | AE2-057 E | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AE2-057 |  |  | 0.1
207461 | AE2-057 C | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AE2-057 |  |  | 0.1
932032 | AC2-009 E | 69 | 231 | 75 | -0.5 | 0.49 | 0.05 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AC2-009 |  |  | 0.1
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0.04 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | W4-058 |  |  | 0.1
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.7 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AA2-058 |  |  | 0.1
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | W4-058 |  |  | 0.1
207419 | AB2-139 E | 34.5 | 228 | 76 | -0.2 | 0.21 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AB2-139 |  |  | 1
961373 | AF2-428 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-428 |  |  | 1
219918 | AC2-009 C | 69 | 231 | 75 | -0.1 | 0.1 | 0.01 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AC2-009 |  |  | 0.1
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0205
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 164.59 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 133.39 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 102.41 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 102.41 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 94.67 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | RED OAK |  |  | 1
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 93.75 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 99.6 | 114.5 | 61.59 |  |  | -0.02052 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 93.2 | 107.1 | 57.61 |  |  | -0.02052 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206327 | 28S RIV G1 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | S RIV |  |  | 1
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 85.3 | 98 | 52.71 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 29.23 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 29.23 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | W2-050 |  |  | 0.1
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W4-060 |  |  | 0.1
924132 | AB2-057 E | 26 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | AB2-057 |  |  | 0.1
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 75.48 |  |  | -0.02051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
219903 | AB2-057 C | 26 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | AB2-057 |  |  | 0.1
205926 | AF2-429 E | 34.5 | 227 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-429 |  |  | 0.1
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W4-060 |  |  | 0.1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V3-024 |  |  | 0.1
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 2 |  |  | 0.1
210323 | AF2-286 E | 13.8 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-286 |  |  | 0.1
205923 | AF2-272 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-272 |  |  | 0.1
205927 | AF2-430 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-430 |  |  | 0.1
205924 | AF2-281 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-281 |  |  | 0.1
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0.23 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-112 |  |  | 0.1
217198 | V3-058 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | V3-058 |  |  | 0.1
217199 | V3-059 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | V3-059 |  |  | 0.1
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V3-024 |  |  | 0.1
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 0.17 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 2 |  |  | 0.1
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0.16 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W3-124 |  |  | 0.1
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0.14 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 1 |  |  | 0.1
218455 | CINNBAY_CGEN | 26.4 | 231 | 64 | 0 | 9 | 7.66 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | X2-088 |  |  | 0.1
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.17 | 0.11 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-112 |  |  | 0.1
205928 | AF2-431 E | 69 | 227 | 75 | 0 | 1.17 | 0.11 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | AF2-431 |  |  | 0.1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.1 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W3-124 |  |  | 0.1
218781 | BRIS_MYERS | 26 | 231 | 77 | 0 | 3 | 2.02 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 1 |  |  | 0.1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | X2-088 |  |  | 0.1
208348 | EELI | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210022 | LING 2 | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210322 | AF2-286 BAT | 13.8 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-286 |  |  | 1
959813 | AF2-272 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-272 |  |  | 1
961383 | AF2-429 BAT | 34.5 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-429 |  |  | 1
961393 | AF2-430 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-430 |  |  | 1
959903 | AF2-281 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-281 |  |  | 1
961403 | AF2-431 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02052 |  |  |  | 0 |  | 1 | MTX | AF2-431 |  |  | 1
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 0 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | NEW |  |  |  | 1
219001 | SEWAREN7GT | 25 | 231 | 58 | 0 | 324.6 | 174.59 |  |  | -0.02053 |  |  |  | 0.036 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
219002 | SEWAREN7ST | 18 | 231 | 58 | 0 | 216.4 | 116.4 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
208947 | WSHO CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208942 | HARR CT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | -0.02052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.02053 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.02053 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W3-029 |  |  | 0.1
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0.93 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W3-003 |  |  | 0.1
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 7.45 |  |  | -0.02052 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0.46 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | V3-070 |  |  | 0.1
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0.38 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 0.1
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0.38 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AB1-139 |  |  | 0.1
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | X2-075 |  |  | 0.1
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 0.1
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W3-029 |  |  | 0.1
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | V3-070 |  |  | 0.1
219908 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 0.23 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-139 |  |  | 0.1
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 0.21 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | X2-075 |  |  | 0.1
219916 | AD2-025 E | 13.2 | 231 | 76 | -2 | 2 | 0 |  |  | -0.02052 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
936193 | AD2-025_E | 13.2 | 231 | 76 | 0 | 2 | 0 |  |  | -0.02052 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W1-132 |  |  | 0.1
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | V4-070 |  |  | 0.1
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-061 |  |  | 0.1
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | V4-069 |  |  | 0.1
217212 | AMBOY SO E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | V3-069 |  |  | 0.1
218527 | CNTRALGAS2 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
218525 | CNTRALGAS1 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0.12 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | X2-089 |  |  | 0.1
218526 | CNTRALGAS2 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
218524 | CNTRALGAS1 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | V4-069 |  |  | 0.1
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | V4-070 |  |  | 0.1
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-061 |  |  | 0.1
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AE1-041 |  |  | 0.1
217213 | AMBOY SO C | 13.2 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | V3-069 |  |  | 0.1
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.07 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | X2-089 |  |  | 0.1
219920 | AE1-041 EBAT | 26.4 | 231 | 76 | -0.5 | 0.5 | 0 |  |  | -0.02053 |  |  |  | 0 |  | 1 | MTX | AE1-041 |  |  | 1
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0.04 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | W2-036 |  |  | 0.1
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0.03 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-052 |  |  | 0.1
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | W2-036 |  |  | 0.1
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-052 |  |  | 0.1
219919 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-041 |  |  | 0.1
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 10.2 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0205
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 302.3 | 162.6 |  |  | -0.02053 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 302.1 | 162.49 |  |  | -0.02053 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
990902 | TOSCO_E | 18 | 231 | 2 | 0 | 137.5 | 0 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | ENERGY | Tosco |  |  | 1
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 139.31 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 135.65 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 113.38 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 96.22 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 96.22 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 50.99 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 45.24 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 72.1 | 82.9 | 44.59 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 43.57 |  |  | -0.02054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 25.52 |  |  | -0.02053 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
218344 | TOSCO_G6 | 18 | 231 | 2 | 37 | 42.5 | 22.86 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | CAPACITY | Tosco |  |  | 1
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 18.4 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 25.21 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-016 |  |  | 0.1
218672 | KENILWRTH E | 26.4 | 231 | 65 | 0 | 8 | 0 |  |  | -0.02053 |  |  |  | 0.1097 |  | 1 | NEW |  |  |  | 1
217831 | PB_NUTCLIF | 26 | 231 | 77 | 0 | 10.7 | 7.21 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217850 | MONTCLAIR_U | 26 | 231 | 77 | 0 | 10.6 | 7.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217825 | UMD_NJ | 26 | 231 | 77 | 0 | 10.5 | 7.08 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 3.55 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V2-025 |  |  | 0.1
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-016 |  |  | 0.1
211089 | AF2-277 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | AF2-277 |  |  | 0.1
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217194 | REDH C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V2-025 |  |  | 0.1
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | W4-059 |  |  | 0.1
219910 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0.14 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
218450 | LINSOLAR E | 26.4 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-080 |  |  | 0.1
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.24 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218449 | LINSOLAR C | 26.4 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W1-101 |  |  | 0.1
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-080 |  |  | 0.1
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0.06 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | AB1-021 |  |  | 0.1
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0.06 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | X2-087 |  |  | 0.1
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | X1-072 |  |  | 0.1
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.05 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W1-101 |  |  | 0.1
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0.05 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-067 |  |  | 0.1
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | X2-087 |  |  | 0.1
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | X1-072 |  |  | 0.1
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-065 |  |  | 0.1
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | AB1-021 |  |  | 0.1
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-067 |  |  | 0.1
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-066 |  |  | 0.1
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-068 |  |  | 0.1
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.02 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | W4-059 |  |  | 0.1
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.02 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-065 |  |  | 0.1
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-068 |  |  | 0.1
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-066 |  |  | 0.1
211088 | AF2-277 BAT | 69 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02054 |  |  |  | 0 |  | 1 | MTX | AF2-277 |  |  | 1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200044 | BETH CT1 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | -0.02055 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200048 | BETH CT5 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
207466 | AF1-324 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.02055 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207458 | AD2-210_C | 34.5 | 228 | 76 | 0 | 8 | 0 |  |  | -0.02054 |  |  |  | 0.05 |  | 1 | NEW |  |  |  | 1
AD2-210 | BATEXP_AD2-210->PJM |  |  | LTF |  | 8 |  |  |  | -0.0205
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -0.02055 |  |  |  | 0 |  | 1 | NEW | V4-001 |  |  | 0.1
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | X1-095 |  |  | 0.1
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | X1-095 |  |  | 0.1
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.07 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | V4-001 |  |  | 0.1
207456 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.02055 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 153 | 82.29 |  |  | -0.02056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 91.3 | 105 | 56.48 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 89.6 | 103 | 55.4 |  |  | -0.02056 |  |  |  | 0.036 |  | 1 | CAPACITY | GILBERT |  |  | 1
206341 | 28GIL 8 | 13.8 | 228 | 58 | 82.2 | 94.5 | 50.83 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
207403 | 28AA2-082 E | 34.5 | 228 | 76 | -18 | 18 | 0 |  |  | -0.02056 |  |  |  | 0.05 |  | 1 | MTX | AA2-082 |  |  | 1
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W3-044 |  |  | 0.1
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX | AA2-061 |  |  | 1
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 0.7 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W3-044 |  |  | 0.1
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX | AA2-060 |  |  | 1
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-046 |  |  | 0.1
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | X1-012 |  |  | 0.1
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0.57 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | BeaverRun |  |  | 0.1
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0.43 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W3-110 |  |  | 0.1
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0.4 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AD2-070 |  |  | 0.1
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | BeaverRun |  |  | 0.1
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | X1-012 |  |  | 0.1
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AD2-070 |  |  | 0.1
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 0.26 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W3-110 |  |  | 0.1
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 0.22 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-046 |  |  | 0.1
AA2-082 | BATEXP_AA2-082->PJM |  |  | LTF |  | 2 |  |  |  | -0.0206
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-097 |  |  | 0.1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AC2-175 |  |  | 0.1
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0.12 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AE1-081 |  |  | 0.1
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-097 |  |  | 0.1
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.09 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AE1-081 |  |  | 0.1
207402 | 28AA2-082 C | 34.5 | 228 | 76 | 0 | 2 | 1.19 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AA2-082 |  |  | 1
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | -0.02056 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH5678 |  |  | 1
207470 | AF1-327 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207468 | AF1-326 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
204651 | 27PORT CT | 13.8 | 227 | 55 | 4 | 37 | 19.9 |  |  | -0.02057 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02057 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 0.1
206747 | 28DSM_X3-029 | 34.5 | 228 | 58 | 0 | 11.15 | 0 |  |  | -0.02056 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
207462 | AF1-133 C | 34.5 | 228 | 75 | 0 | 12 | 1.11 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AF1-133 |  |  | 0.1
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-073 |  |  | 0.1
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W3-077 |  |  | 0.1
944682 | AF1-133 E | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AF1-133 |  |  | 0.1
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.02057 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 0.1
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.02056 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W2-091 |  |  | 0.1
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W3-077 |  |  | 0.1
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 3.04 | 0.28 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-073 |  |  | 0.1
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 3.8 | 2.04 |  |  | -0.02057 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W1-127 |  |  | 0.1
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-064 |  |  | 0.1
916006 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 4.4 | 2.69 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W2-091 |  |  | 0.1
916005 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 3.45 | 2.11 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | Y2-018 |  |  | 0.1
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0.12 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | U2-059 |  |  | 0.1
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W1-127 |  |  | 0.1
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-064 |  |  | 0.1
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | U2-059 |  |  | 0.1
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.47 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 0.35 | 0.03 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | Y2-018 |  |  | 0.1
207455 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.02056 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | -0.02058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | -0.02058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 128.98 |  |  | -0.02058 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 107.57 |  |  | -0.02058 |  |  |  | 0.036 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 107.57 |  |  | -0.02058 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 140.5 | 75.57 |  |  | -0.02057 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | -0.02058 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | -0.02058 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | -0.02058 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
208946 | MACR CT | 12.5 | 229 | 55 | 61.4 | 70.6 | 37.97 |  |  | -0.02058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 21 | 11.3 |  |  | -0.02059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209945 | AF2-278 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02059 |  |  |  | 0 |  | 1 | NEW | AF2-278 |  |  | 0.1
209944 | AF2-278 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02059 |  |  |  | 0 |  | 1 | MTX | AF2-278 |  |  | 1
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 26.98 |  |  | -0.02059 |  |  |  | 0 |  | 1 | NEW | S14 |  |  | 0.8
208940 | ALLE CT | 12.5 | 229 | 55 | 48.7 | 56 | 30.12 |  |  | -0.02059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 6.74 |  |  | -0.02059 |  |  |  | 0 |  | 1 | CAPACITY | S14 |  |  | 0.8
209007 | NOEN IPP | 13.8 | 229 | 12 | 96.9 | 111.4 | 105.11 |  |  | -0.0206 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
935072 | AD1-143 E1 | 69 | 229 | 74 | 0 | 34.28 | 20.93 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.8
211065 | PASP 1_2 C | 13.8 | 229 | 75 | 0 | 8 | 0.74 |  |  | -0.0206 |  |  |  | 0 |  | 1 | CAPACITY | AC1-087 |  |  | 0.1
926082 | PASP 1 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | U4-014 |  |  | 0.1
942581 | PASP 2 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AC1-087 |  |  | 0.1
935071 | AD1-143 C1 | 69 | 229 | 75 | 0 | 5.72 | 0.53 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.1
935082 | AD1-143 E2 | 69 | 229 | 75 | 0 | 4.8 | 0.44 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.1
210319 | WCAR 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02061 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
935081 | AD1-143 C2 | 69 | 229 | 75 | 0 | 0.2 | 0.02 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.1
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 124.2 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 72.8 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 55.94 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | U2-073 A |  |  | 0.8
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 52.08 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 0.8
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 24.52 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | U2-073 B |  |  | 0.8
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 14.6 | 7.03 |  |  | -0.02062 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 A |  |  | 0.8
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 7.75 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 0.8
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 8.4 | 4.05 |  |  | -0.02062 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 B |  |  | 0.8
208920 | WLPK | 12.5 | 229 | 60 | 35.5 | 40.8 | 28.68 |  |  | -0.02065 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 32 |  |  | -0.02066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 31.63 |  |  | -0.02066 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
211375 | BEAC | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.02066 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 15.92 |  |  | -0.02066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
211591 | HARW | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | -0.02066 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | -0.02066 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
916009 | LOR2_Q27 E | 0.7 | 229 | 74 | 0 | 88.8 | 54.21 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW | Q27 |  |  | 0.8
208941 | FISH CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | -0.02066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916001 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 44.5 | 21.44 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW | N47 |  |  | 0.8
916008 | LOR1 E | 0.7 | 229 | 74 | 0 | 23.8 | 14.53 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW | N14 |  |  | 0.8
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 5.16 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY | N47 |  |  | 0.8
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 81.14 |  |  | -0.02066 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 77.37 |  |  | -0.02066 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.2 | 6.84 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY | Q27 |  |  | 0.8
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.14 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY | N14 |  |  | 0.8
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1251.7 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 4.3 |  |  | -0.02067 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 40.29 |  |  | -0.02067 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 30.66 |  |  | -0.02067 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 5.19 |  |  | -0.02067 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1253.3 |  |  | -0.02067 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
921653 | AA2-008 E | 230 | 229 | 58 | 0 | 57 | 0 |  |  | -0.02068 |  |  |  | 0.036 |  | 1 | ENERGY | MOXIE PATRIOT |  |  | 1
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 25.15 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW | U2-030 |  |  | 0.8
209018 | SUNBIPCT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | -0.02069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 0.26 |  |  | -0.02068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208948 | WILL CT | 12.5 | 229 | 55 | 23.1 | 26.6 | 14.31 |  |  | -0.02068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 3.76 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | U2-030 |  |  | 0.8
212464 | AF2-289 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-289 |  |  | 0.1
212451 | AF2-427 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-427 |  |  | 0.1
211938 | AF2-285 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-285 |  |  | 0.1
212495 | AF2-284 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-284 |  |  | 0.1
212455 | AF2-290 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW | AF2-290 |  |  | 0.1
212005 | ALWD | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212345 | PENS | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212435 | SMIL | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212494 | AF2-284 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-284 |  |  | 1
212461 | AF2-289 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-289 |  |  | 1
212450 | AF2-427 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-427 |  |  | 1
211937 | AF2-285 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-285 |  |  | 1
212454 | AF2-290 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02069 |  |  |  | 0 |  | 1 | MTX | AF2-290 |  |  | 1
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 758.5 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 757.9 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 26.19 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 26.03 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 23.83 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.02069 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 15.71 |  |  | -0.02069 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
208944 | JENK CT | 12.5 | 229 | 55 | 24 | 27.6 | 14.85 |  |  | -0.02069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
946263 | BECR K09 E | 0.69 | 229 | 74 | 0 | 20.7 | 12.64 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW | L18 |  |  | 0.8
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.02 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | L18 |  |  | 0.8
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 213 |  |  | -0.0207 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 130.16 |  |  | -0.0207 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | -0.0207 |  |  |  | 0.036 |  | 1 | CAPACITY | Hummel |  |  | 1
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | -0.0207 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
211374 | AVOC | 12.5 | 229 | 77 | 0 | 17.4 | 10.8 |  |  | -0.02071 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | -0.02073 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | -0.02073 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | -0.02073 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 37.91 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 0.8
209031 | WAYM IPP E | 34.5 | 229 | 74 | 0 | 55.5 | 33.88 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | K21 |  |  | 0.8
209009 | PEIP 2 | 13.8 | 229 | 56 | 38 | 43.7 | 23.5 |  |  | -0.02073 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.02073 |  |  |  | 0.0975 |  | 1 | MTX | Z2-107 |  |  | 1
209010 | PEIP 1 | 13.8 | 229 | 64 | 17.4 | 26.5 | 21.42 |  |  | -0.02073 |  |  |  | 0.28996 |  | 1 | CAPACITY |  |  |  | 1
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 5.49 |  |  | -0.02073 |  |  |  | 0 |  | 1 | CAPACITY | K21 |  |  | 0.8
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 5.34 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 0.8
209972 | AF2-288 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-288 |  |  | 0.1
209937 | AF2-287 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-287 |  |  | 0.1
211490 | AF2-282 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-282 |  |  | 0.1
211554 | AF2-283 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-283 |  |  | 0.1
209971 | AF2-288 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-288 |  |  | 1
209936 | AF2-287 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-287 |  |  | 1
211489 | AF2-282 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-282 |  |  | 1
211553 | AF2-283 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-283 |  |  | 1
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 28.23 |  |  | -0.02085 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 0.8
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 11.56 |  |  | -0.02085 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 0.8
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.3 | 8.34 |  |  | -0.02085 |  |  |  | 0 |  | 1 | CAPACITY | K28 |  |  | 0.8
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 41.39 |  |  | -0.02088 |  |  |  | 0 |  | 1 | NEW | P59 |  |  | 0.8
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 5.64 |  |  | -0.02088 |  |  |  | 0 |  | 1 | CAPACITY | P59 |  |  | 0.8
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 389 |  |  |  | -0.0209
916000 | 01BACKB E | 34.5 | 201 | 74 | 0 | 57.9 | 27.9 |  |  | -0.02091 |  |  |  | 0 |  | 1 | NEW | K19 |  |  | 0.8
237013 | AA2-103 E | 0.48 | 201 | 76 | 0 | 20 | 0 |  |  | -0.02091 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 3.9 |  |  | -0.02091 |  |  |  | 0 |  | 1 | CAPACITY | K19 |  |  | 0.8
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 20.96 |  |  | -0.02093 |  |  |  | 0 |  | 1 | NEW | U2-061 |  |  | 0.8
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 3.13 |  |  | -0.02093 |  |  |  | 0 |  | 1 | CAPACITY | U2-061 |  |  | 0.8
943302 | AF1-001 E | 34.5 | 201 | 75 | 0 | 7.25 | 0.53 |  |  | -0.02094 |  |  |  | 0 |  | 1 | NEW | AF1-001 |  |  | 0.1
237039 | AF1-001 C | 34.5 | 201 | 75 | 0 | 6.5 | 0.47 |  |  | -0.02094 |  |  |  | 0 |  | 1 | CAPACITY | AF1-001 |  |  | 0.1
243415 | 05WWVSTA | 69 | 205 | 61 | 69.8 | 96 | 53.26 |  |  | -0.02099 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 21.4 | 11.51 |  |  | -0.021 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 7.03 |  |  | -0.021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 6.96 |  |  | -0.021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1308.8 | 1308.8 |  |  | -0.02105 |  |  |  | 0 |  | 1 | CAPACITY | MTG1 |  |  | 1
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 236.66 |  |  | -0.02109 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | -0.02109 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | -0.02109 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 25.91 |  |  | -0.02113 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 253.85 |  |  | -0.02114 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.02114 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 73.26 |  |  | -0.02114 |  |  |  | 0 |  | 1 | NEW | P28 |  |  | 0.8
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 31.73 |  |  | -0.02114 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 11.51 |  |  | -0.02114 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 13.37 |  |  | -0.02114 |  |  |  | 0 |  | 1 | CAPACITY | P28 |  |  | 0.8
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 317.2 | 121.14 |  |  | -0.02114 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | -0.02114 |  |  |  | 0.036 |  | 1 | CAPACITY | RONCO |  |  | 1
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | -0.02114 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
237068 | AA2-119 GEN | 20.5 | 201 | 58 | 0 | 600 | 0 |  |  | -0.02115 |  |  |  | 0.036 |  | 1 | NEW | Harrison |  |  | 1
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1407 | 1407 |  |  | -0.02115 |  |  |  | 0 |  | 1 | CAPACITY | GVG2 |  |  | 1
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1389 | 1389 |  |  | -0.02115 |  |  |  | 0 |  | 1 | CAPACITY | GVG1 |  |  | 1
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.22 |  |  | -0.02117 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 552 |  |  | -0.02118 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 545.5 |  |  | -0.02118 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 850.6 |  |  | -0.02119 |  |  |  | 0 |  | 1 | CAPACITY | Cone1 |  |  | 1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 850 |  |  | -0.02119 |  |  |  | 0 |  | 1 | CAPACITY | Cone2 |  |  | 1
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 710 |  |  | -0.02119 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
913142 | Y1-033 E OP1 | 0.7 | 226 | 74 | 0 | 34.02 | 20.77 |  |  | -0.02122 |  |  |  | 0 |  | 1 | NEW | Y1-033 |  |  | 0.8
203926 | AA2-133 GEN | 13.8 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | -0.02122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 3.05 |  |  | -0.02122 |  |  |  | 0 |  | 1 | CAPACITY | Y1-033 |  |  | 0.8
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 59.57 |  |  | -0.02125 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 14.76 |  |  | -0.02127 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
916002 | 01ELLIOTTS E | 34.5 | 201 | 74 | 0 | 44.9 | 21.63 |  |  | -0.02129 |  |  |  | 0 |  | 1 | NEW | N32 |  |  | 0.8
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 2.65 |  |  | -0.02129 |  |  |  | 0 |  | 1 | CAPACITY | N32 |  |  | 0.8
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | -0.0213 |  |  |  | 0 |  | 1 | CAPACITY | X1-109 |  |  | 1
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | -0.0213 |  |  |  | 0.036 |  | 1 | CAPACITY | X1-109 |  |  | 1
203937 | 26AA1-144 G2 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203936 | 26AA1-144 G1 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | -0.02131 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.11 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235587 | 01HARRN3 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235586 | 01HARRN2 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235585 | 01HARRN1 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 41.94 |  |  | -0.02132 |  |  |  | 0.39467 |  | 1 | CAPACITY |  |  |  | 1
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0.11 |  |  | -0.02132 |  |  |  | 0 |  | 1 | NEW | V4-073 |  |  | 0.1
253303 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.07 |  |  | -0.02132 |  |  |  | 0 |  | 1 | CAPACITY | V4-073 |  |  | 0.1
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.02133 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.02135 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 25.64 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | K23 |  |  | 0.8
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 19.54 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | L13 |  |  | 0.8
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 17.58 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 0.8
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.02135 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 3.85 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | Lookout Wind |  |  | 0.8
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 3.6 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | L13 |  |  | 0.8
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 4.8 | 2.93 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | K23 |  |  | 0.8
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 1.1 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 0.8
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 124.5 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | -0.02135 |  |  |  | 0.036 |  | 1 | CAPACITY | T-174 |  |  | 1
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | -0.02135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | -0.02135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237041 | AE2-055 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | -0.02136 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 0.1
940682 | AE2-055 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02136 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 0.1
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | -0.02137 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | -0.02137 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.02137 |  |  |  | 0 |  | 1 | MTX | AC1-025 |  |  | 1
203938 | 26AA2-132 | 34.5 | 226 | 29 | 0 | 19.9 | 0 |  |  | -0.02138 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
236828 | 01GRAYMONT | 46 | 201 | 75 | 0 | 4 | 0.29 |  |  | -0.02139 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 34.19 |  |  | -0.0214 |  |  |  | 0 |  | 1 | NEW | K02 |  |  | 0.8
237083 | AE1-147_GEN | 0.6 | 201 | 75 | 0 | 19.98 | 1.46 |  |  | -0.02139 |  |  |  | 0 |  | 1 | CAPACITY | AE1-147 |  |  | 0.1
939171 | AE1-147_E | 0.6 | 201 | 75 | 0 | 7.98 | 0.58 |  |  | -0.02139 |  |  |  | 0 |  | 1 | NEW | AE1-147 |  |  | 0.1
203944 | AF2-271 E | 46 | 226 | 75 | 0 | 3 | 0.28 |  |  | -0.02139 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | -0.0214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 11.3 |  |  | -0.0214 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 410 | 156.58 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235619 | 01SBEND1 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235620 | 01SBEND2 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235622 | 01SBEND4 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235621 | 01SBEND3 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 39.07 |  |  | -0.02142 |  |  |  | 0 |  | 1 | NEW | N39 |  |  | 0.8
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 34.19 |  |  | -0.02142 |  |  |  | 0 |  | 1 | NEW | O38 |  |  | 0.8
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 11.1 | 6.78 |  |  | -0.02142 |  |  |  | 0 |  | 1 | CAPACITY | N39 |  |  | 0.8
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.1 | 5.56 |  |  | -0.02142 |  |  |  | 0 |  | 1 | CAPACITY | O38 |  |  | 0.8
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 852.3 | 852.3 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | Keys1 |  |  | 1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 851.6 | 851.6 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | Keys2 |  |  | 1
237048 | AF1-022 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | AF1-022 |  |  | 0.1
943512 | AF1-022 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | -0.02143 |  |  |  | 0 |  | 1 | NEW | AF1-022 |  |  | 0.1
957932 | AF2-087 E | 46 | 226 | 75 | 0 | 4.2 | 0.39 |  |  | -0.02143 |  |  |  | 0 |  | 1 | NEW | AF2-087 |  |  | 0.1
203941 | AF2-087 C | 46 | 226 | 75 | 0 | 3.05 | 0.28 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | AF2-087 |  |  | 0.1
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 10.04 |  |  | -0.02145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916004 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | -0.02144 |  |  |  | 0 |  | 1 | NEW | K22 |  |  | 0.8
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.55 |  |  | -0.02144 |  |  |  | 0 |  | 1 | CAPACITY | K22 |  |  | 0.8
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.53 |  |  | -0.02144 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 11.3 |  |  | -0.02145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 44 | 26.86 |  |  | -0.02147 |  |  |  | 0 |  | 1 | NEW | P60 |  |  | 0.8
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 5.19 |  |  | -0.02147 |  |  |  | 0 |  | 1 | CAPACITY | P60 |  |  | 0.8
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 49.15 |  |  | -0.02148 |  |  |  | 0 |  | 1 | NEW | P47 |  |  | 0.8
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.2 | 9.28 |  |  | -0.02148 |  |  |  | 0 |  | 1 | CAPACITY | P47 |  |  | 0.8
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 31.6 | 19.29 |  |  | -0.0215 |  |  |  | 0 |  | 1 | NEW | Q53 |  |  | 0.8
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 21.5 | 11.56 |  |  | -0.02149 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203942 | AF2-270 E | 23 | 226 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02149 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 3.91 |  |  | -0.0215 |  |  |  | 0 |  | 1 | CAPACITY | Q53 |  |  | 0.8
203940 | AF1-140 C | 23 | 226 | 75 | 0 | 9.78 | 0.9 |  |  | -0.0215 |  |  |  | 0 |  | 1 | CAPACITY | AF1-140 |  |  | 0.1
944752 | AF1-140 E | 23 | 226 | 75 | 0 | 6.52 | 0.6 |  |  | -0.0215 |  |  |  | 0 |  | 1 | NEW | AF1-140 |  |  | 0.1
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 62.3 | 38.03 |  |  | -0.02151 |  |  |  | 0 |  | 1 | NEW | R32 |  |  | 0.8
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 54.4 | 33.21 |  |  | -0.02151 |  |  |  | 0 |  | 1 | NEW | O18 |  |  | 0.8
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 26.2 | 15.99 |  |  | -0.02151 |  |  |  | 0 |  | 1 | NEW | K13 |  |  | 0.8
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 7.75 |  |  | -0.02151 |  |  |  | 0 |  | 1 | CAPACITY | R32 |  |  | 0.8
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | -0.02151 |  |  |  | 0 |  | 1 | CAPACITY | O18 |  |  | 0.8
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 1.95 |  |  | -0.02151 |  |  |  | 0 |  | 1 | CAPACITY | K13 |  |  | 0.8
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 525.7 |  |  | -0.02152 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200503 | 26C.SLOPE | 115 | 226 | 11 | 17 | 50 | 0 |  |  | -0.02152 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 41.7 | 25.46 |  |  | -0.02153 |  |  |  | 0 |  | 1 | NEW | Q36 |  |  | 0.8
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 5.07 |  |  | -0.02153 |  |  |  | 0 |  | 1 | CAPACITY | Q36 |  |  | 0.8
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 0.2 |  |  | -0.02155 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
237046 | AF1-021 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | -0.02155 |  |  |  | 0 |  | 1 | CAPACITY | AF1-021 |  |  | 0.1
943502 | AF1-021 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | -0.02155 |  |  |  | 0 |  | 1 | NEW | AF1-021 |  |  | 0.1
203946 | AE2-131 C | 34.5 | 226 | 75 | 0 | 12 | 1.11 |  |  | -0.02156 |  |  |  | 0 |  | 1 | CAPACITY | AE2-131 |  |  | 0.1
941352 | AE2-131 E | 34.5 | 226 | 75 | 0 | 8 | 0.74 |  |  | -0.02156 |  |  |  | 0 |  | 1 | NEW | AE2-131 |  |  | 0.1
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 127.94 |  |  | -0.02157 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 0.2 |  |  | -0.02156 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200665 | 26SHAWVL 3 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | -0.02157 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200666 | 26SHAWVL 4 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | -0.02157 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 0.15 |  |  | -0.02158 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 92.04 |  |  | -0.02159 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
200722 | 26SHAWVL 2 | 18 | 226 | 30 | 62 | 125 | 117.94 |  |  | -0.02158 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200715 | 26SHAWVL 1 | 18 | 226 | 30 | 62 | 123 | 116.05 |  |  | -0.02158 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 17.22 |  |  | -0.02159 |  |  |  | 0 |  | 1 | NEW | V3-030 |  |  | 0.8
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 3.24 |  |  | -0.02159 |  |  |  | 0 |  | 1 | CAPACITY | V3-030 |  |  | 0.8
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4 |  |  | -0.0216 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
916003 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 13.3 | 6.41 |  |  | -0.02161 |  |  |  | 0 |  | 1 | NEW | K20 |  |  | 0.8
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 0.82 |  |  | -0.02161 |  |  |  | 0 |  | 1 | CAPACITY | K20 |  |  | 0.8
200809 | 26SITHE | 138 | 226 | 60 | 0 | 36 | 25.31 |  |  | -0.02163 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 620 |  |  | -0.02163 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | -0.02164 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | -0.02164 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 8.66 |  |  | -0.02166 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
237054 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 195.92 |  |  | -0.02167 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
237043 | AE2-125 C | 25 | 201 | 75 | 0 | 8.28 | 0.6 |  |  | -0.02166 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 0.1
941312 | AE2-125 E | 25 | 201 | 75 | 0 | 5.52 | 0.4 |  |  | -0.02166 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 0.1
200805 | 26COLVER13 | 13.2 | 226 | 12 | 95.7 | 110 | 0 |  |  | -0.02169 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 34.62 |  |  | -0.02169 |  |  |  | 0 |  | 1 | NEW | Z1-069 |  |  | 0.8
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 17.1 | 10.44 |  |  | -0.02169 |  |  |  | 0 |  | 1 | CAPACITY | Z1-069 |  |  | 0.8
237036 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 7.64 |  |  | -0.02172 |  |  |  | 0.1042 |  | 1 | CAPACITY | AD2-002 |  |  | 1
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.02172 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-068 |  |  | 0.1
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-069 |  |  | 0.1
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-165 |  |  | 0.1
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-166 |  |  | 0.1
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-165 |  |  | 0.1
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-166 |  |  | 0.1
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-068 |  |  | 0.1
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-069 |  |  | 0.1
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 63.89 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 63.82 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253127 | 09CEDRVL | 69 | 209 | 77 | 0 | 1.8 | 1.3 |  |  | -0.02174 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 2.26 |  |  | -0.02176 |  |  |  | 0 |  | 1 | NEW | AC2-067 |  |  | 0.1
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 1.93 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY | AC2-067 |  |  | 0.1
237050 | AF1-155 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY | AF1-155 |  |  | 0.1
944902 | AF1-155 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02176 |  |  |  | 0 |  | 1 | NEW | AF1-155 |  |  | 0.1
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 650 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 614 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235590 | 01PLEAS1 | 26 | 201 | 16 | 300 | 639 | 0 |  |  | -0.02177 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235591 | 01PLEAS2 | 26 | 201 | 16 | 350 | 639 | 0 |  |  | -0.02177 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 42.3 |  |  | -0.02179 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 173.6 | 199.5 | 76.19 |  |  | -0.02181 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 167 | 191.9 | 73.29 |  |  | -0.02181 |  |  |  | 0.036 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 164.1 | 188.6 | 72.03 |  |  | -0.02181 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | -0.02181 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | -0.02181 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | -0.02185 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | -0.02185 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.02187 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.02187 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.02187 |  |  |  | 0.036 |  | 1 | NEW | AB1-069 |  |  | 1
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 170.9 | 65.27 |  |  | -0.02187 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 170.8 | 65.23 |  |  | -0.02187 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 3.83 |  |  | -0.02187 |  |  |  | 0.0789 |  | 1 | CAPACITY | ALLEG LD_5 |  |  | 1
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 4.22 |  |  | -0.02189 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 3.77 |  |  | -0.02196 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237052 | AF1-210 C | 25 | 201 | 75 | 0 | 9.54 | 0.7 |  |  | -0.02199 |  |  |  | 0 |  | 1 | CAPACITY | AF1-210 |  |  | 0.1
945452 | AF1-210 E | 25 | 201 | 75 | 0 | 6.36 | 0.46 |  |  | -0.02199 |  |  |  | 0 |  | 1 | NEW | AF1-210 |  |  | 0.1
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 21.23 |  |  | -0.0221 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
203932 | AE1-123 | 34.5 | 226 | 55 | 0 | 18 | 9.68 |  |  | -0.0221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 164.5 |  |  | -0.02214 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 155.36 |  |  | -0.02214 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 21.09 |  |  | -0.02214 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 30.93 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 30.55 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 30.17 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 2.69 |  |  | -0.02222 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 62 | 33.35 |  |  | -0.02235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 139.32 |  |  | -0.02239 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.02239 |  |  |  | 0.036 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.02239 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.02239 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 80.2 |  |  | -0.02242 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 10.54 |  |  | -0.02249 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203939 | AE1-160 C | 34.5 | 226 | 75 | 0 | 12.7 | 1.17 |  |  | -0.0225 |  |  |  | 0 |  | 1 | CAPACITY | AE1-160 |  |  | 0.1
939292 | AE1-160 E | 34.5 | 226 | 75 | 0 | 7.3 | 0.68 |  |  | -0.0225 |  |  |  | 0 |  | 1 | NEW | AE1-160 |  |  | 0.1
253029 | 09GRNVIL | 138 | 209 | 77 | 0 | 4.5 | 3.26 |  |  | -0.02253 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 113.43 |  |  | -0.0226 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | -0.0226 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | -0.0226 |  |  |  | 0.036 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 770.1 |  |  | -0.02262 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254026 | 15USSILL | 138 | 215 | 77 | 0 | 66 | 27.72 |  |  | -0.02266 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 790.2 |  |  | -0.02266 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254024 | 15CLAIRT | 138 | 215 | 77 | 0 | 35 | 14.7 |  |  | -0.02267 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
270122 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 185.22 |  |  | -0.0227 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 77.49 |  |  | -0.0227 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
254037 | 15UNIVRS | 138 | 215 | 77 | 0 | 1.1 | 0.46 |  |  | -0.02272 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 567.5 |  |  | -0.02275 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239022 | 02NWCAG3 | 14.4 | 202 | 57 | 20 | 92.3 | 35.25 |  |  | -0.02282 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 38.8 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253970 | 15BI2 | 13.8 | 215 | 58 | 83.2 | 95.6 | 36.51 |  |  | -0.02282 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.5 | 18.52 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 6.91 |  |  | -0.02282 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 620.4 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239024 | 02NWCAG5 | 16.5 | 202 | 57 | 23 | 145 | 55.38 |  |  | -0.02285 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | -0.02285 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239023 | 02NWCAG4 | 14.4 | 202 | 57 | 20 | 93 | 35.52 |  |  | -0.02286 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 0.04 |  |  | -0.02286 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0.53 |  |  | -0.02293 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 0.1
254303 | AC2-168 C | 138 | 215 | 75 | 0 | 4.4 | 0.32 |  |  | -0.02293 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 0.1
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.26 |  |  | -0.02293 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 216.9 |  |  | -0.02295 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 13.77 |  |  | -0.02296 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | -0.02295 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | -0.02295 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253924 | 15SHELL | 138 | 215 | 58 | 0 | 98 | 0 |  |  | -0.02298 |  |  |  | 0.036 |  | 1 | ENERGY | Y3-103 |  |  | 1
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 15.2 | 5.8 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | -0.02298 |  |  |  | 0.036 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254304 | AE2-114 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AE2-114 |  |  | 0.1
254305 | AE2-115 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AE2-115 |  |  | 0.1
941202 | AE2-114 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | -0.02301 |  |  |  | 0 |  | 1 | NEW | AE2-114 |  |  | 0.1
941212 | AE2-115 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | -0.02301 |  |  |  | 0 |  | 1 | NEW | AE2-115 |  |  | 0.1
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | -0.02301 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 2.69 |  |  | -0.02302 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 156.58 |  |  | -0.02305 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | -0.02305 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | -0.02305 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
253197 | 09PIQUA3 | 69 | 209 | 77 | 0 | 38.3 | 2.77 |  |  | -0.02307 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 899.3 |  |  | -0.02307 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253900 | 15BVRVL1 | 22 | 215 | 44 | 781.7 | 898.5 | 898.5 |  |  | -0.02307 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 280 | 106.93 |  |  | -0.02314 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | -0.02314 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | -0.02314 |  |  |  | 0.036 |  | 1 | CAPACITY | Y2-050 |  |  | 1
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 26.1 | 16.36 |  |  | -0.02318 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 307.6 | 117.47 |  |  | -0.02321 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | -0.02321 |  |  |  | 0.036 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | -0.02321 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.02322 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
241951 | AB1-105 OP | 345 | 202 | 58 | 0 | 850 | 0 |  |  | -0.02327 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 4.3 |  |  | -0.02336 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.02338 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.02338 |  |  |  | 0.036 |  | 1 | CAPACITY | Guernsey |  |  | 1
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.02338 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.02342 |  |  |  | 0 |  | 1 | NEW | U2-090 |  |  | 0.8
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.02342 |  |  |  | 0 |  | 1 | NEW | V3-007 |  |  | 0.8
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.02342 |  |  |  | 0 |  | 1 | CAPACITY | U2-090 |  |  | 0.8
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.02342 |  |  |  | 0 |  | 1 | CAPACITY | V3-007 |  |  | 0.8
270106 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.02355 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
245305 | 05WOOSTER | 69 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.02356 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245304 | 05WOOSTER | 23 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.02358 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243158 | 05WOOSTE | 138 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.02359 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 2.55 |  |  | -0.02378 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.0238 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.02382 |  |  |  | 0 |  | 1 | NEW | U3-002 |  |  | 0.8
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 6.36 |  |  | -0.02382 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 0.8
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 6.17 |  |  | -0.02382 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 0.8
253234 | 09VERSAL | 69 | 209 | 77 | 0 | 5.4 | 3.91 |  |  | -0.02388 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 243 | 92.8 |  |  | -0.02391 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -0.02391 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -0.02391 |  |  |  | 0.036 |  | 1 | CAPACITY | DRESDEN |  |  | 1
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1247 |  |  | -0.02396 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.02405 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
253160 | 09JCKCEN | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.02422 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 7.55 |  |  | -0.0243 |  |  |  | 0 |  | 1 | NEW | Z1-035 |  |  | 0.8
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 1.13 |  |  | -0.0243 |  |  |  | 0 |  | 1 | CAPACITY | Z1-035 |  |  | 0.8
243362 | 05RANDOLPH1 | 138 | 205 | 77 | 0 | 4 | 3.06 |  |  | -0.02435 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253158 | 09INDI L | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.02437 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253363 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.02465 |  |  |  | 0.05 |  | 1 | MTX | AC1-212 |  |  | 1
253178 | 09MINSTR | 69 | 209 | 77 | 0 | 10 | 4.61 |  |  | -0.02465 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
AC1-212 | BATEXP_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0247
253362 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.28 |  |  | -0.02465 |  |  |  | 0 |  | 1 | CAPACITY | AC1-212 |  |  | 1
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 46.25 |  |  | -0.02543 |  |  |  | 0 |  | 1 | NEW | S71 |  |  | 0.8
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 11.56 |  |  | -0.02543 |  |  |  | 0 |  | 1 | CAPACITY | S71 |  |  | 0.8
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 25 | 0.37 |  |  | -0.02557 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253128 | 09CELINA | 69 | 209 | 77 | 0 | 4 | 2.89 |  |  | -0.02564 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.48 |  |  | -0.02595 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 627.1 |  |  | -0.02602 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 54.49 |  |  | -0.02612 |  |  |  | 0 |  | 1 | NEW | AC2-176 |  |  | 0.8
270201 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 8.14 |  |  | -0.02612 |  |  |  | 0 |  | 1 | CAPACITY | AC2-176 |  |  | 0.8
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.02646 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 19.51 |  |  | -0.02646 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 18.94 |  |  | -0.02646 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 9.4 |  |  | -0.02648 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 29.6 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 28.95 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 28.68 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.02708 |  |  |  | 0 |  | 1 | CAPACITY | Z2-115 |  |  | 0.1
247968 | Z2-115 E | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.02708 |  |  |  | 0 |  | 1 | NEW | Z2-115 |  |  | 0.1
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 125.75 |  |  | -0.02741 |  |  |  | 0 |  | 1 | NEW | U2-072 |  |  | 0.8
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 18.79 |  |  | -0.02741 |  |  |  | 0 |  | 1 | CAPACITY | U2-072 |  |  | 0.8
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 76.89 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 3 |  |  | 0.8
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 60.22 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 4 |  |  | 0.8
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 39.65 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 21 |  |  | 0.8
247903 | 05FR-22G E | 0.69 | 205 | 74 | 0 | 78.8 | 37.97 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 22 |  |  | 0.8
247900 | 05FR-11G E | 0.6 | 205 | 74 | 0 | 78.3 | 37.72 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 11 |  |  | 0.8
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 37.1 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 12 |  |  | 0.8
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 14.02 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 4 |  |  | 0.8
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 12.38 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 11 |  |  | 0.8
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 21 |  |  | 0.8
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 22 |  |  | 0.8
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 3 |  |  | 0.8
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 12 |  |  | 0.8
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 0.88 |  |  | -0.02773 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
925135 | AB2-170 E | 0.55 | 205 | 75 | 0 | 80.6 | 0 |  |  | -0.02774 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 0.1
247549 | V3-028 C | 345 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.02774 |  |  |  | 0 |  | 1 | CAPACITY | V3-028 |  |  | 0.1
925133 | AB2-170 C | 0.55 | 205 | 75 | 0 | 49.4 | 0 |  |  | -0.02774 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 0.1
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02774 |  |  |  | 0 |  | 1 | NEW | V3-028 |  |  | 0.1
907201 | AC2-103 E1 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.02807 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 0.8
907202 | AC2-103 E2 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.02807 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 0.8
241885 | AC2-103 C1 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.02807 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 0.8
241886 | AC2-103 C2 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.02807 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 0.8
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 20.96 |  |  | -0.02822 |  |  |  | 0 |  | 1 | NEW | U1-059 |  |  | 0.8
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 7.71 |  |  | -0.02822 |  |  |  | 0 |  | 1 | NEW | W1-056 |  |  | 0.8
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 4.63 |  |  | -0.02822 |  |  |  | 0 |  | 1 | CAPACITY | U1-059 |  |  | 0.8
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.16 |  |  | -0.02822 |  |  |  | 0 |  | 1 | CAPACITY | W1-056 |  |  | 0.8
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 0.8
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 0.8
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 0.8
270174 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 0.8
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.0285 |  |  |  | 0 |  | 1 | NEW | V4-010 |  |  | 0.8
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.0285 |  |  |  | 0 |  | 1 | CAPACITY | V4-010 |  |  | 0.8
247454 | 05OGG STREET | 69 | 205 | 77 | 0 | 10 | 7.16 |  |  | -0.02858 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 345.1 | 131.79 |  |  | -0.02913 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 162.6 | 62.1 |  |  | -0.02913 |  |  |  | 0.036 |  | 1 | CAPACITY | FREMONT |  |  | 1
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 159.1 | 60.76 |  |  | -0.02913 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
244357 | 05GRANGER EL | 34.5 | 205 | 2 | 0 | 3.2 | 0 |  |  | -0.02922 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 896 |  |  | -0.02952 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 22.88 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 22.8 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 22.19 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 22.07 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246235 | 05BLUFFTON | 69 | 205 | 77 | 0 | 2 | 1.43 |  |  | -0.03039 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  |  |  | -0.0305
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 101.27 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 0.19 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
918421 | AA1-056 | 345 | 202 | 58 | 0 | 46 | 0 |  |  | -0.03061 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.03064 |  |  |  | 0.036 |  | 1 | NEW | AB1-107 |  |  | 1
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 0 |  |  | -0.03066 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.03066 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 124.58 |  |  | -0.03066 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.03066 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.03066 |  |  |  | 0.036 |  | 1 | CAPACITY | OREGON |  |  | 1
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 1.46 |  |  | -0.03078 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 0.19 |  |  | -0.03167 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 8.4 |  |  | -0.0321 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.03214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.03214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.2 | 45.52 |  |  | -0.03214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 0.16 |  |  | -0.03214 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.03228 |  |  |  | 0 |  | 1 | NEW | R60 2 |  |  | 0.8
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.03228 |  |  |  | 0 |  | 1 | NEW | R60 1 |  |  | 0.8
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 84.83 | 40.87 |  |  | -0.03228 |  |  |  | 0 |  | 1 | NEW | R60 3 |  |  | 0.8
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 7.95 |  |  | -0.03228 |  |  |  | 0 |  | 1 | CAPACITY | R60 3 |  |  | 0.8
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.03228 |  |  |  | 0 |  | 1 | CAPACITY | R60 2 |  |  | 0.8
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.03228 |  |  |  | 0 |  | 1 | CAPACITY | R60 1 |  |  | 0.8
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.03304 |  |  |  | 0 |  | 1 | NEW | V1-011 |  |  | 0.8
247607 | V1-011 GEN | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.03304 |  |  |  | 0 |  | 1 | CAPACITY | V1-011 |  |  | 0.8
243017 | 05HAVILAND1 | 138 | 205 | 77 | 0 | 4.5 | 3.22 |  |  | -0.03304 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 174.1 | 83.88 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | S06 |  |  | 0.8
930042 | AB1-006 E2 | 0.69 | 205 | 74 | 0 | 96.75 | 46.61 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 0.8
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 88.2 | 42.49 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T127 4 |  |  | 0.8
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 84.8 | 40.86 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T126 2 |  |  | 0.8
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 84.7 | 40.81 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T126 3 |  |  | 0.8
247943 | T-127 E | 0.69 | 205 | 74 | 0 | 79.8 | 38.45 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T127 5 |  |  | 0.8
930041 | AB1-006 E1 | 0.69 | 205 | 74 | 0 | 77.25 | 37.22 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 0.8
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 12.48 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | S06 |  |  | 0.8
270180 | AB1-006 W1 | 0.65 | 205 | 74 | 0 | 22.75 | 10.96 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 0.8
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 9.73 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T127 5 |  |  | 0.8
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 7.37 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T126 3 |  |  | 0.8
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 7.32 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T126 2 |  |  | 0.8
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 5.68 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T127 4 |  |  | 0.8
270181 | AB1-006 W2 | 0.69 | 205 | 74 | 0 | 3.25 | 1.57 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 0.8
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 57.21 |  |  | -0.03363 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 57.17 |  |  | -0.03363 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149 | 56.9 |  |  | -0.03363 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 57.82 |  |  | -0.03405 |  |  |  | 0 |  | 1 | NEW | T131 |  |  | 0.8
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 76.1 | 36.67 |  |  | -0.03406 |  |  |  | 0 |  | 1 | NEW | R49 |  |  | 0.8
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 31.8 |  |  | -0.03405 |  |  |  | 0 |  | 1 | NEW | AC1-173 |  |  | 0.8
247521 | T131 | 0.69 | 205 | 74 | 26.1 | 30 | 14.45 |  |  | -0.03405 |  |  |  | 0 |  | 1 | CAPACITY | T131 |  |  | 0.8
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 11.03 |  |  | -0.03406 |  |  |  | 0 |  | 1 | CAPACITY | R49 |  |  | 0.8
270191 | AC1-173 C | 0.65 | 205 | 74 | 0 | 9.9 | 4.77 |  |  | -0.03405 |  |  |  | 0 |  | 1 | CAPACITY | AC1-173 |  |  | 0.8
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1186 | 1186 |  |  | -0.04004 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247529 | 05COVRT2 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.04241 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 2 |  |  | 1
247530 | 05COVRT3 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.04241 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247528 | 05COVRT1 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.04241 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.04241 |  |  |  | 0 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247531 | 05COVRT4 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.04241 |  |  |  | 0 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 114.1 | 131.2 | 50.11 |  |  | -0.04241 |  |  |  | 0 |  | 1 | CAPACITY | Covert 2 |  |  | 1
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 1014.5 |  |  | -0.04383 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.02 |  |  | -0.04384 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.04398 |  |  |  | 0.036 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.04398 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 127.17 |  |  | -0.04398 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
247604 | X1-042 | 12 | 205 | 64 | 0 | 3.8 | 2.55 |  |  | -0.04411 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.04415 |  |  |  | 0 |  | 1 | CAPACITY | Z2-113 |  |  | 0.1
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.04415 |  |  |  | 0 |  | 1 | NEW | Z2-113 |  |  | 0.1
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.3 | 0.72 |  |  | -0.04424 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 1.75 |  |  | -0.04442 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.04448 |  |  |  | 0 |  | 1 | CAPACITY | Z2-116 |  |  | 0.1
247969 | Z2-116 E | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.04448 |  |  |  | 0 |  | 1 | NEW | Z2-116 |  |  | 0.1
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 2.16 |  |  | -0.04452 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 3.33 |  |  | -0.04493 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
246476 | 05NILES | 34.5 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.04547 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246477 | 05NILES | 69 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.04547 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 3.89 |  |  | -0.04559 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.6 | 1.44 |  |  | -0.04571 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243352 | 05NTRDAM | 138 | 205 | 77 | 0 | 57.6 | 41.21 |  |  | -0.04579 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
244415 | 05OLIV SLR C | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.0481 |  |  |  | 0 |  | 1 | CAPACITY | OLIV SLR |  |  | 0.1
247967 | 05OLIV SLR E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.0481 |  |  |  | 0 |  | 1 | NEW | OLIV SLR |  |  | 0.1
243353 | 05OLIVE | 138 | 205 | 77 | 0 | 5 | 3.58 |  |  | -0.0481 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 95.86 |  |  | -0.05079 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.05079 |  |  |  | 0.036 |  | 1 | CAPACITY | X2-052 |  |  | 1
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.05079 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
MDU | PJM->LTFIMP_MDU |  |  | LTF |  | 10.1 |  |  |  | -0.0876

## GD-W193
****** PJM Winter Generator Deliverability Detailed Report ****** PJM [TARA Ver 2101.1.0.0 64-bit - Mon Jun 21 18:04:01 2021]
FG Index [All Queue] | 193 | FG ID | 188 | Monitored Facility:274750 CRETE EC ;BP 345 255112 17STJOHN 345 1 / Contingency:AEP_P1-2_#695_1681_SRT-A[Single]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 80/20 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
1557 | 105.11 | 108.16 | AC | 919.72 | 591.42 | 0 | 105.02 | 20.42 | 1636.58 | 1684.1 | 0.008493 | 0 | 11936 | 0 | 8098.2 | 0.08582 | 3837.86 | 3837.86 | 0 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | FRMP | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited? | Ramping Limit
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.9308 | 1 | CAPACITY |  |  |  | 1
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.8664 | 1 | CAPACITY |  |  |  | 1
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.8064 | 1 | CAPACITY |  |  |  | 1
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 28.72 | 75.2 | EightyTwenty | 0.5003 | 23.2543 | 37.6223 |  | 0.0692 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 1183 | 1183 | EightyTwenty | 0.15472 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 1154 | 1154 | EightyTwenty | 0.15427 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 131.6 | 63.4 | 105.28 | EightyTwenty | 0.14817 | 6.2046 | 19.499 |  | 0 | 0.7506 | 1 | NEW | O22 2 |  |  | 0.8
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 114.9 | 55.36 | 91.92 | EightyTwenty | 0.14817 | 5.4172 | 17.0246 |  | 0 | 0.7506 | 1 | NEW | O22 1 |  |  | 0.8
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 16.91 | 28.08 | EightyTwenty | 0.14817 | 1.6549 | 5.2007 |  | 0 | 0.7506 | 1 | CAPACITY | O22 2 |  |  | 0.8
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 8.86 | 14.72 | EightyTwenty | 0.14817 | 0.8675 | 2.7263 |  | 0 | 0.7506 | 1 | CAPACITY | O22 1 |  |  | 0.8
274661 | LASCO STA;2U | 25 | 222 | 49 | 132 | 1134.8 | 1134.8 | 1134.8 | EightyTwenty | 0.14585 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274660 | LASCO STA;1U | 25 | 222 | 49 | 135 | 1131.2 | 1131.2 | 1131.2 | EightyTwenty | 0.14584 |  |  |  | 0 | 0.7506 | 1 | CAPACITY |  |  |  | 1
274687 | WILL CNTY;4U | 20 | 222 | 15 | 49.4 | 510 | 510 | 510 | EightyTwenty | 0.14193 |  |  |  | 0 | 0.7506 | 1 | CAPACITY | WILL4 |  |  | 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 69.62 | 182.3 | EightyTwenty | 0.14051 | 15.8321 | 25.6143 |  | 0.036 | 0.7236 | 1 | CAPACITY | Kendall 2 |  |  | 1
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 69.62 | 182.3 | EightyTwenty | 0.14051 | 15.8321 | 25.6143 |  | 0.036 | 0.6976 | 1 | CAPACITY | Kendall 1 |  |  | 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 46.55 | 121.9 | EightyTwenty | 0.14051 | 10.5866 | 17.1277 |  | 0 | 0.7236 | 1 | CAPACITY | Kendall 2 |  |  | 1
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 46.55 | 121.9 | EightyTwenty | 0.14051 | 10.5866 | 17.1277 |  | 0 | 0.6976 | 1 | CAPACITY | Kendall 1 |  |  | 1
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 73.43 | 121.92 | EightyTwenty | 0.13923 | 6.7518 | 21.2185 |  | 0 | 0.6976 | 1 | NEW | P10 |  |  | 0.8
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 57.82 | 96 | EightyTwenty | 0.13923 | 5.3163 | 16.7075 |  | 0 | 0.6976 | 1 | NEW | N15 |  |  | 0.8
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 13.2 | 21.92 | EightyTwenty | 0.13923 | 1.2139 | 3.8149 |  | 0 | 0.6976 | 1 | CAPACITY | N15 |  |  | 0.8
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 4.91 | 8.16 | EightyTwenty | 0.13923 | 0.4519 | 1.4201 |  | 0 | 0.6976 | 1 | CAPACITY | P10 |  |  | 0.8
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 289.95 | 518 | EightyTwenty | 0.13919 | 31.742 | 72.1002 |  | 0.1042 | 0.6249 | 1 | CAPACITY | Joliet8 |  |  | 1
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 293.58 | 518 | EightyTwenty | 0.1391 | 31.2172 | 72.0541 |  | 0.1042 | 0.5598 | 1 | CAPACITY | Joliet7 |  |  | 1
276642 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 213.08 | 557.95 | EightyTwenty | 0.13774 | 47.5026 | 76.8533 |  | 0 | 0.5396 | 1 | CAPACITY | AC1-204 |  |  | 1
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.5023 | 1 | CAPACITY |  |  |  | 1
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.4675 | 1 | CAPACITY |  |  |  | 1
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.4352 | 1 | CAPACITY |  |  |  | 1
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.405 | 1 | CAPACITY |  |  |  | 1
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13774 | 12.7706 | 20.6613 |  | 0.0692 | 0.377 | 1 | CAPACITY |  |  |  | 1
276640 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 213.08 | 557.95 | EightyTwenty | 0.13748 | 47.4136 | 76.7093 |  | 0.036 | 0.5396 | 1 | CAPACITY | AC1-204 |  |  | 1
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.3509 | 1 | CAPACITY |  |  |  | 1
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.3266 | 1 | CAPACITY |  |  |  | 1
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.304 | 1 | CAPACITY |  |  |  | 1
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 0 | 150 | 57.29 | 150 | EightyTwenty | 0.13748 | 12.7467 | 20.6226 |  | 0.0692 | 0.283 | 1 | CAPACITY |  |  |  | 1
276660 | AB1-122 CT2 | 22.5 | 222 | 58 | 0 | 575 | 219.6 | 575 | EightyTwenty | 0.13655 | 48.5314 | 78.5176 |  | 0 | 0.2728 | 1 | CAPACITY | AB1-122 |  |  | 1
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 167 | 63.78 | 167 | EightyTwenty | 0.13132 | 13.5553 | 21.9307 |  | 0.0692 | 0.2539 | 1 | CAPACITY |  |  |  | 1
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 167 | 63.78 | 167 | EightyTwenty | 0.13132 | 13.5553 | 21.9307 |  | 0.0692 | 0.2364 | 1 | CAPACITY |  |  |  | 1
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 58.05 | 152 | EightyTwenty | 0.13111 | 12.3181 | 19.9293 |  | 0.0692 | 0.22 | 1 | CAPACITY |  |  |  | 1
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 58.05 | 152 | EightyTwenty | 0.13111 | 12.3181 | 19.9293 |  | 0.0692 | 0.2048 | 1 | CAPACITY |  |  |  | 1
276658 | AB1-122 CT1 | 22.5 | 222 | 58 | 0 | 575 | 219.6 | 575 | EightyTwenty | 0.12575 | 44.691 | 72.3043 |  | 0.036 | 0.2728 | 1 | CAPACITY | AB1-122 |  |  | 1
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 32.9 |  | 32.9 | CLTF | 0.12226 | 4.0223 | 4.0223 | 0.2794
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  | 158.9 | CLTF | 0.08095 | 12.8624 | 12.8624 | 1.3495
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1063 |  | 1063 | LTF/CBM | 0.04958 | 52.7027 | 52.7027 | 9.028
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.0209 | 1.1556 | 1.1556 | -0.4697
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 1348 |  | 1348 | LTF/CBM | 0.01933 | 26.0567 | 26.0567 | 11.4485
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  | 175 | CLTF | 0.01763 | 3.086 | 3.086 | 1.4863
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.01298 | 0.7225 | 0.7225 | -0.4726
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.3 |  | 173.3 | CLTF | 0.01226 | 2.1237 | 2.1237 | -1.4714
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.01053 | 0.6082 | 0.6082 | -0.4905
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.0093 | 0.3256 | 0.3256 | -0.2973
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  | 140 | CLTF | 0.00679 | 0.9508 | 0.9508 | 1.189
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 18 |  | 18 | LTF/CBM | 0.00343 | 0.0617 | 0.0617 | 0.1529
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00294 | 0.147 | 0.147 | -0.4251
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00275 | 0.1367 | 0.1367 | -0.4221
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00111 | 0.0607 | 0.0607 | -0.4637
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 44.4 | 51 | 19.48 |  |  | 0.1311 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 113.7 | 43.42 |  |  | 0.13062 |  |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | 0.13058 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.13058 |  |  |  | 0.0975 |  | 1 | MTX | Z1-106 |  |  | 1
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.13058 |  |  |  | 0.05 |  | 1 | MTX | Z1-106 |  |  | 1
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 244.23 |  |  | 0.13047 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK7 |  |  | 1
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 263.89 |  |  | 0.13012 |  |  |  | 0.1042 |  | 1 | CAPACITY | WAUK8 |  |  | 1
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 38.5 |  |  | 0.13012 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 46.21 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 45.87 |  |  | 0.12989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
276618 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 6.71 |  |  | 0.12969 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 160.3 | 184.3 | 70.39 |  |  | 0.12961 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 158.6 | 182.3 | 69.62 |  |  | 0.12961 |  |  |  | 0.036 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 46.55 |  |  | 0.12961 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 4 |  |  | 1
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 46.55 |  |  | 0.12961 |  |  |  | 0 |  | 1 | CAPACITY | Kendall 3 |  |  | 1
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 88.4 | 101.6 | 38.8 |  |  | 0.12944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 87.5 | 100.6 | 38.42 |  |  | 0.12944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 24 | 27.6 | 10.54 |  |  | 0.12944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 90.5 | 104 | 39.72 |  |  | 0.12943 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.12921 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 63.01 |  |  | 0.12921 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 63.01 |  |  | 0.12921 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 80.3 | 30.67 |  |  | 0.12904 |  |  |  | 0.036 |  | 1 | CAPACITY | EQUISTAR MORRIS |  |  | 1
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.12854 |  |  |  | 0.0975 |  | 1 | MTX | Z1-108 |  |  | 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 10.1 | 6.78 |  |  | 0.12838 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 209.23 |  |  | 0.12706 |  |  |  | 0.1042 |  | 1 | CAPACITY | Joliet9 |  |  | 1
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 77.09 |  |  | 0.12698 |  |  |  | 0 |  | 1 | NEW | O50 |  |  | 0.8
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.12698 |  |  |  | 0 |  | 1 | CAPACITY | O50 |  |  | 0.8
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.12657 |  |  |  | 0.0975 |  | 1 | MTX | Z1-107 |  |  | 1
276617 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 5.88 |  |  | 0.12657 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
293519 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.12651 |  |  |  | 0 |  | 1 | NEW | S36 |  |  | 0.8
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 67.45 |  |  | 0.12651 |  |  |  | 0 |  | 1 | NEW | S37 |  |  | 0.8
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.12651 |  |  |  | 0 |  | 1 | CAPACITY | S36 |  |  | 0.8
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 16.86 |  |  | 0.12651 |  |  |  | 0 |  | 1 | CAPACITY | S37 |  |  | 0.8
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.12586 |  |  |  | 0.0975 |  | 1 | MTX | AA2-123 |  |  | 1
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 197.5 | 95.16 |  |  | 0.12518 |  |  |  | 0 |  | 1 | NEW | Q57 |  |  | 0.8
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 19.27 |  |  | 0.12518 |  |  |  | 0 |  | 1 | CAPACITY | Q57 |  |  | 0.8
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 1.46 |  |  | 0.12335 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 1.03 |  |  | 0.12335 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
272363 | ESS H440 ; R | 138 | 222 | 2 | 0 | 22 | 0 |  |  | 0.12308 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 42.21 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | P26 |  |  | 0.8
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 56 | 26.98 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | Z1-073 |  |  | 0.8
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 22.6 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | WestBrooklyn |  |  | 0.8
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 10.98 |  |  | 0.12294 |  |  |  | 0 |  | 1 | NEW | Sublette |  |  | 0.8
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 10.55 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | P26 |  |  | 0.8
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 14.4 | 6.94 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | Z1-073 |  |  | 0.8
276602 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 3.42 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | WestBrooklyn |  |  | 0.8
276603 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 1.54 |  |  | 0.12294 |  |  |  | 0 |  | 1 | CAPACITY | Sublette |  |  | 0.8
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 4.3 |  |  | 0.12209 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 156.6 | 180 | 68.74 |  |  | 0.12193 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 155.8 | 179.1 | 68.4 |  |  | 0.12193 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 154.7 | 177.8 | 67.9 |  |  | 0.12193 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 62.88 |  |  | 0.12155 |  |  |  | 0 |  | 1 | NEW | AA1-018 |  |  | 0.8
270839 | OTTER CRK; R | 345 | 222 | 74 | 0 | 19.5 | 9.4 |  |  | 0.12155 |  |  |  | 0 |  | 1 | CAPACITY | AA1-018 |  |  | 0.8
274656 | BYRON ;1U | 25 | 222 | 45 | 648.1 | 1168.5 | 1168.5 |  |  | 0.12122 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274657 | BYRON ;2U | 25 | 222 | 45 | 658.5 | 1141.5 | 1141.5 |  |  | 0.12122 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.3 | 6.25 |  |  | 0.12033 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80.6 | 38.83 |  |  | 0.12 |  |  |  | 0 |  | 1 | NEW | P46 |  |  | 0.8
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 9.35 |  |  | 0.12 |  |  |  | 0 |  | 1 | CAPACITY | P46 |  |  | 0.8
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.11924 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 769 |  |  | 0.11908 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.11732 |  |  |  | 0 |  | 1 | NEW | P36 2 |  |  | 0.8
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 104.8 | 50.49 |  |  | 0.11732 |  |  |  | 0 |  | 1 | NEW | P36 1 |  |  | 0.8
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 32.5 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 32.42 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 32.12 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 32.04 |  |  | 0.11732 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.11732 |  |  |  | 0 |  | 1 | CAPACITY | P36 1 |  |  | 0.8
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 7.32 |  |  | 0.11732 |  |  |  | 0 |  | 1 | CAPACITY | P36 2 |  |  | 0.8
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 29.41 |  |  | 0.11505 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11489 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11489 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 64.77 |  |  | 0.11475 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 64.28 |  |  | 0.11475 |  |  |  | 0.036 |  | 1 | CAPACITY | NELSON |  |  | 1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 47.32 |  |  | 0.11475 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 46.9 |  |  | 0.11475 |  |  |  | 0 |  | 1 | CAPACITY | NELSON |  |  | 1
293516 | O-009 E | 0.69 | 222 | 74 | 0 | 169.6 | 81.71 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O09 |  |  | 0.8
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 42.26 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O29 1 |  |  | 0.8
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 23.17 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O29 2 |  |  | 0.8
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 21.3 |  |  | 0.11329 |  |  |  | 0 |  | 1 | NEW | O29 3 |  |  | 0.8
274881 | WALNUT RG;1U | 0.69 | 222 | 74 | 0 | 42.4 | 20.43 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O09 |  |  | 0.8
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 10.55 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O29 1 |  |  | 0.8
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 5.78 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O29 2 |  |  | 0.8
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 5.35 |  |  | 0.11329 |  |  |  | 0 |  | 1 | CAPACITY | O29 3 |  |  | 0.8
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 20.47 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 20.32 |  |  | 0.11192 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 28.52 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | O35 |  |  | 0.8
927209 | AC1-214 E2 | 0.69 | 222 | 74 | 0 | 55.15 | 26.57 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | AC1-214 2 |  |  | 0.8
916212 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 44.75 | 21.56 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | Z1-072 |  |  | 0.8
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 14.8 | 7.13 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | O35 |  |  | 0.8
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 9.7 | 4.67 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | Z1-072 |  |  | 0.8
276645 | AC1-214 C1 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 1 |  |  | 0.8
276646 | AC1-214 C2 | 0.69 | 222 | 74 | 0 | 8.5 | 4.09 |  |  | 0.11006 |  |  |  | 0 |  | 1 | CAPACITY | AC1-214 2 |  |  | 0.8
927208 | AC1-214 E1 | 0.69 | 222 | 74 | 0 | 5.25 | 2.53 |  |  | 0.11006 |  |  |  | 0 |  | 1 | NEW | AC1-214 1 |  |  | 0.8
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.10919 |  |  |  | 0 |  | 1 | NEW | P11 1 |  |  | 0.8
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 38.54 |  |  | 0.10919 |  |  |  | 0 |  | 1 | NEW | P11 2 |  |  | 0.8
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.10919 |  |  |  | 0 |  | 1 | CAPACITY | P11 1 |  |  | 0.8
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 9.64 |  |  | 0.10919 |  |  |  | 0 |  | 1 | CAPACITY | P11 2 |  |  | 0.8
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 137 | 66.01 |  |  | 0.10762 |  |  |  | 0 |  | 1 | NEW | L05_CE22 |  |  | 0.8
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 13 | 6.26 |  |  | 0.10762 |  |  |  | 0 |  | 1 | CAPACITY | L05_CE22 |  |  | 0.8
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 68.74 |  |  | 0.10647 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.10647 |  |  |  | 0.036 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 61.1 |  |  | 0.10647 |  |  |  | 0 |  | 1 | CAPACITY | CORDOVA |  |  | 1
274663 | QUAD CITI;2U | 18 | 222 | 48 | 132 | 911.2 | 911.2 |  |  | 0.10644 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274662 | QUAD CITI;1U | 18 | 222 | 48 | 132 | 909.5 | 909.5 |  |  | 0.10637 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 18.94 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 18.87 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 18.83 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 18.79 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 18.71 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 18.67 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 18.64 |  |  | 0.10514 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.09688 |  |  |  | 0 |  | 1 | NEW | O51 1 |  |  | 0.8
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 127.5 | 61.43 |  |  | 0.09688 |  |  |  | 0 |  | 1 | NEW | O51 2 |  |  | 0.8
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.09688 |  |  |  | 0 |  | 1 | CAPACITY | O51 2 |  |  | 0.8
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 10.84 |  |  | 0.09688 |  |  |  | 0 |  | 1 | CAPACITY | O51 1 |  |  | 0.8
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 83.83 |  |  | 0.09145 |  |  |  | 0 |  | 1 | NEW | Z2-087 |  |  | 0.8
924049 | AB2-047 E2 | 0.69 | 222 | 74 | 0 | 109.6 | 52.81 |  |  | 0.09145 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 0.8
924048 | AB2-047 E1 | 0.69 | 222 | 74 | 0 | 107.9 | 51.99 |  |  | 0.09145 |  |  |  | 0 |  | 1 | NEW | AB2-047 |  |  | 0.8
270681 | BRIGHTSTK; R | 345 | 222 | 74 | 0 | 26 | 12.53 |  |  | 0.09145 |  |  |  | 0 |  | 1 | CAPACITY | Z2-087 |  |  | 0.8
276655 | AB2-047 C1 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.09145 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 0.8
276656 | AB2-047 C2 | 0.69 | 222 | 74 | 0 | 16.25 | 7.83 |  |  | 0.09145 |  |  |  | 0 |  | 1 | CAPACITY | AB2-047 |  |  | 0.8
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0.41 |  |  | 0.0897 |  |  |  | 0 |  | 1 | NEW | X3-005 |  |  | 0.1
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 0.25 |  |  | 0.0897 |  |  |  | 0 |  | 1 | CAPACITY | X3-005 |  |  | 0.1
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 163.2 | 78.63 |  |  | 0.08104 |  |  |  | 0 |  | 1 | NEW | S27 |  |  | 0.8
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 162.2 | 78.15 |  |  | 0.08104 |  |  |  | 0 |  | 1 | NEW | S28 |  |  | 0.8
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 17.25 |  |  | 0.08104 |  |  |  | 0 |  | 1 | CAPACITY | S28 |  |  | 0.8
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 16.77 |  |  | 0.08104 |  |  |  | 0 |  | 1 | CAPACITY | S27 |  |  | 0.8
276174 | W4-005 E | 0.69 | 222 | 74 | 0 | 260.4 | 125.46 |  |  | 0.06741 |  |  |  | 0 |  | 1 | NEW | W4-005 |  |  | 0.8
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 21.97 |  |  | 0.06741 |  |  |  | 0 |  | 1 | CAPACITY | W4-005 |  |  | 0.8
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 89.13 |  |  | 0.06612 |  |  |  | 0 |  | 1 | NEW | X2-022 |  |  | 0.8
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 31.32 |  |  | 0.06612 |  |  |  | 0.1042 |  | 1 | NEW | W2-048 |  |  | 0.8
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 61.87 |  |  | 0.06586 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.05944 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 556 |  |  | 0.05942 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 62.67 |  |  | 0.0536 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | 0.0205
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | 0.0205
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0025
342442 | 2W GLASGOW | 69 | 320 | 77 | 0 | 1 | 0.67 |  |  | -0.00289 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
939134 | AE1-143 C | 0.64 | 320 | 75 | 0 | 64.14 | 4.68 |  |  | -0.00755 |  |  |  | 0 |  | 1 | CAPACITY | AE1-143 |  |  | 0.1
939135 | AE1-143 E | 0.64 | 320 | 75 | 0 | 31.86 | 2.33 |  |  | -0.00755 |  |  |  | 0 |  | 1 | NEW | AE1-143 |  |  | 0.1
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 85.93 |  |  | -0.00846 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 44.3 |  |  | -0.00845 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
341329 | 2COLESBURG | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | -0.00859 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 682 |  |  |  | -0.009
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 38.84 |  |  | -0.00936 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
342070 | 2PINE GROVE | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | -0.01011 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
936570 | AD2-072_C | 0.6 | 320 | 75 | 0 | 63.75 | 0 |  |  | -0.01142 |  |  |  | 0 |  | 1 | CAPACITY | AD2-072 |  |  | 0.1
936576 | AD2-072_E | 0.6 | 320 | 75 | 0 | 31.25 | 0 |  |  | -0.01142 |  |  |  | 0 |  | 1 | NEW | AD2-072 |  |  | 0.1
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 94.5 |  |  |  | -0.0117
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 59.6 |  |  |  | -0.0119
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1300 |  |  | -0.012 |  |  |  | 0 |  | 1 | CAPACITY | RKG2 |  |  | 1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1356 |  |  | -0.012 |  |  |  | 0 |  | 1 | CAPACITY | RKG1 |  |  | 1
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | -0.01257 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 52.58 | 20.08 |  |  | -0.01257 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 52.58 | 20.08 |  |  | -0.01257 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 93.75 |  |  | -0.01349 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG2 |  |  | 1
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 125.1 | 93.15 |  |  | -0.01349 |  |  |  | 0.1042 |  | 1 | CAPACITY | CRG1 |  |  | 1
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 78.63 |  |  | -0.01349 |  |  |  | 0 |  | 1 | CAPACITY | CRG2 |  |  | 1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 104.7 | 77.96 |  |  | -0.01349 |  |  |  | 0 |  | 1 | CAPACITY | CRG1 |  |  | 1
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 610.3 |  |  | -0.01349 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 42.01 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 108.1 | 41.28 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 106.7 | 40.75 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 27.88 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 70.9 | 27.08 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 70.6 | 26.96 |  |  | -0.01364 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316222 | AC1-221 C | 0.6 | 345 | 75 | 0 | 51.2 | 7.68 |  |  | -0.0137 |  |  |  | 0 |  | 1 | CAPACITY | AC1-221 |  |  | 0.1
316283 | AC2-100 C | 0.57 | 345 | 75 | 0 | 45.6 | 6.84 |  |  | -0.0137 |  |  |  | 0 |  | 1 | CAPACITY | AC2-100 |  |  | 0.1
932763 | AC2-100 E | 0.57 | 345 | 75 | 0 | 16.4 | 2.46 |  |  | -0.0137 |  |  |  | 0 |  | 1 | NEW | AC2-100 |  |  | 0.1
927255 | AC1-221 E | 0.6 | 345 | 75 | 0 | 14.6 | 2.19 |  |  | -0.0137 |  |  |  | 0 |  | 1 | NEW | AC1-221 |  |  | 0.1
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | -0.01382 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 29.02 |  |  | -0.01382 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315131 | 1EDGECMA | 13.8 | 345 | 11 | 7.5 | 58 | 0 |  |  | -0.01408 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 9.9 |  |  | -0.01409 |  |  |  | 0 |  | 1 | CAPACITY | AB2-059 |  |  | 0.1
316049 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 8.4 |  |  | -0.01409 |  |  |  | 0 |  | 1 | CAPACITY | AB1-081 |  |  | 0.1
316263 | AC1-034 C | 0.55 | 345 | 75 | 0 | 42.75 | 6.41 |  |  | -0.01409 |  |  |  | 0 |  | 1 | CAPACITY | AC1-034 |  |  | 0.1
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 5.1 |  |  | -0.01409 |  |  |  | 0 |  | 1 | NEW | AB2-059 |  |  | 0.1
925595 | AC1-034 E | 0.55 | 345 | 75 | 0 | 32.25 | 4.84 |  |  | -0.01409 |  |  |  | 0 |  | 1 | NEW | AC1-034 |  |  | 0.1
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01409 |  |  |  | 0 |  | 1 | NEW | AB1-081 |  |  | 0.1
341200 | 2BROMLEYEK | 69 | 320 | 77 | 0 | 2 | 1.35 |  |  | -0.01413 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | -0.01426 |  |  |  | 0 |  | 1 | CAPACITY | Z2-088 |  |  | 0.1
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | -0.01426 |  |  |  | 0 |  | 1 | NEW | Z2-088 |  |  | 0.1
316319 | Z2-044 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | -0.01427 |  |  |  | 0 |  | 1 | CAPACITY | Z2-044 |  |  | 0.1
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0.54 |  |  | -0.01427 |  |  |  | 0 |  | 1 | NEW | Z2-044 |  |  | 0.1
316005 | AA1-067 C | 230 | 345 | 75 | 0 | 10.5 | 1.58 |  |  | -0.01445 |  |  |  | 0 |  | 1 | CAPACITY | AA1-067 |  |  | 0.1
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0.68 |  |  | -0.01445 |  |  |  | 0 |  | 1 | NEW | AA1-067 |  |  | 0.1
244012 | 05PINNACLE | 4 | 205 | 75 | 0 | 11 | 0.8 |  |  | -0.01455 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
316327 | AA2-057 C | 0.63 | 345 | 75 | 0 | 50 | 7.5 |  |  | -0.01457 |  |  |  | 0 |  | 1 | CAPACITY | AA2-057 |  |  | 0.1
919710 | AA2-057 E | 0.63 | 345 | 75 | 0 | 24.9 | 3.73 |  |  | -0.01457 |  |  |  | 0 |  | 1 | NEW | AA2-057 |  |  | 0.1
316210 | AC1-098 C | 0.6 | 345 | 75 | 0 | 37.6 | 5.64 |  |  | -0.01467 |  |  |  | 0 |  | 1 | CAPACITY | AC1-098 |  |  | 0.1
926206 | AC1-098 E | 0.6 | 345 | 75 | 0 | 22.4 | 3.36 |  |  | -0.01467 |  |  |  | 0 |  | 1 | NEW | AC1-098 |  |  | 0.1
316212 | AC1-099 C | 0.6 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | -0.01467 |  |  |  | 0 |  | 1 | CAPACITY | AC1-099 |  |  | 0.1
926214 | AC1-099 E | 0.6 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | -0.01467 |  |  |  | 0 |  | 1 | NEW | AC1-099 |  |  | 0.1
316274 | AC1-208 C | 0.38 | 345 | 75 | 0 | 55.4 | 8.31 |  |  | -0.01473 |  |  |  | 0 |  | 1 | CAPACITY | AC1-208 |  |  | 0.1
927146 | AC1-208 E | 0.38 | 345 | 75 | 0 | 24.5 | 0 |  |  | -0.01473 |  |  |  | 0 |  | 1 | NEW | AC1-208 |  |  | 0.1
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 15 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 42 |  |  | -0.01486 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
TILTON | PJM->LTFIMP_TILTON |  |  | LTF |  | 63 |  |  |  | -0.015
316174 | AB2-169_C | 0.63 | 345 | 75 | 0 | 39 | 5.85 |  |  | -0.01498 |  |  |  | 0 |  | 1 | CAPACITY | AB2-169 |  |  | 0.1
925122 | AB2-169 E | 0.63 | 345 | 75 | 0 | 35 | 5.25 |  |  | -0.01498 |  |  |  | 0 |  | 1 | NEW | AB2-169 |  |  | 0.1
316248 | AF1-058 C | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01497 |  |  |  | 0 |  | 1 | CAPACITY | AF1-058 |  |  | 0.1
943902 | AF1-058 E | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01497 |  |  |  | 0 |  | 1 | NEW | AF1-058 |  |  | 0.1
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 45.6 |  |  | -0.01499 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 6.68 |  |  | -0.01501 |  |  |  | 0 |  | 1 | CAPACITY | AC1-054 |  |  | 0.1
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 3.08 |  |  | -0.01501 |  |  |  | 0 |  | 1 | NEW | AC1-054 |  |  | 0.1
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 5.18 |  |  | -0.01503 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 0.1
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 2.54 |  |  | -0.01503 |  |  |  | 0 |  | 1 | NEW | AC1-105 |  |  | 0.1
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 74.1 | 55.58 |  |  | -0.01505 |  |  |  | 0.036 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 45.9 | 34.43 |  |  | -0.01505 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
270183 | AB2-010_C | 138 | 205 | 75 | 0 | 10 | 0.73 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 0.1
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 34.7 | 26.03 |  |  | -0.01505 |  |  |  | 0 |  | 1 | CAPACITY | ROSEMARY |  |  | 1
270182 | AB2-011_C | 138 | 205 | 75 | 0 | 8 | 0.58 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 0.1
923772 | AB2-011_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-011 |  |  | 0.1
923762 | AB2-010_E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.01506 |  |  |  | 0 |  | 1 | NEW | AB2-010 |  |  | 0.1
316003 | AC1-222 C | 0.6 | 345 | 75 | 0 | 38.8 | 5.82 |  |  | -0.01508 |  |  |  | 0 |  | 1 | CAPACITY | AC1-222 |  |  | 0.1
927264 | AC1-222 E | 0.6 | 345 | 75 | 0 | 25.9 | 3.88 |  |  | -0.01508 |  |  |  | 0 |  | 1 | NEW | AC1-222 |  |  | 0.1
316317 | KELFORD C | 115 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01511 |  |  |  | 0 |  | 1 | CAPACITY | Z2-043 |  |  | 0.1
917332 | KELFORD E | 115 | 345 | 75 | 0 | 7 | 1.05 |  |  | -0.01511 |  |  |  | 0 |  | 1 | NEW | Z2-043 |  |  | 0.1
316011 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 12.6 |  |  | -0.01519 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 0.1
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | -0.01519 |  |  |  | 0 |  | 1 | NEW | AB1-132 |  |  | 0.1
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 110 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 50.3 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 48 |  |  | -0.01519 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 8.22 |  |  | -0.01521 |  |  |  | 0 |  | 1 | CAPACITY | AA2-053 |  |  | 0.1
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 3.38 |  |  | -0.01521 |  |  |  | 0 |  | 1 | NEW | AA2-053 |  |  | 0.1
316238 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 0.1
316239 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 0.1
316237 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 0.1
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-078 |  |  | 0.1
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-077 |  |  | 0.1
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01523 |  |  |  | 0 |  | 1 | NEW | AB2-079 |  |  | 0.1
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.01525 |  |  |  | 0 |  | 1 | NEW | AB2-043 |  |  | 0.1
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 2.84 |  |  | -0.01525 |  |  |  | 0 |  | 1 | CAPACITY | AB2-043 |  |  | 0.1
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 8.16 |  |  | -0.01527 |  |  |  | 0 |  | 1 | CAPACITY | AB2-060 |  |  | 0.1
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 3.84 |  |  | -0.01527 |  |  |  | 0 |  | 1 | NEW | AB2-060 |  |  | 0.1
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 37.51 |  |  | -0.01529 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
316243 | AE2-151 C | 115 | 345 | 75 | 0 | 6.5 | 0.98 |  |  | -0.01528 |  |  |  | 0 |  | 1 | CAPACITY | AE2-151 |  |  | 0.1
941542 | AE2-151 E | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | -0.01528 |  |  |  | 0 |  | 1 | NEW | AE2-151 |  |  | 0.1
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 67 | 10.05 |  |  | -0.01533 |  |  |  | 0 |  | 1 | CAPACITY | AA1-065 |  |  | 0.1
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01533 |  |  |  | 0 |  | 1 | NEW | AA1-065 |  |  | 0.1
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 0.52 |  |  | -0.01534 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 0.1
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0.22 |  |  | -0.01534 |  |  |  | 0 |  | 1 | NEW | AB2-099 |  |  | 0.1
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 7.64 |  |  | -0.01535 |  |  |  | 0 |  | 1 | CAPACITY | AA1-063A |  |  | 0.1
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01535 |  |  |  | 0 |  | 1 | NEW | AA1-063A |  |  | 0.1
923994 | AB2-040_E | 0.6 | 345 | 75 | 0 | 69.51 | 10.43 |  |  | -0.01538 |  |  |  | 0 |  | 1 | NEW | AB2-040 |  |  | 0.1
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 6.06 |  |  | -0.01538 |  |  |  | 0 |  | 1 | CAPACITY | AB1-173 |  |  | 0.1
316181 | AB2-040 GEN | 0.6 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01538 |  |  |  | 0 |  | 1 | CAPACITY | AB2-040 |  |  | 0.1
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | -0.01538 |  |  |  | 0 |  | 1 | NEW | AB1-173 |  |  | 0.1
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 6.3 |  |  | -0.01542 |  |  |  | 0 |  | 1 | CAPACITY | AB2-174 |  |  | 0.1
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 5.7 |  |  | -0.01542 |  |  |  | 0 |  | 1 | NEW | AB2-174 |  |  | 0.1
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 11 |  |  | -0.01545 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 5.74 |  |  | -0.01547 |  |  |  | 0 |  | 1 | CAPACITY | AC1-075 |  |  | 0.1
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 3.26 |  |  | -0.01547 |  |  |  | 0 |  | 1 | NEW | AC1-075 |  |  | 0.1
316205 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 1.92 |  |  | -0.01547 |  |  |  | 0 |  | 1 | CAPACITY | AC1-080 |  |  | 0.1
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 1.08 |  |  | -0.01547 |  |  |  | 0 |  | 1 | NEW | AC1-080 |  |  | 0.1
316318 | V4-068 C | 115 | 345 | 75 | 0 | 3.2 | 0.48 |  |  | -0.0155 |  |  |  | 0 |  | 1 | CAPACITY | V4-068 |  |  | 0.1
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.0155 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0.27 |  |  | -0.0155 |  |  |  | 0 |  | 1 | NEW | V4-068 |  |  | 0.1
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.2 | 441.2 |  |  | -0.01553 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 437.1 |  |  | -0.01553 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 1.39 |  |  | -0.01558 |  |  |  | 0 |  | 1 | NEW | AC1-036 |  |  | 0.1
316034 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 1.29 |  |  | -0.01558 |  |  |  | 0 |  | 1 | CAPACITY | AC1-036 |  |  | 0.1
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | -0.0156 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 0.1
270130 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0.56 |  |  | -0.0156 |  |  |  | 0 |  | 1 | NEW | AC1-117 |  |  | 0.1
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | -0.01563 |  |  |  | 0 |  | 1 | NEW | AA2-088 |  |  | 0.1
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | -0.01563 |  |  |  | 0 |  | 1 | CAPACITY | AA2-088 |  |  | 0.1
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | -0.01569 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 1 |  |  | 0.1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 5.03 |  |  | -0.01569 |  |  |  | 0 |  | 1 | CAPACITY | AB2-100 2 |  |  | 0.1
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | -0.01569 |  |  |  | 0 |  | 1 | NEW | AB2-100 1 |  |  | 0.1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 2.47 |  |  | -0.01569 |  |  |  | 0 |  | 1 | NEW | AB2-100 2 |  |  | 0.1
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 8.4 |  |  | -0.01573 |  |  |  | 0 |  | 1 | CAPACITY | AA2-178 |  |  | 0.1
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 3.6 |  |  | -0.01573 |  |  |  | 0 |  | 1 | NEW | AA2-178 |  |  | 0.1
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 422.31 |  |  | -0.01578 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | -0.01578 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | -0.01578 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 203.28 |  |  | -0.01578 |  |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY |  |  | 1
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 15.7 | 10.53 |  |  | -0.01586 |  |  |  | 0.1097 |  | 1 | CAPACITY | AMELIA LF_1-A |  |  | 1
313853 | 3PONTONDP | 115 | 345 | 65 | 0 | 4 | 0 |  |  | -0.01586 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53 | 53 |  |  | -0.01585 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 448.57 |  |  | -0.01587 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | -0.01587 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | -0.01587 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-086 |  |  | 1
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 258.04 |  |  | -0.01587 |  |  |  | 0 |  | 1 | CAPACITY | Z1-086 |  |  | 1
314541 | 3WATKINS | 115 | 345 | 75 | 0 | 4 | 0.6 |  |  | -0.01587 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 7.5 |  |  | -0.01591 |  |  |  | 0 |  | 1 | CAPACITY | AB2-015 |  |  | 0.1
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 6.15 |  |  | -0.01591 |  |  |  | 0 |  | 1 | NEW | AB2-015 |  |  | 0.1
961092 | AF2-400 E | 115 | 345 | 75 | 0 | 4.43 | 0.66 |  |  | -0.01591 |  |  |  | 0 |  | 1 | NEW | af2-400 |  |  | 0.1
316300 | AF2-400 C | 115 | 345 | 75 | 0 | 2.71 | 0.41 |  |  | -0.01591 |  |  |  | 0 |  | 1 | CAPACITY | AF2-400 |  |  | 0.1
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 4.44 |  |  | -0.01593 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
316074 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 1.35 |  |  | -0.01596 |  |  |  | 0 |  | 1 | CAPACITY | AD1-157 |  |  | 0.1
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01596 |  |  |  | 0 |  | 1 | NEW | AD1-157 |  |  | 0.1
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.01598 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 52.4 |  |  | -0.01604 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 107.08 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 105.41 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 67.13 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 41.06 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 39.39 |  |  | -0.01605 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 258.69 |  |  | -0.01606 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 0.8
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | -0.01606 |  |  |  | 0 |  | 1 | NEW | Z1-036 |  |  | 0.8
251298 | 08CRITDN | 69 | 212 | 77 | 0 | 2.7 | 1.9 |  |  | -0.01606 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.2 | 27.3 |  |  | -0.01608 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.0161 |  |  |  | 0 |  | 1 | NEW | AC1-145 |  |  | 0.1
925665 | AC1-042 E | 0.4 | 345 | 75 | 0 | 26.04 | 3.91 |  |  | -0.0161 |  |  |  | 0 |  | 1 | NEW | AC1-042 |  |  | 0.1
316217 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 2.85 |  |  | -0.0161 |  |  |  | 0 |  | 1 | CAPACITY | AC1-145 |  |  | 0.1
316197 | AC1-042 C | 0.4 | 345 | 75 | 0 | 15.96 | 2.39 |  |  | -0.0161 |  |  |  | 0 |  | 1 | CAPACITY | AC1-042 |  |  | 0.1
316315 | AB2-025 C | 230 | 345 | 75 | 0 | 13.65 | 2.05 |  |  | -0.01619 |  |  |  | 0 |  | 1 | CAPACITY | AB2-025 |  |  | 0.1
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | -0.01619 |  |  |  | 0 |  | 1 | NEW | AB2-025 |  |  | 0.1
901082 | W1-029 E | 230 | 345 | 74 | 0 | 169 | 167.31 |  |  | -0.01624 |  |  |  | 0 |  | 1 | NEW | W1-029 |  |  | 0.8
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 38.61 |  |  | -0.01624 |  |  |  | 0 |  | 1 | CAPACITY | W1-029 |  |  | 0.8
316321 | Z2-027 C | 230 | 345 | 75 | 0 | 13.8 | 2.07 |  |  | -0.0163 |  |  |  | 0 |  | 1 | CAPACITY | Z2-027 |  |  | 0.1
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.0163 |  |  |  | 0 |  | 1 | NEW | Z2-027 |  |  | 0.1
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 30.18 |  |  | -0.01631 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 0.8
270111 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 4.51 |  |  | -0.01631 |  |  |  | 0 |  | 1 | NEW | Y1-006 |  |  | 0.8
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 12.2 | 6.77 |  |  | -0.01632 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.01632 |  |  |  | 0.0789 |  | 1 | ENERGY |  |  |  | 1
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.1 | 5.05 |  |  | -0.01632 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.01632 |  |  |  | 0 |  | 1 | MTX | AD2-205 |  |  | 1
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 1.95 |  |  | -0.01634 |  |  |  | 0 |  | 1 | CAPACITY | AB2-022 |  |  | 0.1
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 1.86 |  |  | -0.01634 |  |  |  | 0 |  | 1 | NEW | Y1-086 |  |  | 0.1
316320 | Y1-086 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | -0.01634 |  |  |  | 0 |  | 1 | CAPACITY | Y1-086 |  |  | 0.1
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 1.05 |  |  | -0.01634 |  |  |  | 0 |  | 1 | NEW | AB2-022 |  |  | 0.1
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 10.06 |  |  | -0.01643 |  |  |  | 0.44065 |  | 1 | CAPACITY |  |  |  | 1
316305 | AF2-043 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AF2-043 |  |  | 0.1
316244 | AE2-225 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AE2-225 |  |  | 0.1
316246 | AF1-032 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AF1-032 |  |  | 0.1
316245 | AE2-229 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | -0.01644 |  |  |  | 0 |  | 1 | CAPACITY | AE2-229 |  |  | 0.1
957492 | AF2-043 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AF2-043 |  |  | 0.1
942132 | AE2-225 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AE2-225 |  |  | 0.1
942172 | AE2-229 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AE2-229 |  |  | 0.1
943612 | AF1-032 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | -0.01644 |  |  |  | 0 |  | 1 | NEW | AF1-032 |  |  | 0.1
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 11.81 |  |  | -0.01646 |  |  |  | 0 |  | 1 | CAPACITY | AA1-139 |  |  | 0.1
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 5.4 |  |  | -0.01646 |  |  |  | 0 |  | 1 | NEW | AA1-139 |  |  | 0.1
932596 | AC2-079 E | 0.64 | 345 | 75 | 0 | 52.7 | 7.91 |  |  | -0.01649 |  |  |  | 0 |  | 1 | NEW | AC2-079 |  |  | 0.1
316311 | AC2-079 C | 0.64 | 345 | 75 | 0 | 32.3 | 4.84 |  |  | -0.01649 |  |  |  | 0 |  | 1 | CAPACITY | AC2-079 |  |  | 0.1
270173 | AC1-122_C | 0.6 | 205 | 75 | 0 | 54.4 | 3.97 |  |  | -0.01652 |  |  |  | 0 |  | 1 | CAPACITY | AC1-122 |  |  | 0.1
926516 | AC1-122_E | 0.6 | 205 | 75 | 0 | 21.5 | 1.57 |  |  | -0.01652 |  |  |  | 0 |  | 1 | NEW | AC1-122 |  |  | 0.1
316150 | AD2-215 C | 230 | 345 | 75 | 0 | 9.8 | 1.47 |  |  | -0.01653 |  |  |  | 0 |  | 1 | CAPACITY | AD2-215 |  |  | 0.1
316072 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 1.46 |  |  | -0.01653 |  |  |  | 0 |  | 1 | CAPACITY | AD1-144 |  |  | 0.1
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | -0.01653 |  |  |  | 0 |  | 1 | NEW | AD1-144 |  |  | 0.1
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0.78 |  |  | -0.01653 |  |  |  | 0 |  | 1 | NEW | AD2-215 |  |  | 0.1
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 27.95 |  |  | -0.01653 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316185 | AD1-033 C | 0.6 | 345 | 75 | 0 | 42 | 6.3 |  |  | -0.01654 |  |  |  | 0 |  | 1 | CAPACITY | AD1-033 |  |  | 0.1
934065 | AD1-033 E | 0.6 | 345 | 75 | 0 | 28 | 4.2 |  |  | -0.01654 |  |  |  | 0 |  | 1 | NEW | AD1-033 |  |  | 0.1
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.01653 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 13.37 |  |  | -0.01653 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316057 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | -0.01653 |  |  |  | 0 |  | 1 | CAPACITY | AC2-196 |  |  | 0.1
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 1 |  |  | -0.01653 |  |  |  | 0 |  | 1 | NEW | AC2-196 |  |  | 0.1
316316 | AC1-027 C | 115 | 345 | 75 | 0 | 11.2 | 1.68 |  |  | -0.01655 |  |  |  | 0 |  | 1 | CAPACITY | AC1-027 |  |  | 0.1
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | -0.01655 |  |  |  | 0 |  | 1 | NEW | AC1-027 |  |  | 0.1
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 10.4 |  |  | -0.01655 |  |  |  | 0 |  | 1 | NEW | Z1-068 |  |  | 0.8
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.49 |  |  | -0.01655 |  |  |  | 0 |  | 1 | CAPACITY | Z1-068 |  |  | 0.8
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 83.11 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 82.06 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 80.64 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315099 | 1CHESPKB | 13.8 | 345 | 20 | 0 | 24.7 | 0 |  |  | -0.01658 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 0.45 |  |  | -0.01658 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316036 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 1.89 |  |  | -0.01658 |  |  |  | 0 |  | 1 | CAPACITY | AC1-147 |  |  | 0.1
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | -0.01658 |  |  |  | 0 |  | 1 | NEW | AC1-147 |  |  | 0.1
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 7.56 |  |  | -0.01657 |  |  |  | 0.1097 |  | 1 | CAPACITY | VIRGINIA BEACH LF_A |  |  | 1
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 11.9 |  |  | -0.01657 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 12.9 |  |  | -0.01657 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 15.2 |  |  | -0.01657 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251542 | 08VERONA | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.0166 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 2.22 |  |  | -0.01661 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.01664 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 0.1
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 2.85 |  |  | -0.01664 |  |  |  | 0 |  | 1 | NEW | AB2-161 |  |  | 0.1
316294 | AC1-161 C | 0.44 | 345 | 75 | 0 | 168.2 | 25.23 |  |  | -0.01667 |  |  |  | 0 |  | 1 | CAPACITY | AC1-161 |  |  | 0.1
926755 | AC1-161 E | 0.44 | 345 | 75 | 0 | 71.8 | 0 |  |  | -0.01667 |  |  |  | 0 |  | 1 | NEW | AC1-161 |  |  | 0.1
316236 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.0167 |  |  |  | 0 |  | 1 | CAPACITY | AE1-162 |  |  | 0.1
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.0167 |  |  |  | 0 |  | 1 | NEW | AE1-162 |  |  | 0.1
932586 | AC2-078 E | 0.64 | 345 | 75 | 0 | 37.2 | 5.58 |  |  | -0.0167 |  |  |  | 0 |  | 1 | NEW | AC2-078 |  |  | 0.1
316289 | AC2-078 C | 0.64 | 345 | 75 | 0 | 22.8 | 3.42 |  |  | -0.0167 |  |  |  | 0 |  | 1 | CAPACITY | AC2-078 |  |  | 0.1
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 2.75 |  |  | -0.01671 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 0.89 |  |  | -0.01677 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 65.18 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 65.11 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 64.36 |  |  | -0.01677 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 844.6 |  |  | -0.01677 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316242 | AE2-079 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY | AE2-079 |  |  | 0.1
316241 | AE2-078 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY | AE2-078 |  |  | 0.1
316247 | AF1-033 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY | AF1-033 |  |  | 0.1
943622 | AF1-033 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01679 |  |  |  | 0 |  | 1 | NEW | AF1-033 |  |  | 0.1
940902 | AE2-079 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01679 |  |  |  | 0 |  | 1 | NEW | AE2-079 |  |  | 0.1
940892 | AE2-078 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01679 |  |  |  | 0 |  | 1 | NEW | AE2-078 |  |  | 0.1
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 843.5 |  |  | -0.01679 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
341584 | 2GRIFFIN | 69 | 320 | 77 | 0 | 3.2 | 2.16 |  |  | -0.01684 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
270205 | AE1-176 | 138 | 205 | 60 | 0 | 2.4 | 1.33 |  |  | -0.01685 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 4.5 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 10.77 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY | AB2-134 |  |  | 0.1
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 10.59 |  |  | -0.01688 |  |  |  | 0 |  | 1 | NEW | AB2-134 |  |  | 0.1
316051 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY | AC2-071 |  |  | 0.1
316322 | AB2-045 C | 230 | 345 | 75 | 0 | 11.43 | 1.72 |  |  | -0.01688 |  |  |  | 0 |  | 1 | CAPACITY | AB2-045 |  |  | 0.1
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01688 |  |  |  | 0 |  | 1 | NEW | AC2-071 |  |  | 0.1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0.94 |  |  | -0.01688 |  |  |  | 0 |  | 1 | NEW | AB2-045 |  |  | 0.1
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 787.1 | 23.61 |  |  | -0.01689 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 7.44 |  |  | -0.01691 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 0.1
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 4.56 |  |  | -0.01691 |  |  |  | 0 |  | 1 | NEW | AB2-160 |  |  | 0.1
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 6.71 |  |  | -0.01691 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 16.8 |  |  | -0.01691 |  |  |  | 0 |  | 1 | CAPACITY | AB2-190 |  |  | 0.1
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 7.2 |  |  | -0.01691 |  |  |  | 0 |  | 1 | NEW | AB2-190 |  |  | 0.1
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | -0.01693 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 20.86 |  |  | -0.01693 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
316301 | AE2-228 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | -0.01699 |  |  |  | 0 |  | 1 | CAPACITY | AE2-228 |  |  | 0.1
942162 | AE2-228 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | -0.01699 |  |  |  | 0 |  | 1 | NEW | AE2-228 |  |  | 0.1
316240 | AF1-291 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.017 |  |  |  | 0 |  | 1 | CAPACITY | AF1-291 |  |  | 0.1
946262 | AF1-291 E | 230 | 345 | 75 | 0 | 8 | 1.2 |  |  | -0.017 |  |  |  | 0 |  | 1 | NEW | AF1-291 |  |  | 0.1
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.01703 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 94.51 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | -0.01703 |  |  |  | 0.036 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 62.26 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF |  |  | 1
342550 | 4BAVARIAN LF | 138 | 320 | 77 | 0 | 4.8 | 3.24 |  |  | -0.01703 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 52.8 | 52.8 |  |  | -0.01703 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316159 | AE1-175 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01704 |  |  |  | 0 |  | 1 | CAPACITY | AE1-175 |  |  | 0.1
316160 | AE1-175 E | 230 | 345 | 75 | 0 | 6.6 | 0.99 |  |  | -0.01704 |  |  |  | 0 |  | 1 | NEW | AE1-175 |  |  | 0.1
242587 | 05CELAN | 138 | 205 | 77 | 0 | 81.6 | 58.39 |  |  | -0.01711 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 98.04 |  |  | -0.01721 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 96.46 |  |  | -0.01721 |  |  |  | 0.036 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 49.66 |  |  | -0.01721 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8 |  |  | 1
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 45.01 |  |  | -0.01721 |  |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7 |  |  | 1
316280 | AD1-041 C | 0.55 | 345 | 75 | 0 | 30 | 4.5 |  |  | -0.01722 |  |  |  | 0 |  | 1 | CAPACITY | AD1-041 |  |  | 0.1
934146 | AD1-041 E | 0.55 | 345 | 75 | 0 | 20 | 3 |  |  | -0.01722 |  |  |  | 0 |  | 1 | NEW | AD1-041 |  |  | 0.1
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 1.97 |  |  | -0.01721 |  |  |  | 0 |  | 1 | CAPACITY | AD2-030 |  |  | 0.1
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01721 |  |  |  | 0 |  | 1 | NEW | AD2-030 |  |  | 0.1
316201 | AC1-065 C | 0.39 | 345 | 75 | 0 | 49.4 | 7.41 |  |  | -0.01723 |  |  |  | 0 |  | 1 | CAPACITY | AC1-065 |  |  | 0.1
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 4.65 |  |  | -0.01723 |  |  |  | 0 |  | 1 | NEW | AC1-065 |  |  | 0.1
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 20 |  |  | -0.01723 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316059 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 1.35 |  |  | -0.01724 |  |  |  | 0 |  | 1 | CAPACITY | AD1-063 |  |  | 0.1
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.1 | 10.8 |  |  | -0.01724 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHARLES CITY_LF |  |  | 1
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01724 |  |  |  | 0 |  | 1 | NEW | AD1-063 |  |  | 0.1
313053 | 6PAPERMILL | 230 | 345 | 77 | 12 | 37 | 0 |  |  | -0.01725 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
316314 | AB2-024 C | 230 | 345 | 75 | 0 | 11.13 | 1.67 |  |  | -0.01725 |  |  |  | 0 |  | 1 | CAPACITY | AB2-024 |  |  | 0.1
315086 | 1SPRUNCD | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | -0.01726 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315085 | 1SPRUNCC | 13.8 | 345 | 56 | 16 | 33 | 24.75 |  |  | -0.01726 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | -0.01725 |  |  |  | 0 |  | 1 | NEW | AB2-024 |  |  | 0.1
316304 | AE2-227 C | 230 | 345 | 75 | 0 | 15 | 2.25 |  |  | -0.01727 |  |  |  | 0 |  | 1 | CAPACITY | AE2-227 |  |  | 0.1
942152 | AE2-227 E | 230 | 345 | 75 | 0 | 10 | 1.5 |  |  | -0.01727 |  |  |  | 0 |  | 1 | NEW | AE2-227 |  |  | 0.1
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 9.99 |  |  | -0.01727 |  |  |  | 0.1097 |  | 1 | CAPACITY | CHESTERFIELD LF_A |  |  | 1
316169 | AC1-164 GEN | 0.44 | 345 | 75 | 192.1 | 220.8 | 33.12 |  |  | -0.01729 |  |  |  | 0 |  | 1 | CAPACITY | AC1-164 |  |  | 0.1
926785 | AC1-164_E | 0.44 | 345 | 75 | 91 | 104.6 | 15.69 |  |  | -0.01729 |  |  |  | 0 |  | 1 | NEW | AC1-164 |  |  | 0.1
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 185.28 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 143.27 |  |  | -0.01731 |  |  |  | 0.036 |  | 1 | CAPACITY | BEAR GARDEN |  |  | 1
AF2-085 | BATEXP_AF2-085->PJM |  |  | LTF |  | 20 |  |  |  | -0.0173
316313 | AB2-026 C | 230 | 345 | 75 | 0 | 13.07 | 1.96 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | AB2-026 |  |  | 0.1
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 12.7 | 1.9 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | AC2-137 |  |  | 0.1
316258 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 1.8 |  |  | -0.01731 |  |  |  | 0 |  | 1 | CAPACITY | AE1-075 |  |  | 0.1
316303 | AF2-085 | 230 | 345 | 76 | 0 | 20 | 13.41 |  |  | -0.01732 |  |  |  | 0.05 |  | 1 | CAPACITY |  |  |  | 1
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 1.11 |  |  | -0.01731 |  |  |  | 0 |  | 1 | NEW | AC2-137 |  |  | 0.1
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0.93 |  |  | -0.01731 |  |  |  | 0 |  | 1 | NEW | AB2-026 |  |  | 0.1
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0.88 |  |  | -0.01731 |  |  |  | 0 |  | 1 | NEW | AE1-075 |  |  | 0.1
316233 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01732 |  |  |  | 0 |  | 1 | CAPACITY | AE1-074 |  |  | 0.1
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01732 |  |  |  | 0 |  | 1 | NEW | AE1-074 |  |  | 0.1
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 64.51 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 64.43 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 64.21 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 64.14 |  |  | -0.01735 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 6.2 |  |  | -0.01736 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.01737 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.01737 |  |  |  | 0 |  | 1 | NEW | AC1-107 |  |  | 1
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.01737 |  |  |  | 0.036 |  | 1 | NEW | AC1-107 |  |  | 1
316312 | AB1-027 C | 230 | 345 | 75 | 0 | 17.5 | 2.63 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AB1-027 |  |  | 0.1
316004 | AC1-112 C | 230 | 345 | 75 | 0 | 10.9 | 1.63 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AC1-112 |  |  | 0.1
316050 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 1.38 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AC2-070 |  |  | 0.1
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 7.5 | 1.13 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AB1-027 |  |  | 0.1
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0.92 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AC1-112 |  |  | 0.1
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0.57 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AC2-070 |  |  | 0.1
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 0.75 |  |  | -0.01742 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 0.72 |  |  | -0.01742 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 8.4 | 1.26 |  |  | -0.01742 |  |  |  | 0 |  | 1 | CAPACITY | AC2-138 |  |  | 0.1
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0.9 |  |  | -0.01742 |  |  |  | 0 |  | 1 | NEW | AC2-138 |  |  | 0.1
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 7.38 |  |  | -0.01744 |  |  |  | 0.20737 |  | 1 | CAPACITY |  |  |  | 1
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 4 |  |  | -0.0175 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316223 | AC1-118 C | 230 | 345 | 75 | 0 | 13.2 | 1.98 |  |  | -0.01759 |  |  |  | 0 |  | 1 | CAPACITY | AC1-118 |  |  | 0.1
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 1.02 |  |  | -0.01759 |  |  |  | 0 |  | 1 | NEW | AC1-118 |  |  | 0.1
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 165.2 | 123.92 |  |  | -0.01771 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 165.1 | 123.84 |  |  | -0.01771 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 126.7 | 95.04 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 124.8 | 93.61 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 103.7 | 77.79 |  |  | -0.01771 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 5 |  |  | 1
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | -0.01771 |  |  |  | 0 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 102.2 | 76.66 |  |  | -0.01771 |  |  |  | 0.036 |  | 1 | CAPACITY | Doswell 6 |  |  | 1
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 127.52 |  |  | -0.01771 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
316234 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01772 |  |  |  | 0 |  | 1 | CAPACITY | AE1-124 |  |  | 0.1
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01772 |  |  |  | 0 |  | 1 | NEW | AE1-124 |  |  | 0.1
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF3 |  |  | 1
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF4 |  |  | 1
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF1 |  |  | 1
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 73.3 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF6 |  |  | 1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF2 |  |  | 1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 124.7 |  |  | -0.01775 |  |  |  | 0 |  | 1 | CAPACITY | CLIF5 |  |  | 1
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 1.17 |  |  | -0.0178 |  |  |  | 0 |  | 1 | NEW | AC1-116 |  |  | 0.1
316035 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 0.7 |  |  | -0.0178 |  |  |  | 0 |  | 1 | CAPACITY | AC1-116 |  |  | 0.1
314860 | 4E MILL | 138 | 345 | 77 | 0 | 50 | 0 |  |  | -0.01798 |  |  |  | 0 |  | 1 | NEWENERGY | Covington |  |  | 1
314859 | 4WSTVACO | 138 | 345 | 2 | 0 | 40.5 | 0 |  |  | -0.01798 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
909222 | X2-060 E | 138 | 345 | 64 | 0 | 30 | 0 |  |  | -0.01798 |  |  |  | 0 |  | 1 | ENERGY | Covington |  |  | 1
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 0.76 |  |  | -0.01798 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 0.75 |  |  | -0.01798 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
918234 | AA1-038_E | 0.69 | 345 | 74 | 0 | 66.7 | 66.03 |  |  | -0.01798 |  |  |  | 0 |  | 1 | NEW | AA1-038 |  |  | 0.8
315616 | AA1-038_C | 0.69 | 345 | 74 | 0 | 9.9 | 9.8 |  |  | -0.01798 |  |  |  | 0 |  | 1 | CAPACITY | AA1-038 |  |  | 0.8
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 5.5 |  |  | -0.01798 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 301.17 |  |  | -0.01801 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | -0.01801 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | -0.01801 |  |  |  | 0 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 134.65 |  |  | -0.01801 |  |  |  | 0.036 |  | 1 | CAPACITY | FLUVANNA |  |  | 1
316299 | AC2-112 C | 0.6 | 345 | 75 | 0 | 103.1 | 15.47 |  |  | -0.01806 |  |  |  | 0 |  | 1 | CAPACITY | AC2-112 |  |  | 0.1
932855 | AC2-112 E | 0.6 | 345 | 75 | 0 | 46.9 | 0 |  |  | -0.01806 |  |  |  | 0 |  | 1 | NEW | AC2-112 |  |  | 0.1
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 8.7 |  |  | -0.01807 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 223.38 |  |  | -0.01808 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 502.3 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 503.8 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 502.2 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 502.8 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 502 |  |  | -0.01809 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 124.52 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 120.47 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 120.09 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 119.87 |  |  | -0.0182 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 0.39 |  |  | -0.01821 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 0.37 |  |  | -0.01821 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 948.5 |  |  | -0.01823 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 948.9 |  |  | -0.01823 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316192 | AB2-158 C | 230 | 345 | 75 | 0 | 71 | 10.65 |  |  | -0.01828 |  |  |  | 0 |  | 1 | CAPACITY | AB2-158 |  |  | 0.1
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 4.08 |  |  | -0.01828 |  |  |  | 0 |  | 1 | NEW | AB2-158 |  |  | 0.1
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 118.52 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 58.13 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 57.83 |  |  | -0.01832 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | -0.01831 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 54.01 |  |  | -0.01831 |  |  |  | 0.036 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | -0.01831 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 1 |  |  | 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 27.75 |  |  | -0.01831 |  |  |  | 0 |  | 1 | CAPACITY | South Anna 2 |  |  | 1
249991 | 08BUFTN1 | 138 | 212 | 77 | 0 | 2.2 | 0 |  |  | -0.01833 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
342031 | 2PACTOLUS | 69 | 320 | 77 | 0 | 2.4 | 1.62 |  |  | -0.01836 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 194.77 |  |  | -0.01841 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | -0.01841 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 199.55 |  |  | -0.01841 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 2 |  |  | -0.01843 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316044 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | -0.01848 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 1 |  |  | 0.1
316045 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 26.06 |  |  | -0.01848 |  |  |  | 0 |  | 1 | CAPACITY | AC1-158 2 |  |  | 0.1
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | -0.01848 |  |  |  | 0 |  | 1 | NEW | AC1-158 1 |  |  | 0.1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 11.44 |  |  | -0.01848 |  |  |  | 0 |  | 1 | NEW | AC1-158 2 |  |  | 0.1
926004 | AC1-076_E | 0.6 | 345 | 75 | 0 | 39.42 | 5.91 |  |  | -0.0185 |  |  |  | 0 |  | 1 | NEW | AC1-076 |  |  | 0.1
316164 | AC1-076_C | 0.6 | 345 | 75 | 0 | 23.8 | 3.57 |  |  | -0.0185 |  |  |  | 0 |  | 1 | CAPACITY | AC1-076 |  |  | 0.1
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | -0.01849 |  |  |  | 0 |  | 1 | CAPACITY | AE1-099 |  |  | 0.1
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | -0.01849 |  |  |  | 0 |  | 1 | CAPACITY | AE1-098 |  |  | 0.1
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | -0.01849 |  |  |  | 0 |  | 1 | NEW | AE1-099 |  |  | 0.1
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0.8 |  |  | -0.01849 |  |  |  | 0 |  | 1 | NEW | AE1-098 |  |  | 0.1
316254 | AC1-120 C | 0.6 | 345 | 75 | 0 | 39.6 | 5.94 |  |  | -0.01854 |  |  |  | 0 |  | 1 | CAPACITY | AC1-120 |  |  | 0.1
926486 | AC1-120 E | 0.6 | 345 | 75 | 0 | 20.4 | 3.06 |  |  | -0.01854 |  |  |  | 0 |  | 1 | NEW | AC1-120 |  |  | 0.1
316170 | AC1-121 C | 0.6 | 345 | 75 | 0 | 13.6 | 2.04 |  |  | -0.01854 |  |  |  | 0 |  | 1 | CAPACITY | AC1-121 |  |  | 0.1
926502 | AC1-121 E | 0.6 | 345 | 75 | 0 | 6.4 | 0.96 |  |  | -0.01854 |  |  |  | 0 |  | 1 | NEW | AC1-121 |  |  | 0.1
925672 | AC1-043 E | 115 | 345 | 75 | 0 | 62 | 9.3 |  |  | -0.01857 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 0.1
316257 | AC1-043 C | 115 | 345 | 75 | 0 | 38 | 5.7 |  |  | -0.01857 |  |  |  | 0 |  | 1 | NEW | AC1-043 |  |  | 0.1
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 1.07 | 0.16 |  |  | -0.01858 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
961102 | AF2-401 E | 115 | 345 | 75 | 0 | 5.8 | 0.87 |  |  | -0.01861 |  |  |  | 0 |  | 1 | NEW | AF2-401 |  |  | 0.1
316302 | AF2-401 C | 115 | 345 | 75 | 0 | 3.52 | 0.53 |  |  | -0.01861 |  |  |  | 0 |  | 1 | CAPACITY | AF2-401 |  |  | 0.1
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 1.46 |  |  | -0.01863 |  |  |  | 0 |  | 1 | NEW | AD1-085 |  |  | 0.1
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 0.9 |  |  | -0.01863 |  |  |  | 0 |  | 1 | CAPACITY | AD1-085 |  |  | 0.1
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 0.72 |  |  | -0.01863 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.44 |  |  | -0.01863 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 2.4 | 1.61 |  |  | -0.01865 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
316267 | AC1-143 C | 0.38 | 345 | 75 | 0 | 41.2 | 6.18 |  |  | -0.01869 |  |  |  | 0 |  | 1 | CAPACITY | AC1-143 |  |  | 0.1
926615 | AC1-143 E | 0.38 | 345 | 75 | 0 | 18.8 | 2.82 |  |  | -0.01869 |  |  |  | 0 |  | 1 | NEW | AC1-143 |  |  | 0.1
316054 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 1.56 |  |  | -0.01869 |  |  |  | 0 |  | 1 | CAPACITY | AC2-074 |  |  | 0.1
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0.79 |  |  | -0.01869 |  |  |  | 0 |  | 1 | NEW | AC2-074 |  |  | 0.1
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 1.83 |  |  | -0.01873 |  |  |  | 0 |  | 1 | NEW | AB2-029 |  |  | 0.1
316006 | AB2-029 C | 230 | 345 | 75 | 0 | 7.6 | 1.14 |  |  | -0.01873 |  |  |  | 0 |  | 1 | CAPACITY | AB2-029 |  |  | 0.1
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 170 | 127.52 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | -0.01877 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 121.37 |  |  | -0.01877 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 120.39 |  |  | -0.01877 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 113.79 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.1 | 113.34 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 112.29 |  |  | -0.01877 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.01884 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.01884 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 19.58 |  |  | -0.01884 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
251269 | 08BEAVR2 | 69 | 212 | 77 | 0 | 2 | 1.41 |  |  | -0.01886 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 188.28 |  |  | -0.01887 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | -0.01887 |  |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 120.77 |  |  | -0.01887 |  |  |  | 0.036 |  | 1 | CAPACITY | POSSUM POINT |  |  | 1
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 1.07 |  |  | -0.01887 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 1.07 |  |  | -0.01887 |  |  |  | 0.28116 |  | 1 | CAPACITY |  |  |  | 1
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.01891 |  |  |  | 0.0975 |  | 1 | MTX | Z1-065 |  |  | 1
316052 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 2 |  |  | -0.01895 |  |  |  | 0 |  | 1 | CAPACITY | AC2-072 |  |  | 0.1
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 1 |  |  | -0.01895 |  |  |  | 0 |  | 1 | NEW | AC2-072 |  |  | 0.1
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 39.45 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
913222 | Y1-054 E | 138 | 212 | 58 | 0 | 20 | 0 |  |  | -0.01896 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
314088 | 6VANDORN | 230 | 345 | 1 | 7 | 21 | 14.08 |  |  | -0.01896 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
250091 | 08RCHLE3 | 138 | 212 | 77 | 0 | 6.7 | 4.72 |  |  | -0.01896 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 734 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 586 |  |  | -0.01896 |  |  |  | 0 |  | 1 | CAPACITY | ZIMM |  |  | 1
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | -0.01897 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251346 | 08IVYDL1 | 69 | 212 | 77 | 0 | 12.5 | 8.81 |  |  | -0.01903 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.01915 |  |  |  | 0 |  | 1 | MTX | Y3-100 |  |  | 1
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.01915 |  |  |  | 0 |  | 1 | MTX | Y3-099 |  |  | 1
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 227.1 |  |  | -0.01918 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  |  |  | -0.0192
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 229.53 |  |  | -0.0192 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | -0.0192 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-039 |  |  | 1
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 166.52 |  |  | -0.0192 |  |  |  | 0 |  | 1 | CAPACITY | X4-039 |  |  | 1
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 44.38 |  |  | -0.01924 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
250041 | 08HAMLTN | 138 | 212 | 77 | 0 | 2.2 | 1.55 |  |  | -0.01925 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 105.16 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2 |  |  | 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 65.84 |  |  | -0.01928 |  |  |  | 0.036 |  | 1 | CAPACITY | Lawrenceburg 1 |  |  | 1
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 600 |  |  | -0.01927 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 6.79 |  |  | -0.01928 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 0.1
270186 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.01928 |  |  |  | 0 |  | 1 | NEW | AC1-089 |  |  | 0.1
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 327.3 | 176.05 |  |  | -0.01929 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | -0.01929 |  |  |  | 0 |  | 1 | CAPACITY | X4-035 |  |  | 1
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 223.1 | 120 |  |  | -0.01929 |  |  |  | 0.036 |  | 1 | CAPACITY | X4-035 |  |  | 1
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 43.03 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | -0.01931 |  |  |  | 0.036 |  | 1 | CAPACITY | PANDA |  |  | 1
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 40.34 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | PANDA |  |  | 1
226704 | AOCX4-046 E | 13.8 | 233 | 58 | 0 | 19.5 | 0 |  |  | -0.01931 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | -0.01931 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226924 | AE1-015 E | 69 | 233 | 75 | 0 | 0.75 | 0.07 |  |  | -0.01931 |  |  |  | 0 |  | 1 | NEW | AE1-015 |  |  | 0.1
226923 | AE1-015 C | 69 | 233 | 75 | 0 | 0.57 | 0.05 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | AE1-015 |  |  | 0.1
226922 | AE1-013 E | 69 | 233 | 75 | 0 | 0.5 | 0.05 |  |  | -0.01931 |  |  |  | 0 |  | 1 | NEW | AE1-013 |  |  | 0.1
226921 | AE1-013 C | 69 | 233 | 75 | 0 | 0.38 | 0.04 |  |  | -0.01931 |  |  |  | 0 |  | 1 | CAPACITY | AE1-013 |  |  | 0.1
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.01933 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 510 |  |  | -0.01933 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 395.08 |  |  | -0.01936 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | -0.01936 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | -0.01936 |  |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 210.86 |  |  | -0.01936 |  |  |  | 0.036 |  | 1 | CAPACITY | WARREN COUNTY CC |  |  | 1
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -0.01938 |  |  |  | 0.036 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 122.51 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 87.53 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | AB1-169 |  |  | 1
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 182.23 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | -0.01938 |  |  |  | 0.036 |  | 1 | CAPACITY | WALDORF |  |  | 1
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 124.03 |  |  | -0.01938 |  |  |  | 0 |  | 1 | CAPACITY | WALDORF |  |  | 1
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 29.05 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 1.86 |  |  | -0.01939 |  |  |  | 0 |  | 1 | NEW | AC2-101 |  |  | 0.1
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 1.58 |  |  | -0.01939 |  |  |  | 0 |  | 1 | NEW | AC2-120 |  |  | 0.1
227282 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 1.14 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY | AC2-101 |  |  | 0.1
227280 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 0.97 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY | AC2-120 |  |  | 0.1
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 8.61 |  |  | -0.01939 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 613.3 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 619.4 |  |  | -0.01939 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 11.01 |  |  | -0.0194 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 10.83 |  |  | -0.0194 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 58.63 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 46.26 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
227024 | SMECOCT | 13.8 | 238 | 57 | 0 | 80.2 | 43.14 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 13.12 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 9.68 |  |  | -0.0194 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | -0.01941 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.39 |  |  | -0.01941 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 3.05 |  |  | -0.01943 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0.16 |  |  | -0.01943 |  |  |  | 0 |  | 1 | NEW | AB2-157 |  |  | 0.1
226910 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.07 |  |  | -0.01943 |  |  |  | 0 |  | 1 | CAPACITY | AB2-157 |  |  | 0.1
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.91 |  |  | -0.01942 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247225 | 05FTHLG2 | 18 | 205 | 57 | 151.2 | 173.8 | 66.38 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247224 | 05FTHLG1 | 18 | 205 | 57 | 151.1 | 173.7 | 66.34 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247231 | 05RIVRG2 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247232 | 05RIVRG3 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 149.2 | 171.5 | 65.5 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 53 | 20.24 |  |  | -0.01944 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 866 |  |  | -0.01945 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 841.8 |  |  | -0.01945 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | -0.01947 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 0.1
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0.45 |  |  | -0.01947 |  |  |  | 0 |  | 1 | NEW | Z2-030 |  |  | 0.1
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | -0.01947 |  |  |  | 0 |  | 1 | CAPACITY | Z2-030 |  |  | 0.1
237077 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0.28 |  |  | -0.01947 |  |  |  | 0 |  | 1 | NEW | AC2-174 |  |  | 0.1
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 0.76 |  |  | -0.01947 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | -0.01949 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 79.07 |  |  | -0.01949 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 0.33 |  |  | -0.01948 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 52 |  |  | -0.01949 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
226920 | AE1-012 E | 115 | 233 | 75 | 0 | 0.34 | 0.03 |  |  | -0.01949 |  |  |  | 0 |  | 1 | NEW | AE1-012 |  |  | 0.1
226919 | AE1-012 C | 115 | 233 | 75 | 0 | 0.22 | 0.02 |  |  | -0.01949 |  |  |  | 0 |  | 1 | CAPACITY | AE1-012 |  |  | 0.1
252507 | AC2-088 C | 0.57 | 212 | 75 | 0 | 38.4 | 2.8 |  |  | -0.01952 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 0.1
932665 | AC2-088 E | 0.57 | 212 | 75 | 0 | 31.6 | 2.31 |  |  | -0.01952 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 0.1
252509 | AD1-136 C | 0.57 | 212 | 75 | 0 | 5.4 | 0.39 |  |  | -0.01952 |  |  |  | 0 |  | 1 | CAPACITY | AC2-088 |  |  | 0.1
935033 | AD1-136 E | 0.57 | 212 | 75 | 0 | 4.6 | 0.34 |  |  | -0.01952 |  |  |  | 0 |  | 1 | NEW | AC2-088 |  |  | 0.1
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.5 | 3.02 |  |  | -0.01952 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | -0.01953 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 29.06 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76 | 29.02 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 28.99 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 28.91 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 28.87 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 28.8 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251364 | 08LEBANO | 69 | 212 | 77 | 0 | 30.6 | 21.57 |  |  | -0.01955 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 1.87 |  |  | -0.01956 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251832 | 08HLCRTG | 0.38 | 212 | 75 | 0 | 120 | 8.76 |  |  | -0.01958 |  |  |  | 0 |  | 1 | CAPACITY | AB1-014 |  |  | 0.1
930062 | AB1-014 E | 0.38 | 212 | 75 | 0 | 77.5 | 5.66 |  |  | -0.01958 |  |  |  | 0 |  | 1 | NEW | AB1-014 |  |  | 0.1
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.87 |  |  | -0.01958 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 19.29 |  |  | -0.01959 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251387 | 08MDDLTW | 69 | 212 | 77 | 0 | 22.5 | 16.62 |  |  | -0.01959 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 26.35 |  |  | -0.0196 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 11.46 |  |  | -0.0196 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 4.93 |  |  | -0.0196 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223967 | METZ E69 | 69 | 233 | 56 | 0 | 20 | 0 |  |  | -0.01961 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
226895 | WOAKV2-037 E | 69 | 233 | 29 | 0 | 4.5 | 0 |  |  | -0.01961 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 31.16 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.5 | 30.74 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 30.59 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 30.4 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 29.56 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251952 | 08MADSN1 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251953 | 08MADSN2 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251954 | 08MADSN3 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251955 | 08MADSN4 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251959 | 08MADSN8 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251957 | 08MADSN6 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251958 | 08MADSN7 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
251956 | 08MADSN5 | 13.8 | 212 | 57 | 62.6 | 72 | 27.5 |  |  | -0.01962 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 3.62 |  |  | -0.01964 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 0.1
237026 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 2.22 |  |  | -0.01964 |  |  |  | 0 |  | 1 | NEW | AB2-129 |  |  | 0.1
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.64 |  |  | -0.01964 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 272.1 | 103.92 |  |  | -0.01965 |  |  |  | 0.036 |  | 1 | CAPACITY | Z1-079 |  |  | 1
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 202.7 | 77.41 |  |  | -0.01965 |  |  |  | 0 |  | 1 | CAPACITY | Z1-079 |  |  | 1
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 54.8 | 40.8 |  |  | -0.01966 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
251828 | CLNTESP1 | 0 | 212 | 76 | 0 | 10 | 0 |  |  | -0.01971 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 113.58 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.1 | 113.46 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 71.15 |  |  | -0.01974 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 2 |  |  | 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | -0.01974 |  |  |  | 0.036 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.2 | 71.11 |  |  | -0.01974 |  |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1 |  |  | 1
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 7.99 |  |  | -0.01976 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 1.44 |  |  | -0.01976 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
923213 | AB1-125_E | 0.6 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | -0.01977 |  |  |  | 0 |  | 1 | NEW | AB1-125 |  |  | 0.1
237006 | AB1-125_C | 0.6 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | -0.01977 |  |  |  | 0 |  | 1 | CAPACITY | AB1-125 |  |  | 0.1
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 41.19 |  |  | -0.0198 |  |  |  | 0 |  | 1 | NEW | M24 |  |  | 0.8
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.0198 |  |  |  | 0.0975 |  | 1 | MTX | M24 BAT |  |  | 1
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 21.15 |  |  | -0.0198 |  |  |  | 0 |  | 1 | NEW | AB1-150 |  |  | 0.8
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 7.23 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY | M24 |  |  | 0.8
237033 | AB1-150 C | 138 | 201 | 74 | 0 | 7.3 | 3.52 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY | AB1-150 |  |  | 0.8
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 7.34 |  |  | -0.0198 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 638.9 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 642.7 |  |  | -0.0198 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247622 | Y3-025 | 69 | 205 | 64 | 0 | 3.18 | 0 |  |  | -0.01982 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.14 |  |  | -0.01982 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 68.9 |  |  | -0.01982 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 289.09 |  |  | -0.01982 |  |  |  | 0.1042 |  | 1 | CAPACITY | Wagner3 |  |  | 1
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | -0.01982 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 7.15 |  |  | -0.01982 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | -0.01985 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 0.78 |  |  | -0.01986 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 57 |  |  | -0.01986 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.2 | 16.24 |  |  | -0.01986 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 29.8 | 16.03 |  |  | -0.01986 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 108.79 |  |  | -0.01987 |  |  |  | 0 |  | 1 | NEW | K11 |  |  | 0.8
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 18.41 |  |  | -0.01987 |  |  |  | 0 |  | 1 | CAPACITY | K11 |  |  | 0.8
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.01988 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 0.1
237025 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.01988 |  |  |  | 0 |  | 1 | NEW | AB1-124 |  |  | 0.1
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0.44 |  |  | -0.01987 |  |  |  | 0 |  | 1 | NEW | AB1-096 |  |  | 0.1
237030 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 0.23 |  |  | -0.01987 |  |  |  | 0 |  | 1 | CAPACITY | AB1-096 |  |  | 0.1
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 81.18 |  |  | -0.01987 |  |  |  | 0 |  | 1 | NEW | T157 |  |  | 0.8
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 20.3 |  |  | -0.01987 |  |  |  | 0 |  | 1 | CAPACITY | T157 |  |  | 0.8
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 0.36 |  |  | -0.01989 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0.63 |  |  | -0.0199 |  |  |  | 0 |  | 1 | NEW | W1-116 |  |  | 0.1
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 0.39 |  |  | -0.0199 |  |  |  | 0 |  | 1 | CAPACITY | W1-116 |  |  | 0.1
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.0199 |  |  |  | 0 |  | 1 | MTX | AB1-055 |  |  | 1
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 553 |  |  | -0.01989 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM2 |  |  | 1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 522.9 |  |  | -0.01989 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 548.2 |  |  | -0.0199 |  |  |  | 0 |  | 1 | CAPACITY | MTSTM1 |  |  | 1
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 36.56 |  |  | -0.0199 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
237003 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0.76 |  |  | -0.01991 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 0.1
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | -0.01991 |  |  |  | 0 |  | 1 | NEW | AC1-039 |  |  | 0.1
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | -0.01991 |  |  |  | 0 |  | 1 | CAPACITY | AA1-109 |  |  | 0.1
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0.33 |  |  | -0.01991 |  |  |  | 0 |  | 1 | NEW | AA1-109 |  |  | 0.1
220904 | CRANE G2 | 20 | 232 | 12 | 0 | 14 | 0 |  |  | -0.01991 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 0.1
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 5.55 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 0.1
253314 | AC1-085 A_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 A |  |  | 0.8
253317 | AC1-085 B_E | 0.6 | 209 | 74 | 0 | 124 | 59.74 |  |  | -0.01993 |  |  |  | 0 |  | 1 | NEW | AC1-085 B |  |  | 0.8
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.61 |  |  | -0.01996 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 139.8 | 75.19 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 61.1 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 55.94 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 27.97 |  |  | -0.01998 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | W4-102 |  |  | 0.1
223402 | AF1-300 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | AF1-300 |  |  | 0.1
223401 | AF1-299 C | 34.5 | 232 | 75 | 0 | 9 | 0.83 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | AF1-299 |  |  | 0.1
946352 | AF1-299 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AF1-299 |  |  | 0.1
946362 | AF1-300 E | 34.5 | 232 | 75 | 0 | 8 | 0.74 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AF1-300 |  |  | 0.1
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | W4-102 |  |  | 0.1
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.4 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 0.1
237024 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0.51 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AB1-123 |  |  | 0.1
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0.24 |  |  | -0.01998 |  |  |  | 0 |  | 1 | NEW | AA1-095 |  |  | 0.1
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 0.21 |  |  | -0.01998 |  |  |  | 0 |  | 1 | CAPACITY | AA1-095 |  |  | 0.1
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 8.21 |  |  | -0.01999 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0.73 |  |  | -0.02001 |  |  |  | 0 |  | 1 | NEW | AB2-097 |  |  | 0.1
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02 |  |  |  | 0 |  | 1 | CAPACITY | AA1-092 |  |  | 0.1
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0.29 |  |  | -0.02 |  |  |  | 0 |  | 1 | NEW | AA1-092 |  |  | 0.1
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02003 |  |  |  | 0 |  | 1 | NEW | AA2-072 |  |  | 0.1
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0.46 |  |  | -0.02003 |  |  |  | 0 |  | 1 | NEW | AC2-136 |  |  | 0.1
237034 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 0.4 |  |  | -0.02003 |  |  |  | 0 |  | 1 | CAPACITY | AC2-136 |  |  | 0.1
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 10.07 |  |  | -0.02005 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0.68 |  |  | -0.02005 |  |  |  | 0 |  | 1 | NEW | AD1-060 |  |  | 0.1
237080 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 0.42 |  |  | -0.02005 |  |  |  | 0 |  | 1 | CAPACITY | AD1-060 |  |  | 0.1
237037 | AE1-188 C | 34.5 | 201 | 75 | 0 | 20.5 | 1.5 |  |  | -0.02008 |  |  |  | 0 |  | 1 | CAPACITY | AE1-188 |  |  | 0.1
237038 | AE2-054 C | 34.5 | 201 | 75 | 0 | 12 | 0.88 |  |  | -0.02007 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 0.1
939592 | AE1-188 E | 34.5 | 201 | 75 | 0 | 11.4 | 0.83 |  |  | -0.02008 |  |  |  | 0 |  | 1 | NEW | AE1-188 |  |  | 0.1
940672 | AE2-054 E | 34.5 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02007 |  |  |  | 0 |  | 1 | NEW | AE2-054 |  |  | 0.1
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 800 |  |  | -0.02008 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02009 |  |  |  | 0 |  | 1 | NEW | AB1-128 |  |  | 0.1
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02009 |  |  |  | 0 |  | 1 | NEW | AB1-127 |  |  | 0.1
235043 | AF1-166 C | 34.5 | 201 | 75 | 0 | 9.6 | 0.7 |  |  | -0.02009 |  |  |  | 0 |  | 1 | CAPACITY | AF1-166 |  |  | 0.1
237001 | AB1-127 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.02009 |  |  |  | 0 |  | 1 | CAPACITY | AB1-127 |  |  | 0.1
237002 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.02009 |  |  |  | 0 |  | 1 | CAPACITY | AB1-128 |  |  | 0.1
945012 | AF1-166 E | 34.5 | 201 | 75 | 0 | 6.4 | 0.47 |  |  | -0.02009 |  |  |  | 0 |  | 1 | NEW | AF1-166 |  |  | 0.1
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | -0.02011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 50 | 30.74 |  |  | -0.02011 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1330 |  |  | -0.02011 |  |  |  | 0 |  | 1 | CAPACITY | AMG3 |  |  | 1
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 800 |  |  | -0.02011 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 19.81 |  |  | -0.02016 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 2.01 |  |  | -0.02018 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 0.1
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 1.23 |  |  | -0.02018 |  |  |  | 0 |  | 1 | NEW | AC1-048 |  |  | 0.1
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 93.64 |  |  | -0.02022 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208904 | HOLT 696 | 13.2 | 229 | 60 | 16 | 58.4 | 41.06 |  |  | -0.02022 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208903 | HOLT 695 | 13.2 | 229 | 60 | 19 | 53.2 | 37.4 |  |  | -0.02022 |  |  |  | 0.38928 |  | 1 | CAPACITY |  |  |  | 1
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 0.45 |  |  | -0.02022 |  |  |  | 0 |  | 1 | CAPACITY | V4-027 |  |  | 0.1
208254 | AF2-280 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02022 |  |  |  | 0 |  | 1 | NEW | AF2-280 |  |  | 0.1
208474 | KINZ 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02022 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208253 | AF2-280 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02022 |  |  |  | 0 |  | 1 | MTX | AF2-280 |  |  | 1
916007 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 0.1 | 0.06 |  |  | -0.02022 |  |  |  | 0 |  | 1 | NEW | V4-027 |  |  | 0.1
208769 | SISO | 12.5 | 229 | 2 | 2.5 | 1.6 | 0 |  |  | -0.02029 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
208876 | WLAN | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02029 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 80.49 |  |  | -0.0203 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 68.19 |  |  | -0.0203 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 53.78 |  |  | -0.0203 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 45.34 |  |  | -0.0203 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 44.99 |  |  | -0.0203 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
209030 | FRFA O01 | 12.5 | 229 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02031 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
208527 | AF2-279 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02031 |  |  |  | 0 |  | 1 | NEW | AF2-279 |  |  | 0.1
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 2 | 1.22 |  |  | -0.02031 |  |  |  | 0 |  | 1 | NEW | V3-051 |  |  | 0.8
208526 | AF2-279 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02031 |  |  |  | 0 |  | 1 | MTX | AF2-279 |  |  | 1
205916 | AD1-020_C | 0.6 | 227 | 75 | 0 | 54 | 4.99 |  |  | -0.02033 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 0.1
205917 | AD1-020 ES | 0.55 | 227 | 75 | 0 | 21.5 | 1.99 |  |  | -0.02033 |  |  |  | 0 |  | 1 | NEW | AD1-020 |  |  | 0.1
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 20.5 | 11.03 |  |  | -0.02033 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205922 | AF2-268 E | 115 | 227 | 75 | 0 | 2 | 0.19 |  |  | -0.02033 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 205.47 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 120.48 |  |  | -0.02033 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA2 |  |  | 1
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 103.81 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | -0.02033 |  |  |  | 0.036 |  | 1 | CAPACITY | DELTA |  |  | 1
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 67.23 |  |  | -0.02033 |  |  |  | 0 |  | 1 | CAPACITY | DELTA |  |  | 1
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1288.2 |  |  | -0.02034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1307 |  |  | -0.02034 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 247.42 |  |  | -0.02035 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | -0.02035 |  |  |  | 0 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 143.07 |  |  | -0.02035 |  |  |  | 0.036 |  | 1 | CAPACITY | Y1-065 |  |  | 1
200055 | ROCKSP 4 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200054 | ROCKSP 3 | 18 | 235 | 57 | 147 | 169 | 90.9 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200052 | ROCKSP 1 | 18 | 235 | 57 | 145.7 | 167.5 | 90.09 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200053 | ROCKSP 2 | 18 | 235 | 57 | 144.9 | 166.5 | 89.56 |  |  | -0.02035 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 64 | 34.42 |  |  | -0.02034 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 188.4 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 187.7 |  |  | -0.02035 |  |  |  | 0.05366 |  | 1 | CAPACITY |  |  |  | 1
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 91.39 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 67.49 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 59.05 |  |  | -0.02036 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 33.74 |  |  | -0.02036 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 171.69 |  |  | -0.02037 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | -0.02037 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 89.82 |  |  | -0.02037 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 89.82 |  |  | -0.02037 |  |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN |  |  | 1
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 20.6 | 11.08 |  |  | -0.02037 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 40.5 | 21.78 |  |  | -0.02038 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.02038 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 33.02 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY | P.H. GLATFELTER_IPP |  |  | 1
205920 | AF2-101 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY | AF2-101 |  |  | 0.1
958072 | AF2-101 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02039 |  |  |  | 0 |  | 1 | NEW | AF2-101 |  |  | 0.1
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 41.2 | 22.16 |  |  | -0.02039 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0.77 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | W1-045 |  |  | 0.1
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.1 | 0.47 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | W1-045 |  |  | 0.1
204555 | 27QUEEN ST | 115 | 227 | 75 | 0 | 5 | 0.46 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
205921 | AF2-151 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY | AF2-151 |  |  | 0.1
958602 | AF2-151 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02039 |  |  |  | 0 |  | 1 | NEW | AF2-151 |  |  | 0.1
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.77 |  |  | -0.02039 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | -0.02041 |  |  |  | 0.036 |  | 1 | NEW | Garrison |  |  | 1
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 2.83 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 103.81 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 102.2 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 8.6 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AA1-102 |  |  | 0.1
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 111.97 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AB1-056 |  |  | 0.8
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 1.28 |  |  | -0.0204 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.0204 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2 |  |  | 1
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 62.5 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Garrison |  |  | 1
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 5.27 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AA1-102 |  |  | 0.1
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232915 | OH NUG4 | 13.8 | 235 | 53 | 38.9 | 44.7 | 0.83 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 0.82 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233935 | AB2-179 C | 0.38 | 235 | 75 | 0 | 37.6 | 3.48 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-179 |  |  | 0.1
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 38.35 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
924802 | AB2-133 E | 69 | 235 | 75 | 0 | 31.2 | 2.89 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-133 |  |  | 0.1
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 30.66 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 29.58 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233906 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 39.32 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AB1-056 |  |  | 0.8
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 388.63 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 26.36 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233939 | AB2-133 C | 69 | 235 | 75 | 0 | 24.6 | 2.28 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-133 |  |  | 0.1
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 25.82 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232901 | NORTHST | 69 | 235 | 56 | 5 | 45 | 24.2 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 23.67 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 16.08 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233930 | AB2-032 GEN | 0.6 | 235 | 75 | 0 | 13.6 | 1.26 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-032 |  |  | 0.1
232905 | CHERITON_25 | 24.9 | 235 | 65 | 0 | 12.5 | 0.23 |  |  | -0.02041 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB1-142 |  |  | 0.1
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 1.25 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB1-141 |  |  | 0.1
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-003 |  |  | 0.1
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-004 |  |  | 0.1
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-005 |  |  | 0.1
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 1.24 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | W1-006 |  |  | 0.1
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-179 |  |  | 0.1
923925 | AB2-153 E | 0.6 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-153 |  |  | 0.1
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | X3-008 |  |  | 0.1
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-004 |  |  | 0.1
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-005 |  |  | 0.1
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-006 |  |  | 0.1
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | W1-003 |  |  | 0.1
917082 | Z2-012 E | 69 | 235 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Z2-012 |  |  | 0.1
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0.86 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Y3-058 |  |  | 0.1
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 9.57 |  |  | -0.0204 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 8.9 | 0.82 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Y3-058 |  |  | 0.1
232920 | IR10 | 13.2 | 235 | 55 | 14 | 16.1 | 8.66 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
233933 | AB2-153 GEN | 0.6 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AB2-153 |  |  | 0.1
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | X3-008 |  |  | 0.1
233901 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 0.7 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Z2-012 |  |  | 0.1
232919 | VN10 | 13.2 | 235 | 55 | 0 | 14.3 | 7.69 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
923928 | AB2-032 E | 0.6 | 235 | 75 | 0 | 6.4 | 0.59 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB2-032 |  |  | 0.1
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB1-142 |  |  | 0.1
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0.58 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AB1-141 |  |  | 0.1
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0.57 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | Y1-079 |  |  | 0.1
925262 | AB2-180 E | 0.38 | 235 | 75 | 0 | 6 | 0.56 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AB2-180 |  |  | 0.1
233942 | AB2-180 C | 0.38 | 235 | 75 | 0 | 14 | 8.72 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AB2-180 |  |  | 0.1
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 0.39 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AB1-137 |  |  | 0.1
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 6.23 |  |  | -0.02041 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0.37 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | X1-032 |  |  | 0.1
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Z2-076 |  |  | 0.1
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 0.37 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Z2-077 |  |  | 0.1
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 20.25 |  |  | -0.0204 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 0.35 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | Y1-079 |  |  | 0.1
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0.34 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | X3-066 |  |  | 0.1
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 3.08 | 0.28 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | X3-066 |  |  | 0.1
960882 | AF2-379 E | 69 | 235 | 75 | 0 | 2.26 | 0.21 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AF2-379 |  |  | 0.1
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0.19 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Y1-080 |  |  | 0.1
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Z2-077 |  |  | 0.1
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0.19 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | Z2-076 |  |  | 0.1
205930 | AF2-099 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AF2-099 |  |  | 0.1
205931 | AF2-100 C | 115 | 227 | 75 | 0 | 1.8 | 0.17 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY | AF2-100 |  |  | 0.1
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02041 |  |  |  | 0 |  | 1 | NEW | AB1-137 |  |  | 0.1
233940 | AF2-379 C | 69 | 235 | 75 | 0 | 1.64 | 0.15 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | AF2-379 |  |  | 0.1
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 0.12 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Y1-080 |  |  | 0.1
958052 | AF2-099 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AF2-099 |  |  | 0.1
958062 | AF2-100 E | 115 | 227 | 75 | 0 | 1.2 | 0.11 |  |  | -0.0204 |  |  |  | 0 |  | 1 | NEW | AF2-100 |  |  | 0.1
233900 | O-025 C | 25 | 235 | 64 | 0 | 6 | 5.11 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 14.34 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.23 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.55 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.21 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 30 |  |  | -0.0204 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.02041 |  |  |  | 0.036 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 67.23 |  |  | -0.02041 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 12.37 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 12.32 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 164.17 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 9.25 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 7.64 |  |  | -0.02041 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 81.14 |  |  | -0.02041 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 8.32 |  |  | -0.02042 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 99.67 |  |  | -0.02042 |  |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1 |  |  | 1
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 13.36 |  |  | -0.02043 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
213893 | PHLISST1 | 20 | 230 | 58 | 232.3 | 267 | 143.61 |  |  | -0.02043 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | -0.02043 |  |  |  | 0.036 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | -0.02043 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 97.89 |  |  | -0.02043 |  |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND |  |  | 1
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1178.3 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 1145.8 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 1138.9 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | -0.02044 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 7.03 |  |  | -0.02044 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 222.4 | 119.62 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | -0.02044 |  |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 166.9 | 89.77 |  |  | -0.02044 |  |  |  | 0.036 |  | 1 | CAPACITY | LIBERTY EDDY |  |  | 1
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 20.98 |  |  | -0.02044 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 18.29 |  |  | -0.02044 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.02045 |  |  |  | 0.1097 |  | 1 | ENERGY |  |  |  | 1
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 7.8 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | -0.02044 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 6.99 |  |  | -0.02045 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208885 | WNHO | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | -0.02045 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208697 | PRIN B34 | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | -0.02045 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 87.67 |  |  | -0.02045 |  |  |  | 0.036 |  | 1 | CAPACITY | GRAYS FERRY |  |  | 1
228203 | P06 | 13.8 | 234 | 57 | 78 | 89.7 | 48.25 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 45.99 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 45.13 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 34.26 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 57.7 | 31.03 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 57.6 | 30.98 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | PEDRICKTOWN PCLP |  |  | 1
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 30.66 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 29.85 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.1 | 39.2 | 21.08 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 20.22 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | -0.02045 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 226.44 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 206.63 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | -0.02045 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | -0.02045 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
228357 | V2-046E | 12.9 | 234 | 75 | 0 | 12.9 | 1.19 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V2-046 |  |  | 0.1
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.1 | 12.43 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
228471 | VALERO1 | 13.8 | 234 | 58 | 19.1 | 22 | 11.83 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | Valero |  |  | 1
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 0.72 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V2-046 |  |  | 0.1
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V4-054 |  |  | 0.1
228473 | VALERO3 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228484 | VALERO4 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228472 | VALERO2 | 13.8 | 234 | 58 | 0 | 10 | 5.38 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Valero |  |  | 1
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V4-054 |  |  | 0.1
228712 | V2-041E | 13.2 | 234 | 75 | 0 | 2.48 | 0.23 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V2-041 |  |  | 0.1
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V2-041 |  |  | 0.1
228721 | V2-035E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V2-035 |  |  | 0.1
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.07 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V2-035 |  |  | 0.1
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 3 | 2.55 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 75 |  |  | -0.02045 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 181.64 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | Q90 |  |  | 1
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 108.33 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Q90 |  |  | 1
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 72.2 | 83 | 44.64 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 43.08 |  |  | -0.02046 |  |  |  | 0.036 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
227801 | ONTC&DCT | 13.8 | 234 | 75 | 33.6 | 38.6 | 3.57 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 35.07 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH |  |  | 1
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | -0.02047 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | -0.02047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 26.36 |  |  | -0.02047 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 22.59 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 16.14 |  |  | -0.02046 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 16.14 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT |  |  | 1
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 13.98 |  |  | -0.02046 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 16.18 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | -0.02046 |  |  |  | 0.30476 |  | 1 | ENERGY |  |  |  | 1
219913 | AD2-042 E | 26.4 | 231 | 75 | 0 | 8.2 | 0.76 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AD2-042 |  |  | 0.1
924052 | AB2-049 E | 69 | 234 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AB2-049 |  |  | 0.1
219915 | AD2-027 E | 26.4 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AD2-027 |  |  | 0.1
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | -0.02046 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0.56 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | W2-030 |  |  | 0.1
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0.53 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | W1-130 |  |  | 0.1
219912 | AD2-042 C | 26.4 | 231 | 75 | 0 | 5 | 0.46 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AD2-042 |  |  | 0.1
214030 | WAYNEJCT | 13.8 | 230 | 29 | 0 | 8.8 | 4.73 |  |  | -0.02046 |  |  |  | 0.19754 |  | 1 | CAPACITY |  |  |  | 1
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.2 | 7.55 |  |  | -0.02046 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 0.1
219914 | AD2-027 C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AD2-027 |  |  | 0.1
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 0.34 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | W2-030 |  |  | 0.1
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | W1-130 |  |  | 0.1
219765 | PARADISE E | 13 | 231 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | U4-036 |  |  | 0.1
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | Y2-081 |  |  | 0.1
230408 | AD2-065 E | 12.9 | 234 | 75 | 0 | 3.03 | 0.28 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AD2-065 |  |  | 0.1
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0.28 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | X3-075 |  |  | 0.1
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Y2-081 |  |  | 0.1
230414 | AF1-041 E | 69 | 234 | 75 | 0 | 2.4 | 0.22 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AF1-041 |  |  | 0.1
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0.22 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | Y3-087 |  |  | 0.1
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 0.21 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | Y3-087 |  |  | 0.1
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | MTX | X2-013 |  |  | 1
219904 | AC1-010 C | 26.4 | 231 | 75 | 0 | 2.2 | 0.2 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AC1-010 |  |  | 0.1
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | U4-036 |  |  | 0.1
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0.16 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | W2-071 |  |  | 0.1
227928 | V4-067E | 12.9 | 234 | 75 | 0 | 1.6 | 0.15 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | V4-067 |  |  | 0.1
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.55 | 0.14 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AC1-030 |  |  | 0.1
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0.13 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AB1-001 |  |  | 0.1
219921 | AF1-264 | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | X3-075 |  |  | 0.1
230410 | AE1-218 E O1 | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AE1-218 |  |  | 0.1
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | AB2-122 |  |  | 0.1
230415 | AB2-049 C | 69 | 234 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AB2-049 |  |  | 0.1
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.02047 |  |  |  | 0 |  | 1 | MTX | Z1-082 |  |  | 1
230407 | AD2-065_C | 12.9 | 234 | 75 | 0 | 1.08 | 0.1 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AD2-065 |  |  | 0.1
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.1 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | W2-071 |  |  | 0.1
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.09 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | V4-067 |  |  | 0.1
219907 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AC1-030 |  |  | 0.1
219138 | THOSOLAR E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | -0.02046 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.08 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AB1-001 |  |  | 0.1
230403 | AB1-116 E | 12.9 | 234 | 28 | 0 | 0.78 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
228733 | AB1-119 E | 12.9 | 234 | 28 | 0 | 0.73 | 0 |  |  | -0.02046 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
230409 | AE1-218 C O1 | 12.9 | 234 | 75 | 0 | 0.8 | 0.07 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AE1-218 |  |  | 0.1
930243 | AB1-063_E | 69 | 231 | 0 | 0 | 0 | -0.7 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.65 | 3.95 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
230413 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.06 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | AB2-122 |  |  | 0.1
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | Y1-075 |  |  | 0.1
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0.05 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | X1-071 |  |  | 0.1
228014 | PVILLEG | 0.48 | 234 | 65 | 0 | 1.3 | 0.77 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219137 | THOSOLAR C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
219917 | AB1-063 E | 69 | 231 | 75 | 0 | 0.4 | 0.04 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | Y1-075 |  |  | 0.1
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.03 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | X1-071 |  |  | 0.1
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.7 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.43 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 28 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 1122.1 |  |  | -0.02046 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 1119.7 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 256.8 | 138.13 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 137.8 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 184.6 | 99.29 |  |  | -0.02048 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill B |  |  | 1
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | -0.02048 |  |  |  | 0.036 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 98.92 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Ford Mill A |  |  | 1
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 27.43 |  |  | -0.02048 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 26.36 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 25.82 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 345.42 |  |  | -0.02047 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris2 |  |  | 1
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 37.2 | 42.75 | 22.99 |  |  | -0.02048 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
213798 | MERCK 3 | 13.8 | 230 | 29 | 13 | 42 | 22.59 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 291.92 |  |  | -0.02047 |  |  |  | 0.1042 |  | 1 | CAPACITY | Bris1 |  |  | 1
213797 | MERCK 2 | 13.8 | 230 | 29 | 4 | 32 | 17.21 |  |  | -0.02048 |  |  |  | 0.1042 |  | 1 | CAPACITY | WEST POINT COGEN_1 |  |  | 1
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | W3-080 |  |  | 0.1
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0.63 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | W2-056 |  |  | 0.1
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | W4-103 |  |  | 0.1
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0.4 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | W2-102 |  |  | 0.1
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 0.39 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | W2-056 |  |  | 0.1
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.02048 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | Y3-026 |  |  | 0.1
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | Y3-026 |  |  | 0.1
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 0.34 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | W3-080 |  |  | 0.1
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 3.56 | 0.33 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | W4-103 |  |  | 0.1
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 0.25 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | W2-102 |  |  | 0.1
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0.21 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AC1-017 |  |  | 0.1
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0.2 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | X1-070 |  |  | 0.1
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AB1-025 S |  |  | 0.1
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0.19 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | AB1-025 N |  |  | 0.1
208580 | MGTN 2 | 12.5 | 229 | 77 | 0 | 4.8 | 2.98 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0.17 |  |  | -0.02047 |  |  |  | 0 |  | 1 | NEW | V4-005 |  |  | 0.1
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 2.75 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219906 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AC1-017 |  |  | 0.1
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 S |  |  | 0.1
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | AB1-025 N |  |  | 0.1
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 0.12 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY | T20 |  |  | 0.1
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | X1-070 |  |  | 0.1
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY | V4-005 |  |  | 0.1
219685 | NATIONAL_GYP | 26 | 231 | 77 | 0 | 2.8 | 1.89 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
916010 | T20SOLAR E | 0.5 | 230 | 75 | 0 | 2 | 1.22 |  |  | -0.02048 |  |  |  | 0 |  | 1 | NEW | T20 |  |  | 0.1
219922 | AF1-261 | 26.4 | 231 | 75 | 0 | 0.9 | 0.61 |  |  | -0.02048 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 0.1
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 749 |  |  | -0.02047 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W2-082 |  |  | 0.1
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W4-025 |  |  | 0.1
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W2-019 |  |  | 0.1
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-129 |  |  | 0.1
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W2-082 |  |  | 0.1
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | X4-015 |  |  | 0.1
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 0.24 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W4-025 |  |  | 0.1
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 0.21 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W2-019 |  |  | 0.1
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-129 |  |  | 0.1
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | X4-015 |  |  | 0.1
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 260.87 |  |  | -0.02049 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
204662 | 27AES GEN1 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | -0.0205 |  |  |  | 0.036 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204663 | 27AES GEN2 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
204664 | 27AES GEN3 | 16 | 227 | 58 | 226.2 | 260 | 139.85 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | IRONWOOD |  |  | 1
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.0205 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 90.42 |  |  | -0.0205 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 76.9 | 88.4 | 47.55 |  |  | -0.0205 |  |  |  | 0.036 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 47.49 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD |  |  | 1
207179 | 28SIXFLAGS | 34.5 | 228 | 77 | 0 | 17 | 0 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 18.29 |  |  | -0.02049 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 32.1 | 17.27 |  |  | -0.0205 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 16.67 |  |  | -0.02049 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
939122 | AE1-142 E O1 | 34.5 | 228 | 75 | 0 | 11.8 | 1.09 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AE1-142 |  |  | 0.1
218780 | PRINCENTON_U | 26 | 231 | 77 | 0 | 31.56 | 21.27 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
207459 | AE1-142 C O1 | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AE1-142 |  |  | 0.1
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0.75 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | Z2-102 |  |  | 0.1
923293 | AB1-138 E | 0.36 | 228 | 75 | 0 | 6 | 0.56 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AB1-138 |  |  | 0.1
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-120 |  |  | 0.1
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0.5 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-119 |  |  | 0.1
207450 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 0.46 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | Z2-102 |  |  | 0.1
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0.45 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | Z1-096 |  |  | 0.1
206280 | 28LAKEHURS | 34.5 | 228 | 55 | 0 | 13.7 | 10.22 |  |  | -0.0205 |  |  |  | 0.17131 |  | 1 | CAPACITY |  |  |  | 1
207445 | AB1-138 C | 0.38 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AB1-138 |  |  | 0.1
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-119 |  |  | 0.1
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 0.31 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-120 |  |  | 0.1
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | X1-085 |  |  | 0.1
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 0.28 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | Z1-096 |  |  | 0.1
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0.23 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-121 Z |  |  | 0.1
219728 | YARDVSOLFA E | 13.2 | 231 | 75 | 0 | 2.42 | 0.22 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.02049 |  |  |  | 0 |  | 1 | MTX | AA1-060 |  |  | 1
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | X1-085 |  |  | 0.1
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Y |  |  | 0.1
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | W1-121 Z |  |  | 0.1
219727 | YARDVSOLFA C | 13.2 | 231 | 75 | 0 | 1.48 | 0.14 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
219622 | TRENT_BIOGAS | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -0.02049 |  |  |  | 0 |  | 1 | NEW | W1-121 Y |  |  | 0.1
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 30 |  |  | -0.02049 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 43.9 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 134.03 |  |  | -0.02051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.02051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 13.18 |  |  | -0.02051 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.02051 |  |  |  | 0.0975 |  | 1 | MTX | AA1-100 |  |  | 1
207454 | AA2-184 E | 34.5 | 228 | 75 | 0 | 11.6 | 1.07 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | BenMoreell |  |  | 0.1
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0.98 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | X1-037 |  |  | 0.1
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-124 |  |  | 0.1
207464 | AF1-023 | 34.5 | 228 | 75 | 0 | 8.4 | 0.78 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | BenMoreell |  |  | 0.1
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0.76 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AC1-207 |  |  | 0.1
207451 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -0.0205 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0.52 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W2-078 |  |  | 0.1
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0.46 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-113 |  |  | 0.1
207420 | AC1-207 TAP | 34.5 | 228 | 75 | 0 | 4.9 | 0.45 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AC1-207 |  |  | 0.1
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0.41 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | W3-079 |  |  | 0.1
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 0.39 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | X1-037 |  |  | 0.1
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0.36 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 3 |  |  | 0.1
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-124 |  |  | 0.1
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | W3-079 |  |  | 0.1
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | Y2-051 |  |  | 0.1
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W2-078 |  |  | 0.1
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 3.23 |  |  | -0.0205 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
205925 | AF2-428 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-428 |  |  | 0.1
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 0.26 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-113 |  |  | 0.1
901032 | W1-024E OP1 | 34.5 | 228 | 75 | 0 | 2.5 | 0.23 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-024 |  |  | 0.1
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 0.22 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 3 |  |  | 0.1
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0.22 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 4 |  |  | 0.1
219679 | NRGCENTER E | 13.2 | 231 | 55 | 0 | 2 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | X4-031 |  |  | 0.1
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | Y2-051 |  |  | 0.1
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | W1-032 |  |  | 0.1
940922 | AE2-081 E | 34.5 | 228 | 75 | 0 | 1.75 | 0.16 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AE2-081 |  |  | 0.1
207460 | AE2-056 C | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AE2-056 |  |  | 0.1
207463 | AE2-081 C | 34.5 | 228 | 75 | 0 | 1.57 | 0.14 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AE2-081 |  |  | 0.1
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 0.14 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-024 |  |  | 0.1
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 4 |  |  | 0.1
940692 | AE2-056 E | 34.5 | 228 | 75 | 0 | 1.4 | 0.13 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AE2-056 |  |  | 0.1
219650 | TRENT_COLLEG | 26 | 231 | 77 | 0 | 3.75 | 2.53 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.0205 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | W1-032 |  |  | 0.1
219818 | TRENTONSOL E | 13.2 | 231 | 75 | 0 | 0.93 | 0.09 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 5 | 4.26 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0.07 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 0.1
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0.06 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AA2-058 |  |  | 0.1
219817 | TRENTONSOL C | 13.2 | 231 | 75 | 0 | 0.57 | 0.05 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
940702 | AE2-057 E | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AE2-057 |  |  | 0.1
207461 | AE2-057 C | 34.5 | 228 | 75 | 0 | 0.5 | 0.05 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | AE2-057 |  |  | 0.1
932032 | AC2-009 E | 69 | 231 | 75 | -0.5 | 0.49 | 0.05 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | AC2-009 |  |  | 0.1
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0.04 |  |  | -0.0205 |  |  |  | 0 |  | 1 | NEW | W4-058 |  |  | 0.1
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.7 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AA2-058 |  |  | 0.1
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | W4-058 |  |  | 0.1
207419 | AB2-139 E | 34.5 | 228 | 76 | -0.2 | 0.21 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AB2-139 |  |  | 1
961373 | AF2-428 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-428 |  |  | 1
219918 | AC2-009 C | 69 | 231 | 75 | -0.1 | 0.1 | 0.01 |  |  | -0.0205 |  |  |  | 0 |  | 1 | CAPACITY | AC2-009 |  |  | 0.1
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0205
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 164.59 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 133.39 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 112.68 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | RARITAN RIVER |  |  | 1
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 102.41 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 102.41 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 94.67 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | RED OAK |  |  | 1
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 94.67 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | RED OAK |  |  | 1
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 93.75 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE |  |  | 1
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 99.6 | 114.5 | 61.59 |  |  | -0.02052 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 93.2 | 107.1 | 57.61 |  |  | -0.02052 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
206327 | 28S RIV G1 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | S RIV |  |  | 1
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 53.73 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 85.3 | 98 | 52.71 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | S RIV |  |  | 1
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 29.23 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 29.23 |  |  | -0.02052 |  |  |  | 0.036 |  | 1 | CAPACITY | PARLIN NUG |  |  | 1
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | W2-050 |  |  | 0.1
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W4-060 |  |  | 0.1
924132 | AB2-057 E | 26 | 231 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | AB2-057 |  |  | 0.1
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 75.48 |  |  | -0.02051 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
219903 | AB2-057 C | 26 | 231 | 75 | 0 | 3.8 | 0.35 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | AB2-057 |  |  | 0.1
205926 | AF2-429 E | 34.5 | 227 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-429 |  |  | 0.1
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W4-060 |  |  | 0.1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V3-024 |  |  | 0.1
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 2 |  |  | 0.1
210323 | AF2-286 E | 13.8 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-286 |  |  | 0.1
205923 | AF2-272 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-272 |  |  | 0.1
205927 | AF2-430 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-430 |  |  | 0.1
205924 | AF2-281 E | 69 | 227 | 75 | 0 | 3 | 0.28 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | AF2-281 |  |  | 0.1
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0.23 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W1-112 |  |  | 0.1
217198 | V3-058 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | V3-058 |  |  | 0.1
217199 | V3-059 E | 26.4 | 231 | 75 | 0 | 2 | 0.19 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | V3-059 |  |  | 0.1
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V3-024 |  |  | 0.1
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 0.17 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 2 |  |  | 0.1
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0.16 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | W3-124 |  |  | 0.1
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0.14 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | V2-009 1 |  |  | 0.1
218455 | CINNBAY_CGEN | 26.4 | 231 | 64 | 0 | 9 | 7.66 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0.13 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW | X2-088 |  |  | 0.1
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.17 | 0.11 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W1-112 |  |  | 0.1
205928 | AF2-431 E | 69 | 227 | 75 | 0 | 1.17 | 0.11 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | AF2-431 |  |  | 0.1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.1 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | W3-124 |  |  | 0.1
218781 | BRIS_MYERS | 26 | 231 | 77 | 0 | 3 | 2.02 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.09 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | V2-009 1 |  |  | 0.1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.02051 |  |  |  | 0 |  | 1 | CAPACITY | X2-088 |  |  | 0.1
208348 | EELI | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02051 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210022 | LING 2 | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
210322 | AF2-286 BAT | 13.8 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-286 |  |  | 1
959813 | AF2-272 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-272 |  |  | 1
961383 | AF2-429 BAT | 34.5 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-429 |  |  | 1
961393 | AF2-430 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-430 |  |  | 1
959903 | AF2-281 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02051 |  |  |  | 0 |  | 1 | MTX | AF2-281 |  |  | 1
961403 | AF2-431 BAT | 69 | 227 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02052 |  |  |  | 0 |  | 1 | MTX | AF2-431 |  |  | 1
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 0 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | NEW |  |  |  | 1
219001 | SEWAREN7GT | 25 | 231 | 58 | 0 | 324.6 | 174.59 |  |  | -0.02053 |  |  |  | 0.036 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
219002 | SEWAREN7ST | 18 | 231 | 58 | 0 | 216.4 | 116.4 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | Sewaren7 |  |  | 1
208947 | WSHO CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208942 | HARR CT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | -0.02052 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.02053 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.02053 |  |  |  | 0 |  | 1 | ENERGY | Sewaren7 |  |  | 1
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W3-029 |  |  | 0.1
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0.93 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W3-003 |  |  | 0.1
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 7.45 |  |  | -0.02052 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0.46 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | V3-070 |  |  | 0.1
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0.38 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 0.1
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0.38 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AB1-139 |  |  | 0.1
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | X2-075 |  |  | 0.1
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AE1-156 |  |  | 0.1
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W3-029 |  |  | 0.1
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | V3-070 |  |  | 0.1
219908 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 0.23 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | AB1-139 |  |  | 0.1
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 0.21 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | X2-075 |  |  | 0.1
219916 | AD2-025 E | 13.2 | 231 | 76 | -2 | 2 | 0 |  |  | -0.02052 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
936193 | AD2-025_E | 13.2 | 231 | 76 | 0 | 2 | 0 |  |  | -0.02052 |  |  |  | 0 |  | 1 | MTX | AD2-025 |  |  | 1
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W1-132 |  |  | 0.1
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | V4-070 |  |  | 0.1
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-061 |  |  | 0.1
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | V4-069 |  |  | 0.1
217212 | AMBOY SO E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | V3-069 |  |  | 0.1
218527 | CNTRALGAS2 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
218525 | CNTRALGAS1 E | 13.2 | 231 | 75 | 0 | 1.42 | 0.13 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0.12 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | X2-089 |  |  | 0.1
218526 | CNTRALGAS2 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
218524 | CNTRALGAS1 C | 13.2 | 231 | 75 | 0 | 1.18 | 0.11 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | V4-069 |  |  | 0.1
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | V4-070 |  |  | 0.1
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-061 |  |  | 0.1
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | AE1-041 |  |  | 0.1
217213 | AMBOY SO C | 13.2 | 231 | 75 | 0 | 0.9 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | V3-069 |  |  | 0.1
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.07 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | X2-089 |  |  | 0.1
219920 | AE1-041 EBAT | 26.4 | 231 | 76 | -0.5 | 0.5 | 0 |  |  | -0.02053 |  |  |  | 0 |  | 1 | MTX | AE1-041 |  |  | 1
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0.04 |  |  | -0.02052 |  |  |  | 0 |  | 1 | NEW | W2-036 |  |  | 0.1
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0.03 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-052 |  |  | 0.1
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY | W2-036 |  |  | 0.1
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-052 |  |  | 0.1
219919 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.02 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | AE1-041 |  |  | 0.1
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 10.2 |  |  | -0.02052 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0205
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 302.3 | 162.6 |  |  | -0.02053 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 302.1 | 162.49 |  |  | -0.02053 |  |  |  | 0.036 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
990902 | TOSCO_E | 18 | 231 | 2 | 0 | 137.5 | 0 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | ENERGY | Tosco |  |  | 1
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 139.31 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 135.65 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 119.95 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET |  |  | 1
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 113.38 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 96.22 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 96.22 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN2 |  |  | 1
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 176.2 | 94.77 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1 |  |  | 1
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 176 | 94.67 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2 |  |  | 1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 64.44 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | BERGEN1 |  |  | 1
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 50.99 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.66 | 50.91 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.2 | 47.98 |  |  | -0.02054 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 46.26 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 45.24 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 72.1 | 82.9 | 44.59 |  |  | -0.02053 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 43.57 |  |  | -0.02054 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 25.52 |  |  | -0.02053 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | -0.02054 |  |  |  | 0.036 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 37.4 | 43 | 23.13 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
218344 | TOSCO_G6 | 18 | 231 | 2 | 37 | 42.5 | 22.86 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | CAPACITY | Tosco |  |  | 1
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 18.4 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY |  |  | 1
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 25.21 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-016 |  |  | 0.1
218672 | KENILWRTH E | 26.4 | 231 | 65 | 0 | 8 | 0 |  |  | -0.02053 |  |  |  | 0.1097 |  | 1 | NEW |  |  |  | 1
217831 | PB_NUTCLIF | 26 | 231 | 77 | 0 | 10.7 | 7.21 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217850 | MONTCLAIR_U | 26 | 231 | 77 | 0 | 10.6 | 7.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
217825 | UMD_NJ | 26 | 231 | 77 | 0 | 10.5 | 7.08 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 3.55 |  |  | -0.02053 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0.29 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V2-025 |  |  | 0.1
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 0.28 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-016 |  |  | 0.1
211089 | AF2-277 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | AF2-277 |  |  | 0.1
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217194 | REDH C | 13 | 231 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V2-025 |  |  | 0.1
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | W4-059 |  |  | 0.1
219910 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0.14 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
218450 | LINSOLAR E | 26.4 | 231 | 75 | 0 | 1.43 | 0.13 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | v1-030 |  |  | 0.1
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0.11 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W2-080 |  |  | 0.1
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.24 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
218449 | LINSOLAR C | 26.4 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | v1-030 |  |  | 0.1
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0.08 |  |  | -0.02053 |  |  |  | 0 |  | 1 | NEW | W1-101 |  |  | 0.1
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W2-080 |  |  | 0.1
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0.06 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | AB1-021 |  |  | 0.1
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0.06 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | X2-087 |  |  | 0.1
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0.06 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | X1-072 |  |  | 0.1
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.05 |  |  | -0.02053 |  |  |  | 0 |  | 1 | CAPACITY | W1-101 |  |  | 0.1
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0.05 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-067 |  |  | 0.1
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | X2-087 |  |  | 0.1
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.04 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | X1-072 |  |  | 0.1
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-065 |  |  | 0.1
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | AB1-021 |  |  | 0.1
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-067 |  |  | 0.1
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-066 |  |  | 0.1
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0.03 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | V3-068 |  |  | 0.1
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.02 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | W4-059 |  |  | 0.1
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.02 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-065 |  |  | 0.1
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-068 |  |  | 0.1
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.01 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | V3-066 |  |  | 0.1
211088 | AF2-277 BAT | 69 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02054 |  |  |  | 0 |  | 1 | MTX | AF2-277 |  |  | 1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 30.15 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 68.31 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
200044 | BETH CT1 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | -0.02055 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH1234 |  |  | 1
200048 | BETH CT5 | 13.8 | 229 | 58 | 102.7 | 118 | 63.47 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | BETH5678 |  |  | 1
207466 | AF1-324 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.02055 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207458 | AD2-210_C | 34.5 | 228 | 76 | 0 | 8 | 0 |  |  | -0.02054 |  |  |  | 0.05 |  | 1 | NEW |  |  |  | 1
AD2-210 | BATEXP_AD2-210->PJM |  |  | LTF |  | 8 |  |  |  | -0.0205
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0.19 |  |  | -0.02055 |  |  |  | 0 |  | 1 | NEW | V4-001 |  |  | 0.1
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0.17 |  |  | -0.02054 |  |  |  | 0 |  | 1 | NEW | X1-095 |  |  | 0.1
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02054 |  |  |  | 0 |  | 1 | CAPACITY | X1-095 |  |  | 0.1
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.07 |  |  | -0.02055 |  |  |  | 0 |  | 1 | CAPACITY | V4-001 |  |  | 0.1
207456 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.02055 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 153 | 82.29 |  |  | -0.02056 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 91.3 | 105 | 56.48 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 89.6 | 103 | 55.4 |  |  | -0.02056 |  |  |  | 0.036 |  | 1 | CAPACITY | GILBERT |  |  | 1
206341 | 28GIL 8 | 13.8 | 228 | 58 | 82.2 | 94.5 | 50.83 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | GILBERT |  |  | 1
207403 | 28AA2-082 E | 34.5 | 228 | 76 | -18 | 18 | 0 |  |  | -0.02056 |  |  |  | 0.05 |  | 1 | MTX | AA2-082 |  |  | 1
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 1.15 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W3-044 |  |  | 0.1
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX | AA2-061 |  |  | 1
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 0.7 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W3-044 |  |  | 0.1
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX | AA2-060 |  |  | 1
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-046 |  |  | 0.1
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0.57 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | X1-012 |  |  | 0.1
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0.57 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | BeaverRun |  |  | 0.1
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0.43 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W3-110 |  |  | 0.1
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0.4 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AD2-070 |  |  | 0.1
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | BeaverRun |  |  | 0.1
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 0.34 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | X1-012 |  |  | 0.1
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 0.32 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AD2-070 |  |  | 0.1
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 0.26 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W3-110 |  |  | 0.1
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 0.22 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-046 |  |  | 0.1
AA2-082 | BATEXP_AA2-082->PJM |  |  | LTF |  | 2 |  |  |  | -0.0206
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-097 |  |  | 0.1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0.15 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AC2-175 |  |  | 0.1
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0.12 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AE1-081 |  |  | 0.1
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-097 |  |  | 0.1
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.09 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AE1-081 |  |  | 0.1
207402 | 28AA2-082 C | 34.5 | 228 | 76 | 0 | 2 | 1.19 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AA2-082 |  |  | 1
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 104.89 |  |  | -0.02056 |  |  |  | 0.036 |  | 1 | CAPACITY | BETH5678 |  |  | 1
207470 | AF1-327 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
207468 | AF1-326 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.02056 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
204651 | 27PORT CT | 13.8 | 227 | 55 | 4 | 37 | 19.9 |  |  | -0.02057 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02057 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 0.1
206747 | 28DSM_X3-029 | 34.5 | 228 | 58 | 0 | 11.15 | 0 |  |  | -0.02056 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
207462 | AF1-133 C | 34.5 | 228 | 75 | 0 | 12 | 1.11 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | AF1-133 |  |  | 0.1
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0.97 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-073 |  |  | 0.1
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0.86 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W3-077 |  |  | 0.1
944682 | AF1-133 E | 34.5 | 228 | 75 | 0 | 8 | 0.74 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | AF1-133 |  |  | 0.1
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0.56 |  |  | -0.02057 |  |  |  | 0 |  | 1 | NEW | AD1-018 |  |  | 0.1
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.02056 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 0.33 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W2-091 |  |  | 0.1
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 3.2 | 0.3 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W3-077 |  |  | 0.1
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 3.04 | 0.28 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-073 |  |  | 0.1
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 3.8 | 2.04 |  |  | -0.02057 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W1-127 |  |  | 0.1
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0.18 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W4-064 |  |  | 0.1
916006 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 4.4 | 2.69 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | W2-091 |  |  | 0.1
916005 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 3.45 | 2.11 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | Y2-018 |  |  | 0.1
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0.12 |  |  | -0.02056 |  |  |  | 0 |  | 1 | NEW | U2-059 |  |  | 0.1
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.1 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W1-127 |  |  | 0.1
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.1 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | W4-064 |  |  | 0.1
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.07 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | U2-059 |  |  | 0.1
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.47 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 0.35 | 0.03 |  |  | -0.02056 |  |  |  | 0 |  | 1 | CAPACITY | Y2-018 |  |  | 0.1
207455 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.02056 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | -0.02058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 457.19 |  |  | -0.02058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 128.98 |  |  | -0.02058 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 107.57 |  |  | -0.02058 |  |  |  | 0.036 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 107.57 |  |  | -0.02058 |  |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL |  |  | 1
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 140.5 | 75.57 |  |  | -0.02057 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | -0.02058 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | -0.02058 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 98.42 |  |  | -0.02058 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
208946 | MACR CT | 12.5 | 229 | 55 | 61.4 | 70.6 | 37.97 |  |  | -0.02058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 21 | 11.3 |  |  | -0.02059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209945 | AF2-278 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02059 |  |  |  | 0 |  | 1 | NEW | AF2-278 |  |  | 0.1
209944 | AF2-278 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02059 |  |  |  | 0 |  | 1 | MTX | AF2-278 |  |  | 1
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 26.98 |  |  | -0.02059 |  |  |  | 0 |  | 1 | NEW | S14 |  |  | 0.8
208940 | ALLE CT | 12.5 | 229 | 55 | 48.7 | 56 | 30.12 |  |  | -0.02059 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 6.74 |  |  | -0.02059 |  |  |  | 0 |  | 1 | CAPACITY | S14 |  |  | 0.8
209007 | NOEN IPP | 13.8 | 229 | 12 | 96.9 | 111.4 | 105.11 |  |  | -0.0206 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
935072 | AD1-143 E1 | 69 | 229 | 74 | 0 | 34.28 | 20.93 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.8
211065 | PASP 1_2 C | 13.8 | 229 | 75 | 0 | 8 | 0.74 |  |  | -0.0206 |  |  |  | 0 |  | 1 | CAPACITY | AC1-087 |  |  | 0.1
926082 | PASP 1 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | U4-014 |  |  | 0.1
942581 | PASP 2 E | 13.8 | 229 | 75 | 0 | 5.8 | 0.54 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AC1-087 |  |  | 0.1
935071 | AD1-143 C1 | 69 | 229 | 75 | 0 | 5.72 | 0.53 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.1
935082 | AD1-143 E2 | 69 | 229 | 75 | 0 | 4.8 | 0.44 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.1
210319 | WCAR 1 | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02061 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
935081 | AD1-143 C2 | 69 | 229 | 75 | 0 | 0.2 | 0.02 |  |  | -0.0206 |  |  |  | 0 |  | 1 | NEW | AD1-143 |  |  | 0.1
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 124.2 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 72.8 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG1 |  |  | 1
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG2 |  |  | 1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 72.6 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG3 |  |  | 1
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG5 |  |  | 1
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 123.4 |  |  | -0.02061 |  |  |  | 0 |  | 1 | CAPACITY | KYG4 |  |  | 1
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 55.94 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | U2-073 A |  |  | 0.8
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 52.08 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 0.8
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 24.52 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | U2-073 B |  |  | 0.8
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 14.6 | 7.03 |  |  | -0.02062 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 A |  |  | 0.8
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 7.75 |  |  | -0.02062 |  |  |  | 0 |  | 1 | NEW | AA2-017 |  |  | 0.8
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 8.4 | 4.05 |  |  | -0.02062 |  |  |  | 0 |  | 1 | CAPACITY | U2-073 B |  |  | 0.8
208920 | WLPK | 12.5 | 229 | 60 | 35.5 | 40.8 | 28.68 |  |  | -0.02065 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 32 |  |  | -0.02066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 31.63 |  |  | -0.02066 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
211375 | BEAC | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.02066 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 15.92 |  |  | -0.02066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
211591 | HARW | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | -0.02066 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 263.56 |  |  | -0.02066 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
916009 | LOR2_Q27 E | 0.7 | 229 | 74 | 0 | 88.8 | 54.21 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW | Q27 |  |  | 0.8
208941 | FISH CT | 12.5 | 229 | 52 | 24.4 | 28 | 0.52 |  |  | -0.02066 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916001 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 44.5 | 21.44 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW | N47 |  |  | 0.8
916008 | LOR1 E | 0.7 | 229 | 74 | 0 | 23.8 | 14.53 |  |  | -0.02066 |  |  |  | 0 |  | 1 | NEW | N14 |  |  | 0.8
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 5.16 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY | N47 |  |  | 0.8
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 81.14 |  |  | -0.02066 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 77.37 |  |  | -0.02066 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.2 | 6.84 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY | Q27 |  |  | 0.8
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.14 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY | N14 |  |  | 0.8
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1251.7 |  |  | -0.02066 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 4.3 |  |  | -0.02067 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 40.29 |  |  | -0.02067 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 30.66 |  |  | -0.02067 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 5.19 |  |  | -0.02067 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1253.3 |  |  | -0.02067 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 205.74 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT |  |  | 1
921653 | AA2-008 E | 230 | 229 | 58 | 0 | 57 | 0 |  |  | -0.02068 |  |  |  | 0.036 |  | 1 | ENERGY | MOXIE PATRIOT |  |  | 1
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 25.15 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW | U2-030 |  |  | 0.8
209018 | SUNBIPCT | 12.5 | 229 | 55 | 35.8 | 41.1 | 22.11 |  |  | -0.02069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 0.26 |  |  | -0.02068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
208948 | WILL CT | 12.5 | 229 | 55 | 23.1 | 26.6 | 14.31 |  |  | -0.02068 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 3.76 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | U2-030 |  |  | 0.8
212464 | AF2-289 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-289 |  |  | 0.1
212451 | AF2-427 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-427 |  |  | 0.1
211938 | AF2-285 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-285 |  |  | 0.1
212495 | AF2-284 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW | AF2-284 |  |  | 0.1
212455 | AF2-290 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW | AF2-290 |  |  | 0.1
212005 | ALWD | 12.5 | 229 | 77 | 0 | 3.2 | 1.99 |  |  | -0.02068 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212345 | PENS | 12.5 | 229 | 77 | 0 | 3 | 1.86 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212435 | SMIL | 12.5 | 229 | 77 | 0 | 2 | 1.24 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
212494 | AF2-284 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-284 |  |  | 1
212461 | AF2-289 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-289 |  |  | 1
212450 | AF2-427 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-427 |  |  | 1
211937 | AF2-285 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02068 |  |  |  | 0 |  | 1 | MTX | AF2-285 |  |  | 1
212454 | AF2-290 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02069 |  |  |  | 0 |  | 1 | MTX | AF2-290 |  |  | 1
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 758.5 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 757.9 |  |  | -0.02068 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 26.19 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 26.03 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 23.83 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.02069 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 15.71 |  |  | -0.02069 |  |  |  | 0.036 |  | 1 | CAPACITY | HUNLOCK |  |  | 1
208944 | JENK CT | 12.5 | 229 | 55 | 24 | 27.6 | 14.85 |  |  | -0.02069 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
946263 | BECR K09 E | 0.69 | 229 | 74 | 0 | 20.7 | 12.64 |  |  | -0.02069 |  |  |  | 0 |  | 1 | NEW | L18 |  |  | 0.8
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.02 |  |  | -0.02069 |  |  |  | 0 |  | 1 | CAPACITY | L18 |  |  | 0.8
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 213 |  |  | -0.0207 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 130.16 |  |  | -0.0207 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | -0.0207 |  |  |  | 0.036 |  | 1 | CAPACITY | Hummel |  |  | 1
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 119.95 |  |  | -0.0207 |  |  |  | 0 |  | 1 | CAPACITY | Hummel |  |  | 1
211374 | AVOC | 12.5 | 229 | 77 | 0 | 17.4 | 10.8 |  |  | -0.02071 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | -0.02073 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | -0.02073 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 251.72 |  |  | -0.02073 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 37.91 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 0.8
209031 | WAYM IPP E | 34.5 | 229 | 74 | 0 | 55.5 | 33.88 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | K21 |  |  | 0.8
209009 | PEIP 2 | 13.8 | 229 | 56 | 38 | 43.7 | 23.5 |  |  | -0.02073 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.02073 |  |  |  | 0.0975 |  | 1 | MTX | Z2-107 |  |  | 1
209010 | PEIP 1 | 13.8 | 229 | 64 | 17.4 | 26.5 | 21.42 |  |  | -0.02073 |  |  |  | 0.28996 |  | 1 | CAPACITY |  |  |  | 1
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 5.49 |  |  | -0.02073 |  |  |  | 0 |  | 1 | CAPACITY | K21 |  |  | 0.8
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 5.34 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AC1-071 |  |  | 0.8
209972 | AF2-288 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-288 |  |  | 0.1
209937 | AF2-287 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-287 |  |  | 0.1
211490 | AF2-282 E | 12.5 | 229 | 75 | 0 | 3 | 0.28 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-282 |  |  | 0.1
211554 | AF2-283 E | 12.5 | 229 | 75 | 0 | 2 | 0.19 |  |  | -0.02073 |  |  |  | 0 |  | 1 | NEW | AF2-283 |  |  | 0.1
209971 | AF2-288 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-288 |  |  | 1
209936 | AF2-287 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-287 |  |  | 1
211489 | AF2-282 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-282 |  |  | 1
211553 | AF2-283 BAT | 12.5 | 229 | 76 | -0.1 | 0.1 | 0 |  |  | -0.02073 |  |  |  | 0 |  | 1 | MTX | AF2-283 |  |  | 1
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 28.23 |  |  | -0.02085 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 0.8
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 11.56 |  |  | -0.02085 |  |  |  | 0 |  | 1 | NEW | K28 |  |  | 0.8
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.3 | 8.34 |  |  | -0.02085 |  |  |  | 0 |  | 1 | CAPACITY | K28 |  |  | 0.8
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 41.39 |  |  | -0.02088 |  |  |  | 0 |  | 1 | NEW | P59 |  |  | 0.8
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 5.64 |  |  | -0.02088 |  |  |  | 0 |  | 1 | CAPACITY | P59 |  |  | 0.8
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 389 |  |  |  | -0.0209
916000 | 01BACKB E | 34.5 | 201 | 74 | 0 | 57.9 | 27.9 |  |  | -0.02091 |  |  |  | 0 |  | 1 | NEW | K19 |  |  | 0.8
237013 | AA2-103 E | 0.48 | 201 | 76 | 0 | 20 | 0 |  |  | -0.02091 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 3.9 |  |  | -0.02091 |  |  |  | 0 |  | 1 | CAPACITY | K19 |  |  | 0.8
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 20.96 |  |  | -0.02093 |  |  |  | 0 |  | 1 | NEW | U2-061 |  |  | 0.8
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 3.13 |  |  | -0.02093 |  |  |  | 0 |  | 1 | CAPACITY | U2-061 |  |  | 0.8
943302 | AF1-001 E | 34.5 | 201 | 75 | 0 | 7.25 | 0.53 |  |  | -0.02094 |  |  |  | 0 |  | 1 | NEW | AF1-001 |  |  | 0.1
237039 | AF1-001 C | 34.5 | 201 | 75 | 0 | 6.5 | 0.47 |  |  | -0.02094 |  |  |  | 0 |  | 1 | CAPACITY | AF1-001 |  |  | 0.1
243415 | 05WWVSTA | 69 | 205 | 61 | 69.8 | 96 | 53.26 |  |  | -0.02099 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 21.4 | 11.51 |  |  | -0.021 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 7.03 |  |  | -0.021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 6.96 |  |  | -0.021 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1308.8 | 1308.8 |  |  | -0.02105 |  |  |  | 0 |  | 1 | CAPACITY | MTG1 |  |  | 1
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 236.66 |  |  | -0.02109 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | -0.02109 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-076 |  |  | 1
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 177.5 |  |  | -0.02109 |  |  |  | 0 |  | 1 | CAPACITY | AA1-076 |  |  | 1
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 25.91 |  |  | -0.02113 |  |  |  | 0.15157 |  | 1 | CAPACITY |  |  |  | 1
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 253.85 |  |  | -0.02114 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.02114 |  |  |  | 0.1042 |  | 1 | ENERGY |  |  |  | 1
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 73.26 |  |  | -0.02114 |  |  |  | 0 |  | 1 | NEW | P28 |  |  | 0.8
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 31.73 |  |  | -0.02114 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 11.51 |  |  | -0.02114 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 13.37 |  |  | -0.02114 |  |  |  | 0 |  | 1 | CAPACITY | P28 |  |  | 0.8
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 317.2 | 121.14 |  |  | -0.02114 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | -0.02114 |  |  |  | 0.036 |  | 1 | CAPACITY | RONCO |  |  | 1
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 174.4 | 66.6 |  |  | -0.02114 |  |  |  | 0 |  | 1 | CAPACITY | RONCO |  |  | 1
237068 | AA2-119 GEN | 20.5 | 201 | 58 | 0 | 600 | 0 |  |  | -0.02115 |  |  |  | 0.036 |  | 1 | NEW | Harrison |  |  | 1
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1407 | 1407 |  |  | -0.02115 |  |  |  | 0 |  | 1 | CAPACITY | GVG2 |  |  | 1
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1389 | 1389 |  |  | -0.02115 |  |  |  | 0 |  | 1 | CAPACITY | GVG1 |  |  | 1
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.22 |  |  | -0.02117 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 552 |  |  | -0.02118 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 545.5 |  |  | -0.02118 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 850.6 |  |  | -0.02119 |  |  |  | 0 |  | 1 | CAPACITY | Cone1 |  |  | 1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 850 |  |  | -0.02119 |  |  |  | 0 |  | 1 | CAPACITY | Cone2 |  |  | 1
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 710 |  |  | -0.02119 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
913142 | Y1-033 E OP1 | 0.7 | 226 | 74 | 0 | 34.02 | 20.77 |  |  | -0.02122 |  |  |  | 0 |  | 1 | NEW | Y1-033 |  |  | 0.8
203926 | AA2-133 GEN | 13.8 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | -0.02122 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 3.05 |  |  | -0.02122 |  |  |  | 0 |  | 1 | CAPACITY | Y1-033 |  |  | 0.8
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 59.57 |  |  | -0.02125 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 14.76 |  |  | -0.02127 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
916002 | 01ELLIOTTS E | 34.5 | 201 | 74 | 0 | 44.9 | 21.63 |  |  | -0.02129 |  |  |  | 0 |  | 1 | NEW | N32 |  |  | 0.8
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 2.65 |  |  | -0.02129 |  |  |  | 0 |  | 1 | CAPACITY | N32 |  |  | 0.8
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | -0.0213 |  |  |  | 0 |  | 1 | CAPACITY | X1-109 |  |  | 1
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 205.74 |  |  | -0.0213 |  |  |  | 0.036 |  | 1 | CAPACITY | X1-109 |  |  | 1
203937 | 26AA1-144 G2 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203936 | 26AA1-144 G1 | 13.8 | 226 | 58 | 0 | 81.5 | 43.84 |  |  | -0.02131 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-144 |  |  | 1
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.11 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235587 | 01HARRN3 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235586 | 01HARRN2 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235585 | 01HARRN1 | 20 | 201 | 16 | 568.5 | 653.4 | 653.4 |  |  | -0.02131 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 41.94 |  |  | -0.02132 |  |  |  | 0.39467 |  | 1 | CAPACITY |  |  |  | 1
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0.11 |  |  | -0.02132 |  |  |  | 0 |  | 1 | NEW | V4-073 |  |  | 0.1
253303 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.07 |  |  | -0.02132 |  |  |  | 0 |  | 1 | CAPACITY | V4-073 |  |  | 0.1
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.02133 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.02135 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 25.64 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | K23 |  |  | 0.8
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 19.54 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | L13 |  |  | 0.8
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 17.58 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 0.8
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.02135 |  |  |  | 0.0975 |  | 1 | MTX |  |  |  | 1
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 3.85 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | Lookout Wind |  |  | 0.8
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 3.6 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | L13 |  |  | 0.8
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 4.8 | 2.93 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | K23 |  |  | 0.8
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 1.1 |  |  | -0.02135 |  |  |  | 0 |  | 1 | NEW | Lookout Wind |  |  | 0.8
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 124.5 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | -0.02135 |  |  |  | 0.036 |  | 1 | CAPACITY | T-174 |  |  | 1
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 117.25 |  |  | -0.02135 |  |  |  | 0 |  | 1 | CAPACITY | T-174 |  |  | 1
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | -0.02135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 14.43 |  |  | -0.02135 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237041 | AE2-055 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | -0.02136 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 0.1
940682 | AE2-055 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02136 |  |  |  | 0 |  | 1 | NEW | AE2-055 |  |  | 0.1
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | -0.02137 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 27.05 |  |  | -0.02137 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.02137 |  |  |  | 0 |  | 1 | MTX | AC1-025 |  |  | 1
203938 | 26AA2-132 | 34.5 | 226 | 29 | 0 | 19.9 | 0 |  |  | -0.02138 |  |  |  | 0.1042 |  | 1 | NEW |  |  |  | 1
236828 | 01GRAYMONT | 46 | 201 | 75 | 0 | 4 | 0.29 |  |  | -0.02139 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 34.19 |  |  | -0.0214 |  |  |  | 0 |  | 1 | NEW | K02 |  |  | 0.8
237083 | AE1-147_GEN | 0.6 | 201 | 75 | 0 | 19.98 | 1.46 |  |  | -0.02139 |  |  |  | 0 |  | 1 | CAPACITY | AE1-147 |  |  | 0.1
939171 | AE1-147_E | 0.6 | 201 | 75 | 0 | 7.98 | 0.58 |  |  | -0.02139 |  |  |  | 0 |  | 1 | NEW | AE1-147 |  |  | 0.1
203944 | AF2-271 E | 46 | 226 | 75 | 0 | 3 | 0.28 |  |  | -0.02139 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 11.51 |  |  | -0.0214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 11.3 |  |  | -0.0214 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 410 | 156.58 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235619 | 01SBEND1 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235620 | 01SBEND2 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235622 | 01SBEND4 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
235621 | 01SBEND3 | 18 | 201 | 58 | 90 | 192.5 | 73.52 |  |  | -0.02143 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 39.07 |  |  | -0.02142 |  |  |  | 0 |  | 1 | NEW | N39 |  |  | 0.8
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 34.19 |  |  | -0.02142 |  |  |  | 0 |  | 1 | NEW | O38 |  |  | 0.8
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 11.1 | 6.78 |  |  | -0.02142 |  |  |  | 0 |  | 1 | CAPACITY | N39 |  |  | 0.8
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.1 | 5.56 |  |  | -0.02142 |  |  |  | 0 |  | 1 | CAPACITY | O38 |  |  | 0.8
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 852.3 | 852.3 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | Keys1 |  |  | 1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 851.6 | 851.6 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | Keys2 |  |  | 1
237048 | AF1-022 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | AF1-022 |  |  | 0.1
943512 | AF1-022 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | -0.02143 |  |  |  | 0 |  | 1 | NEW | AF1-022 |  |  | 0.1
957932 | AF2-087 E | 46 | 226 | 75 | 0 | 4.2 | 0.39 |  |  | -0.02143 |  |  |  | 0 |  | 1 | NEW | AF2-087 |  |  | 0.1
203941 | AF2-087 C | 46 | 226 | 75 | 0 | 3.05 | 0.28 |  |  | -0.02143 |  |  |  | 0 |  | 1 | CAPACITY | AF2-087 |  |  | 0.1
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 10.04 |  |  | -0.02145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
916004 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | -0.02144 |  |  |  | 0 |  | 1 | NEW | K22 |  |  | 0.8
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.55 |  |  | -0.02144 |  |  |  | 0 |  | 1 | CAPACITY | K22 |  |  | 0.8
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.53 |  |  | -0.02144 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 11.3 |  |  | -0.02145 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 44 | 26.86 |  |  | -0.02147 |  |  |  | 0 |  | 1 | NEW | P60 |  |  | 0.8
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 5.19 |  |  | -0.02147 |  |  |  | 0 |  | 1 | CAPACITY | P60 |  |  | 0.8
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 49.15 |  |  | -0.02148 |  |  |  | 0 |  | 1 | NEW | P47 |  |  | 0.8
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.2 | 9.28 |  |  | -0.02148 |  |  |  | 0 |  | 1 | CAPACITY | P47 |  |  | 0.8
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 31.6 | 19.29 |  |  | -0.0215 |  |  |  | 0 |  | 1 | NEW | Q53 |  |  | 0.8
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 21.5 | 11.56 |  |  | -0.02149 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
203942 | AF2-270 E | 23 | 226 | 75 | 0 | 3.72 | 0.34 |  |  | -0.02149 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 3.91 |  |  | -0.0215 |  |  |  | 0 |  | 1 | CAPACITY | Q53 |  |  | 0.8
203940 | AF1-140 C | 23 | 226 | 75 | 0 | 9.78 | 0.9 |  |  | -0.0215 |  |  |  | 0 |  | 1 | CAPACITY | AF1-140 |  |  | 0.1
944752 | AF1-140 E | 23 | 226 | 75 | 0 | 6.52 | 0.6 |  |  | -0.0215 |  |  |  | 0 |  | 1 | NEW | AF1-140 |  |  | 0.1
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 62.3 | 38.03 |  |  | -0.02151 |  |  |  | 0 |  | 1 | NEW | R32 |  |  | 0.8
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 54.4 | 33.21 |  |  | -0.02151 |  |  |  | 0 |  | 1 | NEW | O18 |  |  | 0.8
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 26.2 | 15.99 |  |  | -0.02151 |  |  |  | 0 |  | 1 | NEW | K13 |  |  | 0.8
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 7.75 |  |  | -0.02151 |  |  |  | 0 |  | 1 | CAPACITY | R32 |  |  | 0.8
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 4.95 |  |  | -0.02151 |  |  |  | 0 |  | 1 | CAPACITY | O18 |  |  | 0.8
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 1.95 |  |  | -0.02151 |  |  |  | 0 |  | 1 | CAPACITY | K13 |  |  | 0.8
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 525.7 |  |  | -0.02152 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200503 | 26C.SLOPE | 115 | 226 | 11 | 17 | 50 | 0 |  |  | -0.02152 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 41.7 | 25.46 |  |  | -0.02153 |  |  |  | 0 |  | 1 | NEW | Q36 |  |  | 0.8
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 5.07 |  |  | -0.02153 |  |  |  | 0 |  | 1 | CAPACITY | Q36 |  |  | 0.8
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 0.2 |  |  | -0.02155 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
237046 | AF1-021 C | 25 | 201 | 75 | 0 | 8.4 | 0.61 |  |  | -0.02155 |  |  |  | 0 |  | 1 | CAPACITY | AF1-021 |  |  | 0.1
943502 | AF1-021 E | 25 | 201 | 75 | 0 | 5.6 | 0.41 |  |  | -0.02155 |  |  |  | 0 |  | 1 | NEW | AF1-021 |  |  | 0.1
203946 | AE2-131 C | 34.5 | 226 | 75 | 0 | 12 | 1.11 |  |  | -0.02156 |  |  |  | 0 |  | 1 | CAPACITY | AE2-131 |  |  | 0.1
941352 | AE2-131 E | 34.5 | 226 | 75 | 0 | 8 | 0.74 |  |  | -0.02156 |  |  |  | 0 |  | 1 | NEW | AE2-131 |  |  | 0.1
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 127.94 |  |  | -0.02157 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 0.2 |  |  | -0.02156 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
200665 | 26SHAWVL 3 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | -0.02157 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200666 | 26SHAWVL 4 | 22 | 226 | 30 | 152.3 | 175 | 165.11 |  |  | -0.02157 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 0.15 |  |  | -0.02158 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 92.04 |  |  | -0.02159 |  |  |  | 0.19357 |  | 1 | CAPACITY |  |  |  | 1
200722 | 26SHAWVL 2 | 18 | 226 | 30 | 62 | 125 | 117.94 |  |  | -0.02158 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200715 | 26SHAWVL 1 | 18 | 226 | 30 | 62 | 123 | 116.05 |  |  | -0.02158 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 17.22 |  |  | -0.02159 |  |  |  | 0 |  | 1 | NEW | V3-030 |  |  | 0.8
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 3.24 |  |  | -0.02159 |  |  |  | 0 |  | 1 | CAPACITY | V3-030 |  |  | 0.8
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4 |  |  | -0.0216 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
916003 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 13.3 | 6.41 |  |  | -0.02161 |  |  |  | 0 |  | 1 | NEW | K20 |  |  | 0.8
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 0.82 |  |  | -0.02161 |  |  |  | 0 |  | 1 | CAPACITY | K20 |  |  | 0.8
200809 | 26SITHE | 138 | 226 | 60 | 0 | 36 | 25.31 |  |  | -0.02163 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 620 |  |  | -0.02163 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | -0.02164 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.41 |  |  | -0.02164 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 8.66 |  |  | -0.02166 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
237054 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 195.92 |  |  | -0.02167 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
237043 | AE2-125 C | 25 | 201 | 75 | 0 | 8.28 | 0.6 |  |  | -0.02166 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 0.1
941312 | AE2-125 E | 25 | 201 | 75 | 0 | 5.52 | 0.4 |  |  | -0.02166 |  |  |  | 0 |  | 1 | NEW | AE2-125 |  |  | 0.1
200805 | 26COLVER13 | 13.2 | 226 | 12 | 95.7 | 110 | 0 |  |  | -0.02169 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 34.62 |  |  | -0.02169 |  |  |  | 0 |  | 1 | NEW | Z1-069 |  |  | 0.8
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 17.1 | 10.44 |  |  | -0.02169 |  |  |  | 0 |  | 1 | CAPACITY | Z1-069 |  |  | 0.8
237036 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 7.64 |  |  | -0.02172 |  |  |  | 0.1042 |  | 1 | CAPACITY | AD2-002 |  |  | 1
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.02172 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-068 |  |  | 0.1
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 2.48 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-069 |  |  | 0.1
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-165 |  |  | 0.1
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 2.45 |  |  | -0.02172 |  |  |  | 0 |  | 1 | CAPACITY | AC1-166 |  |  | 0.1
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-165 |  |  | 0.1
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 1.19 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-166 |  |  | 0.1
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-068 |  |  | 0.1
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 1.16 |  |  | -0.02172 |  |  |  | 0 |  | 1 | NEW | AC1-069 |  |  | 0.1
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 63.89 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 63.82 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 63.78 |  |  | -0.02174 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253127 | 09CEDRVL | 69 | 209 | 77 | 0 | 1.8 | 1.3 |  |  | -0.02174 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 2.26 |  |  | -0.02176 |  |  |  | 0 |  | 1 | NEW | AC2-067 |  |  | 0.1
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 1.93 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY | AC2-067 |  |  | 0.1
237050 | AF1-155 C | 46 | 201 | 75 | 0 | 12 | 0.88 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY | AF1-155 |  |  | 0.1
944902 | AF1-155 E | 46 | 201 | 75 | 0 | 8 | 0.58 |  |  | -0.02176 |  |  |  | 0 |  | 1 | NEW | AF1-155 |  |  | 0.1
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 650 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 614 |  |  | -0.02176 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235590 | 01PLEAS1 | 26 | 201 | 16 | 300 | 639 | 0 |  |  | -0.02177 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
235591 | 01PLEAS2 | 26 | 201 | 16 | 350 | 639 | 0 |  |  | -0.02177 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 42.3 |  |  | -0.02179 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 173.6 | 199.5 | 76.19 |  |  | -0.02181 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 167 | 191.9 | 73.29 |  |  | -0.02181 |  |  |  | 0.036 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 164.1 | 188.6 | 72.03 |  |  | -0.02181 |  |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE |  |  | 1
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | -0.02181 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 29.51 |  |  | -0.02181 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | -0.02185 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 11.98 |  |  | -0.02185 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.02187 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.02187 |  |  |  | 0 |  | 1 | NEW | AB1-069 |  |  | 1
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.02187 |  |  |  | 0.036 |  | 1 | NEW | AB1-069 |  |  | 1
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 170.9 | 65.27 |  |  | -0.02187 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 170.8 | 65.23 |  |  | -0.02187 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 3.83 |  |  | -0.02187 |  |  |  | 0.0789 |  | 1 | CAPACITY | ALLEG LD_5 |  |  | 1
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 4.22 |  |  | -0.02189 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 3.77 |  |  | -0.02196 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
237052 | AF1-210 C | 25 | 201 | 75 | 0 | 9.54 | 0.7 |  |  | -0.02199 |  |  |  | 0 |  | 1 | CAPACITY | AF1-210 |  |  | 0.1
945452 | AF1-210 E | 25 | 201 | 75 | 0 | 6.36 | 0.46 |  |  | -0.02199 |  |  |  | 0 |  | 1 | NEW | AF1-210 |  |  | 0.1
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 21.23 |  |  | -0.0221 |  |  |  | 0.21852 |  | 1 | CAPACITY |  |  |  | 1
203932 | AE1-123 | 34.5 | 226 | 55 | 0 | 18 | 9.68 |  |  | -0.0221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 164.5 |  |  | -0.02214 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 155.36 |  |  | -0.02214 |  |  |  | 0.0272 |  | 1 | CAPACITY |  |  |  | 1
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 21.09 |  |  | -0.02214 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 31.32 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 30.93 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 30.55 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 30.17 |  |  | -0.02221 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 2.69 |  |  | -0.02222 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 62 | 33.35 |  |  | -0.02235 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 139.32 |  |  | -0.02239 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.02239 |  |  |  | 0.036 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.02239 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 64.16 |  |  | -0.02239 |  |  |  | 0 |  | 1 | CAPACITY | WATERFORD |  |  | 1
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 80.2 |  |  | -0.02242 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 28.78 |  |  | -0.02247 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 10.54 |  |  | -0.02249 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
203939 | AE1-160 C | 34.5 | 226 | 75 | 0 | 12.7 | 1.17 |  |  | -0.0225 |  |  |  | 0 |  | 1 | CAPACITY | AE1-160 |  |  | 0.1
939292 | AE1-160 E | 34.5 | 226 | 75 | 0 | 7.3 | 0.68 |  |  | -0.0225 |  |  |  | 0 |  | 1 | NEW | AE1-160 |  |  | 0.1
253029 | 09GRNVIL | 138 | 209 | 77 | 0 | 4.5 | 3.26 |  |  | -0.02253 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 113.43 |  |  | -0.0226 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | -0.0226 |  |  |  | 0 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 71.22 |  |  | -0.0226 |  |  |  | 0.036 |  | 1 | CAPACITY | WASHINGTON |  |  | 1
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 770.1 |  |  | -0.02262 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254026 | 15USSILL | 138 | 215 | 77 | 0 | 66 | 27.72 |  |  | -0.02266 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 790.2 |  |  | -0.02266 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
254024 | 15CLAIRT | 138 | 215 | 77 | 0 | 35 | 14.7 |  |  | -0.02267 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
270122 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 185.22 |  |  | -0.0227 |  |  |  | 0.036 |  | 1 | CAPACITY |  |  |  | 1
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 77.49 |  |  | -0.0227 |  |  |  | 0.24937 |  | 1 | CAPACITY |  |  |  | 1
254037 | 15UNIVRS | 138 | 215 | 77 | 0 | 1.1 | 0.46 |  |  | -0.02272 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 567.5 |  |  | -0.02275 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239022 | 02NWCAG3 | 14.4 | 202 | 57 | 20 | 92.3 | 35.25 |  |  | -0.02282 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 38.8 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253970 | 15BI2 | 13.8 | 215 | 58 | 83.2 | 95.6 | 36.51 |  |  | -0.02282 |  |  |  | 0.036 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.5 | 18.52 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND |  |  | 1
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 6.91 |  |  | -0.02282 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 620.4 |  |  | -0.02282 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239024 | 02NWCAG5 | 16.5 | 202 | 57 | 23 | 145 | 55.38 |  |  | -0.02285 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 585 |  |  | -0.02285 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239023 | 02NWCAG4 | 14.4 | 202 | 57 | 20 | 93 | 35.52 |  |  | -0.02286 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 0.04 |  |  | -0.02286 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0.53 |  |  | -0.02293 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 0.1
254303 | AC2-168 C | 138 | 215 | 75 | 0 | 4.4 | 0.32 |  |  | -0.02293 |  |  |  | 0 |  | 1 | NEW | AC2-168 |  |  | 0.1
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.26 |  |  | -0.02293 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 216.9 |  |  | -0.02295 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 13.77 |  |  | -0.02296 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | -0.02295 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 600 |  |  | -0.02295 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253924 | 15SHELL | 138 | 215 | 58 | 0 | 98 | 0 |  |  | -0.02298 |  |  |  | 0.036 |  | 1 | ENERGY | Y3-103 |  |  | 1
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 25.8 | 9.85 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 15.2 | 5.8 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | -0.02298 |  |  |  | 0.036 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 15.1 | 5.77 |  |  | -0.02298 |  |  |  | 0 |  | 1 | CAPACITY | Y3-103 |  |  | 1
254304 | AE2-114 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AE2-114 |  |  | 0.1
254305 | AE2-115 C | 138 | 215 | 75 | 0 | 10.26 | 0.75 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AE2-115 |  |  | 0.1
941202 | AE2-114 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | -0.02301 |  |  |  | 0 |  | 1 | NEW | AE2-114 |  |  | 0.1
941212 | AE2-115 E | 138 | 215 | 75 | 0 | 6.84 | 0.5 |  |  | -0.02301 |  |  |  | 0 |  | 1 | NEW | AE2-115 |  |  | 0.1
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | -0.02301 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 119.27 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 91.73 |  |  | -0.02301 |  |  |  | 0 |  | 1 | CAPACITY | AA1-123 |  |  | 1
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 2.69 |  |  | -0.02302 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 156.58 |  |  | -0.02305 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | -0.02305 |  |  |  | 0.036 |  | 1 | CAPACITY | AA1-044 |  |  | 1
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 112.66 |  |  | -0.02305 |  |  |  | 0 |  | 1 | CAPACITY | AA1-044 |  |  | 1
253197 | 09PIQUA3 | 69 | 209 | 77 | 0 | 38.3 | 2.77 |  |  | -0.02307 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 899.3 |  |  | -0.02307 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253900 | 15BVRVL1 | 22 | 215 | 44 | 781.7 | 898.5 | 898.5 |  |  | -0.02307 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 280 | 106.93 |  |  | -0.02314 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | -0.02314 |  |  |  | 0 |  | 1 | CAPACITY | Y2-050 |  |  | 1
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 206 | 78.67 |  |  | -0.02314 |  |  |  | 0.036 |  | 1 | CAPACITY | Y2-050 |  |  | 1
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 26.1 | 16.36 |  |  | -0.02318 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 307.6 | 117.47 |  |  | -0.02321 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | -0.02321 |  |  |  | 0.036 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 288.2 | 110.07 |  |  | -0.02321 |  |  |  | 0 |  | 1 | CAPACITY | Z2-028 |  |  | 1
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.02322 |  |  |  | 0.0692 |  | 1 | ENERGY |  |  |  | 1
241951 | AB1-105 OP | 345 | 202 | 58 | 0 | 850 | 0 |  |  | -0.02327 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 4.3 |  |  | -0.02336 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.02338 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.02338 |  |  |  | 0.036 |  | 1 | CAPACITY | Guernsey |  |  | 1
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 233.73 |  |  | -0.02338 |  |  |  | 0 |  | 1 | CAPACITY | Guernsey |  |  | 1
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.02342 |  |  |  | 0 |  | 1 | NEW | U2-090 |  |  | 0.8
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.02342 |  |  |  | 0 |  | 1 | NEW | V3-007 |  |  | 0.8
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.02342 |  |  |  | 0 |  | 1 | CAPACITY | U2-090 |  |  | 0.8
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.02342 |  |  |  | 0 |  | 1 | CAPACITY | V3-007 |  |  | 0.8
270106 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.02355 |  |  |  | 0 |  | 1 | ENERGY |  |  |  | 1
245305 | 05WOOSTER | 69 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.02356 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
245304 | 05WOOSTER | 23 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.02358 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
243158 | 05WOOSTE | 138 | 205 | 77 | 0 | 1 | 0.72 |  |  | -0.02359 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 2.55 |  |  | -0.02378 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 0.17 |  |  | -0.0238 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.02382 |  |  |  | 0 |  | 1 | NEW | U3-002 |  |  | 0.8
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 6.36 |  |  | -0.02382 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 0.8
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 6.17 |  |  | -0.02382 |  |  |  | 0 |  | 1 | CAPACITY | U3-002 |  |  | 0.8
253234 | 09VERSAL | 69 | 209 | 77 | 0 | 5.4 | 3.91 |  |  | -0.02388 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 243 | 92.8 |  |  | -0.02391 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -0.02391 |  |  |  | 0 |  | 1 | CAPACITY | DRESDEN |  |  | 1
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 182.2 | 69.58 |  |  | -0.02391 |  |  |  | 0.036 |  | 1 | CAPACITY | DRESDEN |  |  | 1
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1247 |  |  | -0.02396 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.02405 |  |  |  | 0 |  | 1 | MTX |  |  |  | 1
253160 | 09JCKCEN | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.02422 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 7.55 |  |  | -0.0243 |  |  |  | 0 |  | 1 | NEW | Z1-035 |  |  | 0.8
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 1.13 |  |  | -0.0243 |  |  |  | 0 |  | 1 | CAPACITY | Z1-035 |  |  | 0.8
243362 | 05RANDOLPH1 | 138 | 205 | 77 | 0 | 4 | 3.06 |  |  | -0.02435 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
253158 | 09INDI L | 69 | 209 | 77 | 0 | 3.4 | 2.46 |  |  | -0.02437 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
253363 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.02465 |  |  |  | 0.05 |  | 1 | MTX | AC1-212 |  |  | 1
253178 | 09MINSTR | 69 | 209 | 77 | 0 | 10 | 4.61 |  |  | -0.02465 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
AC1-212 | BATEXP_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0247
253362 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.28 |  |  | -0.02465 |  |  |  | 0 |  | 1 | CAPACITY | AC1-212 |  |  | 1
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 46.25 |  |  | -0.02543 |  |  |  | 0 |  | 1 | NEW | S71 |  |  | 0.8
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 11.56 |  |  | -0.02543 |  |  |  | 0 |  | 1 | CAPACITY | S71 |  |  | 0.8
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 25 | 0.37 |  |  | -0.02557 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
253128 | 09CELINA | 69 | 209 | 77 | 0 | 4 | 2.89 |  |  | -0.02564 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.48 |  |  | -0.02595 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 627.1 |  |  | -0.02602 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 54.49 |  |  | -0.02612 |  |  |  | 0 |  | 1 | NEW | AC2-176 |  |  | 0.8
270201 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 8.14 |  |  | -0.02612 |  |  |  | 0 |  | 1 | CAPACITY | AC2-176 |  |  | 0.8
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.02646 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 19.51 |  |  | -0.02646 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 18.94 |  |  | -0.02646 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 9.4 |  |  | -0.02648 |  |  |  | 0.1097 |  | 1 | CAPACITY |  |  |  | 1
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 29.6 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 29.1 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 28.95 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 28.68 |  |  | -0.0265 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.02708 |  |  |  | 0 |  | 1 | CAPACITY | Z2-115 |  |  | 0.1
247968 | Z2-115 E | 12 | 205 | 75 | 0 | 1.25 | 0.09 |  |  | -0.02708 |  |  |  | 0 |  | 1 | NEW | Z2-115 |  |  | 0.1
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 125.75 |  |  | -0.02741 |  |  |  | 0 |  | 1 | NEW | U2-072 |  |  | 0.8
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 18.79 |  |  | -0.02741 |  |  |  | 0 |  | 1 | CAPACITY | U2-072 |  |  | 0.8
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 76.89 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 3 |  |  | 0.8
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 60.22 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 4 |  |  | 0.8
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 39.65 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 21 |  |  | 0.8
247903 | 05FR-22G E | 0.69 | 205 | 74 | 0 | 78.8 | 37.97 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 22 |  |  | 0.8
247900 | 05FR-11G E | 0.6 | 205 | 74 | 0 | 78.3 | 37.72 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 11 |  |  | 0.8
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 37.1 |  |  | -0.02769 |  |  |  | 0 |  | 1 | NEW | Q01 12 |  |  | 0.8
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 14.02 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 4 |  |  | 0.8
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 12.38 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 11 |  |  | 0.8
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 21 |  |  | 0.8
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 22 |  |  | 0.8
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 3 |  |  | 0.8
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 6.02 |  |  | -0.02769 |  |  |  | 0 |  | 1 | CAPACITY | Q01 12 |  |  | 0.8
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 0.88 |  |  | -0.02773 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
925135 | AB2-170 E | 0.55 | 205 | 75 | 0 | 80.6 | 0 |  |  | -0.02774 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 0.1
247549 | V3-028 C | 345 | 205 | 75 | 0 | 57 | 4.16 |  |  | -0.02774 |  |  |  | 0 |  | 1 | CAPACITY | V3-028 |  |  | 0.1
925133 | AB2-170 C | 0.55 | 205 | 75 | 0 | 49.4 | 0 |  |  | -0.02774 |  |  |  | 0 |  | 1 | NEW | AB2-170 |  |  | 0.1
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0.9 |  |  | -0.02774 |  |  |  | 0 |  | 1 | NEW | V3-028 |  |  | 0.1
907201 | AC2-103 E1 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.02807 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 0.8
907202 | AC2-103 E2 | 0.69 | 202 | 74 | 0 | 129.48 | 62.38 |  |  | -0.02807 |  |  |  | 0 |  | 1 | NEW | AC2-103 |  |  | 0.8
241885 | AC2-103 C1 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.02807 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 0.8
241886 | AC2-103 C2 | 0.69 | 202 | 74 | 0 | 19.34 | 9.32 |  |  | -0.02807 |  |  |  | 0 |  | 1 | CAPACITY | AC2-103 |  |  | 0.8
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 20.96 |  |  | -0.02822 |  |  |  | 0 |  | 1 | NEW | U1-059 |  |  | 0.8
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 7.71 |  |  | -0.02822 |  |  |  | 0 |  | 1 | NEW | W1-056 |  |  | 0.8
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 4.63 |  |  | -0.02822 |  |  |  | 0 |  | 1 | CAPACITY | U1-059 |  |  | 0.8
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.16 |  |  | -0.02822 |  |  |  | 0 |  | 1 | CAPACITY | W1-056 |  |  | 0.8
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 0.8
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 0.8
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-028 |  |  | 0.8
270174 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.02832 |  |  |  | 0 |  | 1 | NEW | U4-029 |  |  | 0.8
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 83.83 |  |  | -0.0285 |  |  |  | 0 |  | 1 | NEW | V4-010 |  |  | 0.8
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 12.53 |  |  | -0.0285 |  |  |  | 0 |  | 1 | CAPACITY | V4-010 |  |  | 0.8
247454 | 05OGG STREET | 69 | 205 | 77 | 0 | 10 | 7.16 |  |  | -0.02858 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 345.1 | 131.79 |  |  | -0.02913 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 162.6 | 62.1 |  |  | -0.02913 |  |  |  | 0.036 |  | 1 | CAPACITY | FREMONT |  |  | 1
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 159.1 | 60.76 |  |  | -0.02913 |  |  |  | 0 |  | 1 | CAPACITY | FREMONT |  |  | 1
244357 | 05GRANGER EL | 34.5 | 205 | 2 | 0 | 3.2 | 0 |  |  | -0.02922 |  |  |  | 0 |  | 1 | NEW |  |  |  | 1
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 896 |  |  | -0.02952 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 22.88 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 22.8 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 22.19 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 22.07 |  |  | -0.02967 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
246235 | 05BLUFFTON | 69 | 205 | 77 | 0 | 2 | 1.43 |  |  | -0.03039 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  |  |  | -0.0305
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 61.1 |  |  | -0.03058 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 101.27 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 0.19 |  |  | -0.03058 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
918421 | AA1-056 | 345 | 202 | 58 | 0 | 46 | 0 |  |  | -0.03061 |  |  |  | 0.036 |  | 1 | ENERGY |  |  |  | 1
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.03064 |  |  |  | 0.036 |  | 1 | NEW | AB1-107 |  |  | 1
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 0 |  |  | -0.03066 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 0 |  |  | -0.03066 |  |  |  | 0 |  | 1 | NEW | AB1-107 |  |  | 1
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 124.58 |  |  | -0.03066 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.03066 |  |  |  | 0 |  | 1 | CAPACITY | OREGON |  |  | 1
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 95.74 |  |  | -0.03066 |  |  |  | 0.036 |  | 1 | CAPACITY | OREGON |  |  | 1
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 1.46 |  |  | -0.03078 |  |  |  | 0 |  | 1 | NEW |  |  |  | 0.1
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 0.19 |  |  | -0.03167 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 8.4 |  |  | -0.0321 |  |  |  | 0.13361 |  | 1 | CAPACITY |  |  |  | 1
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.03214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.7 | 45.71 |  |  | -0.03214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.2 | 45.52 |  |  | -0.03214 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 0.16 |  |  | -0.03214 |  |  |  | 0.1042 |  | 1 | CAPACITY |  |  |  | 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.03228 |  |  |  | 0 |  | 1 | NEW | R60 2 |  |  | 0.8
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 84.93 | 40.92 |  |  | -0.03228 |  |  |  | 0 |  | 1 | NEW | R60 1 |  |  | 0.8
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 84.83 | 40.87 |  |  | -0.03228 |  |  |  | 0 |  | 1 | NEW | R60 3 |  |  | 0.8
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 7.95 |  |  | -0.03228 |  |  |  | 0 |  | 1 | CAPACITY | R60 3 |  |  | 0.8
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.03228 |  |  |  | 0 |  | 1 | CAPACITY | R60 2 |  |  | 0.8
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 7.9 |  |  | -0.03228 |  |  |  | 0 |  | 1 | CAPACITY | R60 1 |  |  | 0.8
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 41.92 |  |  | -0.03304 |  |  |  | 0 |  | 1 | NEW | V1-011 |  |  | 0.8
247607 | V1-011 GEN | 0.69 | 205 | 74 | 0 | 13 | 6.26 |  |  | -0.03304 |  |  |  | 0 |  | 1 | CAPACITY | V1-011 |  |  | 0.8
243017 | 05HAVILAND1 | 138 | 205 | 77 | 0 | 4.5 | 3.22 |  |  | -0.03304 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 174.1 | 83.88 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | S06 |  |  | 0.8
930042 | AB1-006 E2 | 0.69 | 205 | 74 | 0 | 96.75 | 46.61 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 0.8
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 88.2 | 42.49 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T127 4 |  |  | 0.8
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 84.8 | 40.86 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T126 2 |  |  | 0.8
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 84.7 | 40.81 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T126 3 |  |  | 0.8
247943 | T-127 E | 0.69 | 205 | 74 | 0 | 79.8 | 38.45 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | T127 5 |  |  | 0.8
930041 | AB1-006 E1 | 0.69 | 205 | 74 | 0 | 77.25 | 37.22 |  |  | -0.03333 |  |  |  | 0 |  | 1 | NEW | AB1-006 |  |  | 0.8
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 12.48 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | S06 |  |  | 0.8
270180 | AB1-006 W1 | 0.65 | 205 | 74 | 0 | 22.75 | 10.96 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 0.8
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 9.73 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T127 5 |  |  | 0.8
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 7.37 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T126 3 |  |  | 0.8
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 7.32 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T126 2 |  |  | 0.8
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 5.68 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | T127 4 |  |  | 0.8
270181 | AB1-006 W2 | 0.69 | 205 | 74 | 0 | 3.25 | 1.57 |  |  | -0.03333 |  |  |  | 0 |  | 1 | CAPACITY | AB1-006 |  |  | 0.8
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 57.21 |  |  | -0.03363 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 57.17 |  |  | -0.03363 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149 | 56.9 |  |  | -0.03363 |  |  |  | 0.0692 |  | 1 | CAPACITY |  |  |  | 1
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 57.82 |  |  | -0.03405 |  |  |  | 0 |  | 1 | NEW | T131 |  |  | 0.8
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 76.1 | 36.67 |  |  | -0.03406 |  |  |  | 0 |  | 1 | NEW | R49 |  |  | 0.8
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 31.8 |  |  | -0.03405 |  |  |  | 0 |  | 1 | NEW | AC1-173 |  |  | 0.8
247521 | T131 | 0.69 | 205 | 74 | 26.1 | 30 | 14.45 |  |  | -0.03405 |  |  |  | 0 |  | 1 | CAPACITY | T131 |  |  | 0.8
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 11.03 |  |  | -0.03406 |  |  |  | 0 |  | 1 | CAPACITY | R49 |  |  | 0.8
270191 | AC1-173 C | 0.65 | 205 | 74 | 0 | 9.9 | 4.77 |  |  | -0.03405 |  |  |  | 0 |  | 1 | CAPACITY | AC1-173 |  |  | 0.8
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1186 | 1186 |  |  | -0.04004 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247529 | 05COVRT2 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.04241 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 2 |  |  | 1
247530 | 05COVRT3 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.04241 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247528 | 05COVRT1 | 16 | 205 | 58 | 191.2 | 219.8 | 83.94 |  |  | -0.04241 |  |  |  | 0.036 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.04241 |  |  |  | 0 |  | 1 | CAPACITY | Covert 3 |  |  | 1
247531 | 05COVRT4 | 16.5 | 205 | 58 | 115 | 132.2 | 50.49 |  |  | -0.04241 |  |  |  | 0 |  | 1 | CAPACITY | Covert 1 |  |  | 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 114.1 | 131.2 | 50.11 |  |  | -0.04241 |  |  |  | 0 |  | 1 | CAPACITY | Covert 2 |  |  | 1
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 1014.5 |  |  | -0.04383 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.02 |  |  | -0.04384 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.04398 |  |  |  | 0.036 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 143.6 |  |  | -0.04398 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 127.17 |  |  | -0.04398 |  |  |  | 0 |  | 1 | CAPACITY | AA2-116 |  |  | 1
247604 | X1-042 | 12 | 205 | 64 | 0 | 3.8 | 2.55 |  |  | -0.04411 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.04415 |  |  |  | 0 |  | 1 | CAPACITY | Z2-113 |  |  | 0.1
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0.17 |  |  | -0.04415 |  |  |  | 0 |  | 1 | NEW | Z2-113 |  |  | 0.1
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.3 | 0.72 |  |  | -0.04424 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 1.75 |  |  | -0.04442 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.04448 |  |  |  | 0 |  | 1 | CAPACITY | Z2-116 |  |  | 0.1
247969 | Z2-116 E | 138 | 205 | 75 | 0 | 1.3 | 0.09 |  |  | -0.04448 |  |  |  | 0 |  | 1 | NEW | Z2-116 |  |  | 0.1
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 2.16 |  |  | -0.04452 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 3.33 |  |  | -0.04493 |  |  |  | 0.0789 |  | 1 | CAPACITY |  |  |  | 1
246476 | 05NILES | 34.5 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.04547 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246477 | 05NILES | 69 | 205 | 77 | 0 | 1.3 | 0.93 |  |  | -0.04547 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 3.89 |  |  | -0.04559 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.6 | 1.44 |  |  | -0.04571 |  |  |  | 0 |  | 1 | CAPACITY |  |  |  | 1
243352 | 05NTRDAM | 138 | 205 | 77 | 0 | 57.6 | 41.21 |  |  | -0.04579 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
244415 | 05OLIV SLR C | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.0481 |  |  |  | 0 |  | 1 | CAPACITY | OLIV SLR |  |  | 0.1
247967 | 05OLIV SLR E | 138 | 205 | 75 | 0 | 2.5 | 0.18 |  |  | -0.0481 |  |  |  | 0 |  | 1 | NEW | OLIV SLR |  |  | 0.1
243353 | 05OLIVE | 138 | 205 | 77 | 0 | 5 | 3.58 |  |  | -0.0481 |  |  |  | 0 |  | 1 | NEWENERGY |  |  |  | 1
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 95.86 |  |  | -0.05079 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.05079 |  |  |  | 0.036 |  | 1 | CAPACITY | X2-052 |  |  | 1
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 88.6 |  |  | -0.05079 |  |  |  | 0 |  | 1 | CAPACITY | X2-052 |  |  | 1
MDU | PJM->LTFIMP_MDU |  |  | LTF |  | 10.1 |  |  |  | -0.0876