## Thermal
2026 RTEP PJM N-1 Thermal Result (Winter)
FG# | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | AC Ld(%) | Cont Type | Contingency | Transformer/Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusion | Comments
N1-W-T18 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69/69 | 363/320 | 141 | 101.21 | Line_FB | 'EKPC_P2-3_COOP S42-1014_SRT-A' | N/A | No |  | limited by non PJM facility, EKPC side ratings WN/WE = 172/178
| Note: |  | The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO/TO

## Votlage Magnitude
2026 RTEP PJM N-1 Voltage Magnitude Result (Winter)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Low/High Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusion | Comments
N1-WVM1 | 200909 | 26LOBO+ | 230 | 226 | 1.0553 | 1.0345 | 1.05 | Line_FB | PN_P2-3_PN-230-3262B_SRT-A | YES
N1-WVM2 | 200908 | 26CHAPMAN+ | 230 | 226 | 1.0501 | 1.034 | 1.05 | Line_FB | PN_P2-3_PN-230-3262B_SRT-A | YES
N1-WVM3 | 200857 | 26MARSHALL | 230 | 226 | 1.0652 | 1.0336 | 1.05 | Line_FB | PN_P2-3_PN-230-3262B_SRT-A | YES
N1-WVM4 | 200701 | 26GROVER | 230 | 226 | 1.0682 | 1.0315 | 1.05 | Line_FB | PN_P2-3_PN-230-3262B_SRT-A | YES