## Summary
2026 RTEP PJM Generation Deliverability Result (Winter)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Transformer/Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusion | Comments
GD-W193 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1636.6 | 1684.1 | 105.11 | 108.16 | AEP_P1-2_#695_1681_SRT-A | Single | WSTE=1658 for PJM side | No |  | The flowgate is on hold. Deactivation of Byron units 1&2, Waukegan units 7&8 and Will County unti 4 have significant impact on this flowgate
GD-W194 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1636.6 | 1684.1 | 105.11 | 108.16 | 765-L11215_-S_SRT-A | Single | WSTE=1658 for PJM side | No |  | The flowgate is on hold. Deactivation of Byron units 1&2, Waukegan units 7&8 and Will County unti 4 have significant impact on this flowgate
GD-245 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 186 | 205.6 | 196.4 | 110.54 | 105.61 | DVP_P7-1: LN 2058-2181_SRT-A | Tower | N/A | No | Pending coordination with external entity | Limited by Non PJM facility. Dominion rating is 251/266/274 for WN/WE/WLD
GD-W8 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363/320 | 141 | 141.3 | 146.2 | 100.19 | 103.67 | EKPC_P2-3_COOP S42-1014_SRT-A | Breaker | N/A | No | Pending coordination with external entity | Limited to Non PJM facility. EKPC rating is 172/178 for WN/WE
GD-W30 | 232233 | PRESTON | 232234 | TODD | 1 | 69 | 235 | 105 | 101.6 | 105.7 | 96.8 | 100.66 | DPL_P4-2_DP11_SRT-A | Breaker | WN/WE =157/195 | No | Substation Equipment exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-W248 | 232107 | TOWNSEND | 232100 | CHURCH | 1 | 138 | 235 | 389 | 368.7 | 390.1 | 94.78 | 100.28 | DPL_P7_1_DBL_1NCB_FSA_SRT-A | Tower | WN/WE =451/546 | No | Substation Equipment exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
| NOTE: |  | The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO/TO