## Sheet1
Percentage of correct off-cost operations projections February 2002: 67.9% (19/28 0 days - no forecast given on OASIS)
Off-Cost Operations - Projection History February 2002
Date | Projected | Occurred | Facility | Contingency | Begin Time | End Time | Begin Time | End Time
2002-02-01 | No | Yes | Erie West #1 345/115kV xfmr | Erie South - Erie West 345kV | 1:16 | 4:05
|  |  | Erie West #1 345/115kV xfmr | Erie South - Erie West 345kV + Seneca Pump | 7:44 | 8:30 | 11:32 | 11:55
|  |  | Keeney AT51 500/230kV xfmr | Keeney AT50 500/230kV xfmr | 17:37 | 18:34
2002-02-02 | Yes | No
2002-02-03 | No | No
2002-02-04 | Yes | Yes | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 6:50 | 7:50 | 17:46 | 21:52
|  |  | Delco Tap - Mickleton | Hope Creek - Red Lion | 23:46 | 2:18
2002-02-05 | Yes | Yes | Delco Tap - Mickleton | Hope Creek - Red Lion | 4:33 | 6:02
|  |  | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 5:36 | 8:30 | 17:17 | 21:39
|  |  | Cly - Collins 115kV | Gardners - Hunterstown 115kV | 6:38 | 8:25
|  |  | Branchburg #1 500/230kV xfmr | Branchburg #2 500/230kV xfmr | 17:27 | 20:20
2002-02-06 | Yes | Yes | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 7:24 | 7:50
2002-02-07 | Yes | Yes | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 7:18 | 8:50
|  |  | Western Transfers | Reactive | 16:52 | 17:11 | 17:41 | 18:05
2002-02-08 | Yes | Yes | Hosensack - N Temple 230kV | Hosensack #4 | 11:59 | 13:28
|  |  | Cedar Grove - Roseland F2206 230kV | Cedar Grove - Roseland B2228 230kV | 21:58 | 0:09
2002-02-09 | No | Yes | Cedar Grove - Roseland B2228 230kV | Cedar Grove - Roseland F2206 230kV | 10:50 | 15:47
|  |  | Cedar Grove - Roseland B2228 230kV | Cedar Grove - Roseland F2206 230kV | 17:30 | 19:59
2002-02-10 | No | Yes | Cedar Grove - Roseland F2206 230kV | Cedar Grove - Roseland B2228 230kV | 15:30 | 18:04 | 19:11 | 20:44
2002-02-11 | No | No
2002-02-12 | No | Yes | Erie West #1 345/115kV xfmr | Erie South - Erie West 345kV | 2:07 | 4:56
|  |  | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 6:15 | 7:50
2002-02-13 | No | No
2002-02-14 | No | Yes | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 5:43 | 8:40
2002-02-15 | No | Yes | Red Lion AT20 230/138kV xfmr | Harmony AT20 230/138kV xfmr | 6:01 | 9:00
|  |  | Preston - Todd 69kV | Vienna AT20 230/138kV xfmr | 6:28 | 9:00
2002-02-16 | No | No
2002-02-17 | No | No
2002-02-18 | No | Yes | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 6:15 | 10:28
2002-02-19 | No | Yes | Church AT2 138/69kV xfmr | Cedar Creek - Red Lion 23030 230kV | 6:23 | 6:30
2002-02-20 | No | No
2002-02-21 | Yes | Yes | Shieldalloy - Vineland 69kV | Cardiff - New Freedom 230kV | 3:50 | 5:02
|  |  | Beckett - Paulsboro 69kV | Chambers - Churchtown 230kV | 6:30 | 7:04 | 10:35 | 13:40
2002-02-22 | No | No
2002-02-23 | No | No
2002-02-24 | No | No
2002-02-25 | Yes | Yes | Edison - Meadow Rd 138kV | Devilsbrook-Plainsboro-Trenton 138kV | 12:57 | 18:25
2002-02-26 | Yes | Yes | Preston - Todd 69kV | Indian River - Milford 230kV | 9:02 | 9:30
|  |  | Talbot - Trappe Tap 69kV | Indian River - Milford 230kV | 12:09 | 12:38 | 16:00 | 18:19
2002-02-27 | No | No
2002-02-28 | No | No
Formulas:
Date = +[Date, row above]+1