## Data Input
Aerial Conductor Ampacity and Thermal Rating
This spreadsheet is based on the overhead conductor methodology as set forth in: IEEE Standard for Calculation the Current-Temperature of Bare Overhead Conductors, IEEE 738™-2006
Project Information
|  |  | Line number or general title: | Line 1234
|  |  | Line description: | Substation A to Substation B
|  |  | Element description: | Line Conductor
|  |  | Prepared by: | Mark Shuck
|  |  | Date prepared: | 2026-07-30 06:24
Conductor Data
Select conductor:
|  |  | Number of conductors per phase: | 1
|  |  | Emissivity (e): | 0.7
|  |  | Absorptivity (a): | 0.9
Conductor Internal & Generated Data
|  |  | Name: |  |  | Overall conductor diameter (in.):
|  |  | Type: |  |  | Low Resistance Temp. (˚C):
|  |  | Size (kcmil): |  |  | Low Temp Resistance (Ω/ 1000ft.):
|  |  | Governing conductor specification: |  |  | High Resistance Temp. (˚C):
High Temp Resistance (Ω/ 1000ft.):
Solar and Geographic Data
|  |  | Latitude (˚N): | 40 |  |  |  | Month: | June
|  |  | Elevation Above Sea Level (ft.): | 200 |  |  |  | Day: | 10
Solar and Geographic Internal & Generated Data | [7 empty] | Hc: Altitude of the sun (˚): | 59.536
|  |  | Suntime (hours): | 14:00 |  |  |  | Qse: Total heat flux (W/ft2): | 71.9867
|  |  | Atmosphere: | Industrial |  |  |  | Zc: Azimuth of the sun (˚): | 65.185
|  |  | Kangle (Wind direction factor): | 1 |  |  |  | θ: Effective angle of incidence of the sun's rays (˚): | 62.601
Max. Allowable Cond. Temp. (˚C) | [7 empty] | At a Glance Rating (Single Conductor)
Spec | Type | Normal | Emerg. |  | Rating Parameters |  |  |  | Planning Rating (A) | Normal | Emerg. | Load Dump
ASTM B 232 | ACSR | 140 | 140 |  |  | Max. Cond. Temp. - Normal (˚C): |  |  | Summer Daytime
ASTM B 524 | ACAR | 100 | 100 |  |  | Wind speed, normal rating (fps): | 0 |  | Summer Nighttime
ASTM B 231 | AAC | 85 | 110 |  |  | Max. Cond. Temp. - Emergency (˚C): |  |  | Winter Daytime
ASTM B 856 | ACSS | 250 | 250 |  |  | Wind speed, emergency rating (fps): | 2.533 |  | Winter Nighttime
ASTM B 857 | ACSSTW | 250 | 250 |  |  | Angle between wind and conductor (˚): | 90 | #VALUE!
ACCC | ACCC | 200 | 200
ACCR | ACCR | 200 | 200
ASTM B 8 | Copper | 85 | 120
AAAC | AAAC | 95 | 135

## Load Dump (hidden)
| Day |  |  |  | Night
| Normal | Emergency |  | Wind (f/s) | Normal | Emergency |  | Material | mCp |  |  |  |  | AAAC
Wind (f/s) | 0 | 2.533 |  |  | 0 | 2.533 |  | Aluminum | 433 |  |  |  |  | AAC
qr: | 0 | 0 |  | qr: | 0 | 0 |  | Copper | 192 |  |  |  |  | AACSR
qs: | 0 | 0 |  | qs: | 0 | 0 |  | Steel | 216 |  |  |  |  | AACTW
qc: | 0.57606 | 0.57606 |  | qc: | 0.56882 | 0.56882 |  | Alumoweld | 242 |  |  |  |  | ACAR
Initial Current: | #DIV/0! | #DIV/0! |  | Initial Current: | #DIV/0! | #DIV/0! | [7 empty] | ACCC
[9 empty] | Aluminum | Steel | Copper | Alumonweld | Total mCp | ACCR
[8 empty] | mCp: | 0.7491 | 0.3443 |  |  |  | ACSR
[9 empty] | 324.3603 | 74.3688 | 0 | 0 | 398.7291 | ACSRTW
Wind (f/s) | 0 | 2.533 |  | Wind (f/s) | 0 | 2.533 | [7 empty] | ACSS
qc0 | 0 | 0 |  | qc0 | 0 | 0 | [7 empty] | ACSSTW
qc1 | 0.57606 | 0.57606 |  | qc1 | 0.56882 | 0.56882 | [7 empty] | HD Copper
qc2 | 0 | 0 |  | qc2 | 0 | 0
pf: | 0.063438 | 0.063438 |  | pf: | 0.063506 | 0.063506
uf: | 0.049666 | 0.049666 |  | uf: | 0.049626 | 0.049626
kf: | 0.0090137 | 0.0090137 |  | kf: | 0.0090054 | 0.0090054
R(Tc): | #DIV/0! | #DIV/0! |  | R(Tc): | #DIV/0! | #DIV/0!
| Conductor Temperature: | 103.276 |  |  | Conductor Temperature: | 102.5391
| Ambient Air Temperature: | 40 |  |  | Ambient Air Temperature: | 40
| Maximum Conductor Temperature: | 140 |  |  | Maximum Conductor Temperature: | 140
| Day |  |  |  | Night
| Initial Temperature (Ti): | 103.276 |  |  | Initial Temperature: | 102.5391
| Initial Current (Ii): | 1112.6869 |  |  | Initial Current: | 1185.491
| Final Temperature (Tf): | 154.6181 |  |  | Final Temperature: | 155.4583
| Temperature @ t15 (Tc): | 140 | 11.9403 |  | Temperature @ t15: | 140 | 12.189
| Time Constant (tau): | #DIV/0! |  |  | Time Constant: | #DIV/0!
| Final Current (If): | 1494.7684 |  |  | Final Current: | 1553.5329

## Rating Report
Line Rating: Aerial Conductor Element
General data
| Line number or general title: | Line 1234
| Line description: | Substation A to Substation B
| Element description: | Line Conductor
| Date prepared: | 2026-07-30 06:24 |  | Prepared by: | Mark Shuck
Conductor data
| Size: |  |  |  | Name: | 0
| Conductor specification: | 0 |  |  | Low Resistance Temp. (˚C): | 0
| Number per phase: | 1 |  |  | Low Temp Resistance (Ω/1000ft.): | 0
| Overall Diameter (in.): | 0 |  |  | High Resisitance Temp. (˚C): | 0
| Emissivity (e): | 0.7 |  |  | High Temp Resistance (Ω/1000ft.): | 0
| Absorptivity (a): | 0.9
Solar and Geographic Data
| Latitude (˚N): | 40 |  |  | Atmosphere: | Industrial
| Elevation Above Sea Level (ft.): | 200 |  |  | Kangle (Wind direction factor): | 1
| Suntime (hours): | 14:00
Rating Parameters
| Max. Cond. Temp. - Normal (˚C): | 0 |  |  | Max. Cond. Temp. - Emergency (˚C): | 0
| Wind speed, normal rating (fps): | 0 |  |  | Wind speed, emergency rating (fps): | 2.533
[5 empty] | Z1: Angle between wind and conductor (˚): | 90
Ratings calculated per IEEE 738™-2006
Aerial Conductor Thermal Rating
Ambient Temperature (˚C) |  | Daytime Rating |  |  | Nighttime Rating
Condition | Temp. | Normal (A) | Emergency (A) | Load Dump (A) | Normal (A) | Emergency (A) | Load Dump (A)
| -15 | 1417.6177 | 1718.4854 | 1856.3347 | 1475.4514 | 1766.4962 | 1906.5933
| -10 | 1392.4529 | 1693.2113 | 1826.6357 | 1451.2897 | 1741.9189 | 1877.4112
| -5 | 1366.8963 | 1667.3616 | 1796.443 | 1426.7875 | 1716.8027 | 1847.775
| 0 | 1340.9153 | 1640.9 | 1765.7183 | 1401.9168 | 1691.1149 | 1817.6479
| 5 | 1314.4742 | 1613.7869 | 1734.4444 | 1376.6479 | 1664.8198 | 1786.9905
Winter Planning | 10 | 1287.5341 | 1585.979 | 1702.4935 | 1350.9481 | 1637.8785 | 1755.7603
| 15 | 1260.0523 | 1557.429 | 1669.8967 | 1324.7825 | 1610.249 | 1723.9117
| 20 | 1231.982 | 1528.085 | 1636.5717 | 1298.1127 | 1581.8851 | 1691.3944
| 25 | 1203.2714 | 1497.8895 | 1602.4583 | 1270.8969 | 1552.7362 | 1658.156
| 30 | 1173.863 | 1466.7787 | 1567.5261 | 1243.0893 | 1522.7464 | 1624.1373
Summer Planning | 35 | 1143.6922 | 1434.6817 | 1531.6499 | 1214.6394 | 1491.8541 | 1589.2994
| 40 | 1112.6869 | 1401.5187 | 1494.7684 | 1185.491 | 1459.9903 | 1553.5329
Spreadsheet developed by the PJM Transmission and Substations Design Subcommittee. Modified by PECO Energy
#VALUE!

## Day Chart
DAY - Steady State Thermal Rating (Ampacity), Amperes
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
|  | Cond. Max. Op Temp. (˚C): | Normal: |  | 0 | Emergency: |  | 0 | Ampacity is per conductor or subconductor
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | Plan. Winter 10 | 15 | 20 | 25 | 30 | Plan. Summer 35 | 40
| (ft./sec.) | (˚C)
Normal Day | 0 | 110 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Day | 2.533 | 110 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Day | 0 | 120 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Day | 2.533 | 120 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Day | 0 | 130 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Day | 2.533 | 130 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Day | 0 | 140 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Day | 2.533 | 140 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Day | 0 | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Day | 2.533 | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Day | 0 | 160 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Day | 2.533 | 160 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Day | 0 | 170 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Day | 2.533 | 170 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Night Chart
NIGHT - Steady State Thermal Rating (Ampacity), Amperes
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
|  | Cond. Max. Op Temp. (˚C): | Normal: |  | 0 | Emergency: |  | 0 | Ampacity is per conductor or subconductor
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | Plan. Winter 10 | 15 | 20 | 25 | 30 | Plan. Summer 35 | 40
| (ft./sec.) | (˚C)
Normal Night | 0 | 110 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Night | 2.533 | 110 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Night | 0 | 120 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Night | 2.533 | 120 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Night | 0 | 130 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Night | 2.533 | 130 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Night | 0 | 140 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Night | 2.533 | 140 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Night | 0 | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Night | 2.533 | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Night | 0 | 160 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Night | 2.533 | 160 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal Night | 0 | 170 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency Night | 2.533 | 170 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Day Normal
Daytime Ampacity - Normal Conditions
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
|  | Cond. Max. Op Temp. (˚C): | Normal: |  | 0 | Emergency: |  | 0 | Ampacity is per conductor or subconductor
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | Plan. Winter 10 | 15 | 20 | 25 | 30 | Plan. Summer 35 | 40
| (ft./sec.) | (˚C)
Normal Day | 0 | 110 | 1259.2212 | 1229.5128 | 1199.1979 | 1168.2185 | 1136.5095 | 1103.9975 | 1070.5991 | 1036.2187 | 1000.7462 | 964.0524 | 925.985 | 886.3612
Normal Day | 0 | 120 | 1314.3651 | 1286.3443 | 1257.8052 | 1228.7009 | 1198.9792 | 1168.5823 | 1137.4454 | 1105.4956 | 1072.6499 | 1038.8137 | 1003.8776 | 967.714
Normal Day | 0 | 130 | 1367.0395 | 1340.5223 | 1313.5568 | 1286.1041 | 1258.1215 | 1229.5622 | 1200.3743 | 1170.5001 | 1139.8749 | 1108.4263 | 1076.0718 | 1042.7173
Normal Day | 0 | 140 | 1417.6177 | 1392.4529 | 1366.8963 | 1340.9153 | 1314.4742 | 1287.5341 | 1260.0523 | 1231.982 | 1203.2714 | 1173.863 | 1143.6922 | 1112.6869
Normal Day | 0 | 150 | 1466.4087 | 1442.47 | 1418.1862 | 1393.5291 | 1368.4684 | 1342.9713 | 1317.0021 | 1290.5218 | 1263.4878 | 1235.8532 | 1207.5664 | 1178.5696
Normal Day | 0 | 160 | 1513.6719 | 1490.8525 | 1467.7267 | 1444.2701 | 1420.4565 | 1396.2577 | 1371.6432 | 1346.5803 | 1321.0329 | 1294.9623 | 1268.3257 | 1241.0762
Normal Day | 0 | 170 | 1559.6276 | 1537.8359 | 1515.7704 | 1493.4096 | 1470.7308 | 1447.7092 | 1424.3188 | 1400.5311 | 1376.3156 | 1351.6393 | 1326.4663 | 1300.7576

## Night Normal
Nighttime Ampacity - Normal Conditions
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
|  | Cond. Max. Op Temp. (˚C): | Normal: |  | 0 | Emergency: |  | 0 | Ampacity is per conductor or subconductor
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | Plan. Winter 10 | 15 | 20 | 25 | 30 | Plan. Summer 35 | 40
| (ft./sec.) | (˚C)
Normal Night | 0 | 110 | 1329.383 | 1301.2774 | 1272.6731 | 1243.5255 | 1213.7854 | 1183.3983 | 1152.3036 | 1120.4332 | 1087.7105 | 1054.0484 | 1019.3475 | 983.4924
Normal Night | 0 | 120 | 1379.9074 | 1353.2445 | 1326.1459 | 1298.5741 | 1270.4881 | 1241.8427 | 1212.5885 | 1182.6704 | 1152.0272 | 1120.5904 | 1088.2827 | 1055.0162
Normal Night | 0 | 130 | 1428.5045 | 1403.1493 | 1377.4104 | 1351.2556 | 1324.65 | 1297.5558 | 1269.9316 | 1241.732 | 1212.9067 | 1183.4005 | 1153.1515 | 1122.0906
Normal Night | 0 | 140 | 1475.4514 | 1451.2897 | 1426.7875 | 1401.9168 | 1376.6479 | 1350.9481 | 1324.7825 | 1298.1127 | 1270.8969 | 1243.0893 | 1214.6394 | 1185.491
Normal Night | 0 | 150 | 1520.9836 | 1497.9173 | 1474.5469 | 1450.848 | 1426.7945 | 1402.3582 | 1377.509 | 1352.2142 | 1326.4381 | 1300.1423 | 1273.2844 | 1245.8182
Normal Night | 0 | 160 | 1565.3028 | 1543.247 | 1520.9181 | 1498.2944 | 1475.3531 | 1452.0694 | 1428.417 | 1404.3676 | 1379.8906 | 1354.9529 | 1329.5187 | 1303.549
Normal Night | 0 | 170 | 1608.5831 | 1587.4635 | 1566.0974 | 1544.4655 | 1522.5473 | 1500.3211 | 1477.7636 | 1454.85 | 1431.5537 | 1407.8459 | 1383.6959 | 1359.0702

## Day Emergency
Daytime Ampacity - Emergency Conditions
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
|  | Cond. Max. Op Temp. (˚C): | Normal: |  | 0 | Emergency: |  | 0 | Ampacity is per conductor or subconductor
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | Plan. Winter 10 | 15 | 20 | 25 | 30 | Plan. Summer 35 | 40
| (ft./sec.) | (˚C)
Emergency Day | 2.533 | 110 | 1565.4314 | 1535.1867 | 1504.1061 | 1472.1254 | 1439.1727 | 1405.1675 | 1370.019 | 1333.6235 | 1295.8624 | 1256.5983 | 1215.6706 | 1172.8897
Emergency Day | 2.533 | 120 | 1618.8677 | 1590.4749 | 1561.3512 | 1531.4444 | 1500.6968 | 1469.0444 | 1436.4157 | 1402.7305 | 1367.8983 | 1331.8159 | 1294.3655 | 1255.4102
Emergency Day | 2.533 | 130 | 1669.7558 | 1643.0079 | 1615.6143 | 1587.5318 | 1558.7129 | 1529.1055 | 1498.6522 | 1467.289 | 1434.9448 | 1401.5396 | 1366.9831 | 1331.1728
Emergency Day | 2.533 | 140 | 1718.4854 | 1693.2113 | 1667.3616 | 1640.9 | 1613.7869 | 1585.979 | 1557.429 | 1528.085 | 1497.8895 | 1466.7787 | 1434.6817 | 1401.5187
Emergency Day | 2.533 | 150 | 1765.3798 | 1741.4358 | 1716.975 | 1691.9661 | 1666.3756 | 1640.1672 | 1613.3011 | 1585.7343 | 1557.4194 | 1528.3046 | 1498.3325 | 1467.4394
Emergency Day | 2.533 | 160 | 1810.7103 | 1787.9746 | 1764.7715 | 1741.0742 | 1716.8538 | 1692.0792 | 1666.7167 | 1640.73 | 1614.0795 | 1586.722 | 1558.6103 | 1529.6924
Emergency Day | 2.533 | 170 | 1854.7068 | 1833.0747 | 1811.0175 | 1788.5118 | 1765.5326 | 1742.0528 | 1718.0436 | 1693.4738 | 1668.3099 | 1642.5153 | 1616.0504 | 1588.8722

## Night Emergency
Nighttime Ampacity - Emergency Conditions
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
|  | Cond. Max. Op Temp. (˚C): | Normal: |  | 0 | Emergency: |  | 0 | Ampacity is per conductor or subconductor
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | Plan. Winter 10 | 15 | 20 | 25 | 30 | Plan. Summer 35 | 40
| (ft./sec.) | (˚C)
Emergency Night | 2.533 | 110 | 1622.4045 | 1593.2418 | 1563.3158 | 1532.5711 | 1500.9461 | 1468.3722 | 1434.7728 | 1400.0617 | 1364.1409 | 1326.8988 | 1288.2066 | 1247.9148
Emergency Night | 2.533 | 120 | 1672.5195 | 1645.053 | 1616.9126 | 1588.0525 | 1558.4222 | 1527.966 | 1496.6225 | 1464.3229 | 1430.9907 | 1396.5395 | 1360.8713 | 1323.8744
Emergency Night | 2.533 | 130 | 1720.4396 | 1694.4919 | 1667.9441 | 1640.7574 | 1612.8898 | 1584.2953 | 1554.9232 | 1524.718 | 1493.6179 | 1461.5543 | 1428.4505 | 1394.2198
Emergency Night | 2.533 | 140 | 1766.4962 | 1741.9189 | 1716.8027 | 1691.1149 | 1664.8198 | 1637.8785 | 1610.249 | 1581.8851 | 1552.7362 | 1522.7464 | 1491.8541 | 1459.9903
Emergency Night | 2.533 | 150 | 1810.9673 | 1787.634 | 1763.814 | 1739.4787 | 1714.5975 | 1689.1374 | 1663.0626 | 1636.3343 | 1608.9102 | 1580.744 | 1551.7851 | 1521.9773
Emergency Night | 2.533 | 160 | 1854.0879 | 1831.8906 | 1809.2508 | 1786.1437 | 1762.5428 | 1738.4194 | 1713.7429 | 1688.4801 | 1662.5952 | 1636.0491 | 1608.7996 | 1580.8001
Emergency Night | 2.533 | 170 | 1896.0587 | 1874.9037 | 1853.3445 | 1831.359 | 1808.9241 | 1786.0149 | 1762.6046 | 1738.6647 | 1714.1643 | 1689.0701 | 1663.3461 | 1636.9533

## HD Copper
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Cu Weight | Spec |  | Values From
HD Copper
2 - 7 | 2 - 7 | 2 | 7 |  | 0.0974 |  |  | 0.2922 |  |  |  | 25 | 0.8921 | 75 | 1.0579 | 204.9 | ASTM B 8 | 2 - 7 | Southwire
1/0 - 7 | 1/0 - 7 | 1/0 | 7 |  | 0.1228 |  |  | 0.3684 |  |  |  | 25 | 0.5615 | 75 | 0.6658 | 325.9 | ASTM B 8 | 1/0 - 7 | Southwire
4/0 - 7 | 4/0 - 7 | 4/0 | 7 |  | 0.1739 |  |  | 0.522 |  |  |  | 20 | 0.27561 | 100 | 0.34851 | 653.3 | ASTM B 8 | 4/0 - 7 | Old Pjm
250 - 19 | 250 - 19 | 250 | 19 |  | 0.1147 |  |  | 0.5735 |  |  |  | 25 | 0.2380 | 75 | 0.2819 | 772 | ASTM B 8 | 250 - 19 | Southwire
500 - 19 | 500 - 19 | 500 | 19 |  | 0.1622 |  |  | 0.811 |  |  |  | 20 | 0.11825 | 100 | 0.14953 | 1544 | ASTM B 8 | 500 - 19 | Old Pjm
1000 - 37 | 1000 - 37 | 1000 | 37 |  | 0.1644 |  |  | 1.1508 |  |  |  | 25 | 0.0640 | 75 | 0.0744 | 3088 | ASTM B 8 | 1000 - 37 | Southwire

## AAAC
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
AAAC
30.58 7 | Akron | 30.58 | 7 |  | 0.0661 |  |  | 0.198 |  |  |  | 25 | 3.5394 | 75 | 4.1430 | 28.5 |  | AAAC | 30.58 7 Akron | Southwire
48.69 7 | Alton | 48.69 | 7 |  | 0.0834 |  |  | 0.250 |  |  |  | 25 | 2.2235 | 75 | 2.6026 | 45.4 |  | AAAC | 48.69 7 Alton | Southwire
77.47 7 | Ames | 77.47 | 7 |  | 0.1052 |  |  | 0.316 |  |  |  | 25 | 1.3973 | 75 | 1.6355 | 72.2 |  | AAAC | 77.47 7 Ames | Southwire
123.3 7 | Azusa | 123.3 | 7 |  | 0.1327 |  |  | 0.398 |  |  |  | 25 | 0.8782 | 75 | 1.0278 | 114.9 |  | AAAC | 123.3 7 Azusa | Southwire
155.4 7 | Anaheim | 155.4 | 7 |  | 0.1490 |  |  | 0.447 |  |  |  | 25 | 0.6969 | 75 | 0.8156 | 144.9 |  | AAAC | 155.4 7 Anaheim | Southwire
195.7 7 | Amherst | 195.7 | 7 |  | 0.1672 |  |  | 0.502 |  |  |  | 25 | 0.5536 | 75 | 0.6478 | 182.5 |  | AAAC | 195.7 7 Amherst | Southwire
246.9 7 | Alliance | 246.9 | 7 |  | 0.1878 |  |  | 0.563 |  |  |  | 25 | 0.4391 | 75 | 0.5137 | 230.2 |  | AAAC | 246.9 19 Amarillo | Southwire
246.9 19 | Amarillo | 246.9 | 19 |  | 0.1140 |  |  | 0.570 |  |  |  | 25 | 0.4391 | 75 | 0.5137 | 230.3 |  | AAAC | 246.9 7 Alliance | Southwire
312.8 19 | Butte | 312.8 | 19 |  | 0.1283 |  |  | 0.642 |  |  |  | 25 | 0.3469 | 75 | 0.4058 | 291.6 |  | AAAC | 312.8 19 Butte | Southwire
394.5 19 | Canton | 394.5 | 19 |  | 0.1441 |  |  | 0.721 |  |  |  | 25 | 0.2755 | 75 | 0.3221 | 367.9 |  | AAAC | 394.5 19 Canton | Southwire
465.4 19 | Cairo | 465.4 | 19 |  | 0.1565 |  |  | 0.783 |  |  |  | 25 | 0.2339 | 75 | 0.2733 | 433.9 |  | AAAC | 465.4 19 Cairo | Southwire
559.5 19 | Darien | 559.5 | 19 |  | 0.1716 |  |  | 0.858 |  |  |  | 25 | 0.1950 | 75 | 0.2278 | 521.7 |  | AAAC | 559.5 19 Darien | Southwire
652.4 19 | Elgin | 652.4 | 19 |  | 0.1853 |  |  | 0.927 |  |  |  | 25 | 0.1677 | 75 | 0.1958 | 608.3 |  | AAAC | 652.4 19 Elgin | Southwire
740.8 37 | Flint | 740.8 | 37 |  | 0.1415 |  |  | 0.991 |  |  |  | 25 | 0.1482 | 75 | 0.1728 | 690.8 |  | AAAC | 740.8 37 Flint | Southwire
927.2 37 | Greeley | 927.2 | 37 |  | 0.1583 |  |  | 1.108 |  |  |  | 25 | 0.1193 | 75 | 0.1389 | 864.6 |  | AAAC | 927.2 37 Greeley | Southwire

## AAC
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
AAC
1/0 7 | Poppy | 1/0 | 7 |  | 0.1228 |  |  | 0.368 |  |  |  | 25 | 0.8829 | 75 | 1.0576 | 98.9 |  | ASTM B 231 | 1/0 7 Poppy | Southwire
2/0 7 | Aster | 2/0 | 7 |  | 0.1379 |  |  | 0.414 |  |  |  | 25 | 0.7000 | 75 | 0.8384 | 124.8 |  | ASTM B 231 | 2/0 7 Aster | Southwire
3/0 7 | Phlox | 3/0 | 7 |  | 0.1548 |  |  | 0.464 |  |  |  | 25 | 0.5543 | 75 | 0.6652 | 157.2 |  | ASTM B 231 | 3/0 7 Phlox | Southwire
4/0 7 | Oxlip | 4/0 | 7 |  | 0.1739 |  |  | 0.522 |  |  |  | 25 | 0.4407 | 75 | 0.5277 | 198.4 |  | ASTM B 231 | 4/0 7 Oxlip | Southwire
1 7 | Pansy | 1 | 7 |  | 0.1093 |  |  | 0.328 |  |  |  | 25 | 1.1128 | 75 | 1.3330 | 78.4 |  | ASTM B 231 | 1 7 Pansy | Southwire
2 7 | Iris | 2 | 7 |  | 0.0974 |  |  | 0.292 |  |  |  | 25 | 1.4031 | 75 | 1.6808 | 62.2 |  | ASTM B 231 | 2 7 Iris | Southwire
4 7 | Rose | 4 | 7 |  | 0.0772 |  |  | 0.232 |  |  |  | 25 | 2.2308 | 75 | 2.6725 | 39.1 |  | ASTM B 231 | 4 7 Rose | Southwire
6 7 | Peachbell | 6 | 7 |  | 0.0612 |  |  | 0.184 |  |  |  | 25 | 3.5471 | 75 | 4.2493 | 24.6 |  | ASTM B 231 | 6 7 Peachbell | Southwire
250 7 | Sneezewort | 250 | 7 |  | 0.1890 |  |  | 0.567 |  |  |  | 25 | 0.3733 | 75 | 0.4469 | 234.4 |  | ASTM B 231 | 250 7 Sneezewort | Southwire
250 19 | Valerian | 250 | 19 |  | 0.1147 |  |  | 0.574 |  |  |  | 25 | 0.3733 | 75 | 0.4469 | 234.3 |  | ASTM B 231 | 250 19 Valerian | Southwire
266.8 7 | Daisy | 266.8 | 7 |  | 0.1953 |  |  | 0.586 |  |  |  | 25 | 0.3499 | 75 | 0.4188 | 250.2 |  | ASTM B 231 | 266.8 7 Daisy | Southwire
266.8 19 | Laurel | 266.8 | 19 |  | 0.1185 |  |  | 0.593 |  |  |  | 25 | 0.3499 | 75 | 0.4188 | 250.1 |  | ASTM B 231 | 266.8 19 Laurel | Southwire
300 19 | Peony | 300 | 19 |  | 0.1257 |  |  | 0.629 |  |  |  | 25 | 0.3113 | 75 | 0.3726 | 281.4 |  | ASTM B 231 | 300 19 Peony | Southwire
336.4 19 | Tulip | 336.4 | 19 |  | 0.1331 |  |  | 0.666 |  |  |  | 25 | 0.2779 | 75 | 0.3325 | 315.5 |  | ASTM B 231 | 336.4 19 Tulip | Southwire
350 19 | Daffodil | 350 | 19 |  | 0.1357 |  |  | 0.679 |  |  |  | 25 | 0.2672 | 75 | 0.3197 | 327.9 |  | ASTM B 231 | 350 19 Daffodil | Southwire
397.5 19 | Canna | 397.5 | 19 |  | 0.1447 |  |  | 0.724 |  |  |  | 25 | 0.2355 | 75 | 0.2817 | 372.9 |  | ASTM B 231 | 397.5 19 Canna | Southwire
450 19 | Goldentuft | 450 | 19 |  | 0.1539 |  |  | 0.769 |  |  |  | 25 | 0.2084 | 75 | 0.2491 | 421.8 |  | ASTM B 231 | 450 19 Goldentuft | Southwire
477 19 | Cosmos | 477 | 19 |  | 0.1584 |  |  | 0.793 |  |  |  | 25 | 0.197 | 75 | 0.235 | 446.8 |  | ASTM B 231 | 477 19 Cosmos | Ratekit
477 37 | Syringa | 477 | 37 |  | 0.1135 |  |  | 0.795 |  |  |  | 25 | 0.1968 | 75 | 0.2352 | 446.8 |  | ASTM B 231 | 477 37 Syringa | Southwire
500 37 | Hyacinth | 500 | 37 |  | 0.1162 |  |  | 0.813 |  |  |  | 25 | 0.1879 | 75 | 0.2245 | 468.3 |  | ASTM B 231 | 500 37 Hyacinth | Southwire
500 19 | Zinnia | 500 | 19 |  | 0.1622 |  |  | 0.811 |  |  |  | 25 | 0.1879 | 75 | 0.2245 | 468.5 |  | ASTM B 231 | 500 19 Zinnia | Southwire
556.5 19 | Dahlia | 556.5 | 19 |  | 0.1711 |  |  | 0.856 |  |  |  | 25 | 0.169 | 75 | 0.202 | 521.4 |  | ASTM B 231 | 556.5 19 Dahlia | Ratekit
556.5 37 | Misteltoe | 556.5 | 37 |  | 0.1226 |  |  | 0.858 |  |  |  | 25 | 0.1691 | 75 | 0.2020 | 521.3 |  | ASTM B 231 | 556.5 37 Misteltoe | Southwire
600 37 | Meadowsweet | 600 | 37 |  | 0.1273 |  |  | 0.891 |  |  |  | 25 | 0.1571 | 75 | 0.1875 | 562 |  | ASTM B 231 | 600 37 Meadowsweet | Southwire
636 37 | Orchid | 636 | 37 |  | 0.1311 |  |  | 0.918 |  |  |  | 25 | 0.1485 | 75 | 0.1771 | 596.1 |  | ASTM B 231 | 636 37 Orchid | Southwire
700 61 | Flag | 700 | 61 |  | 0.1071 |  |  | 0.964 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.8 |  | ASTM B 231 | 700 61 Flag | Southwire
700 37 | Verbena | 700 | 37 |  | 0.1375 |  |  | 0.963 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.7 |  | ASTM B 231 | 700 37 Verbena | Southwire
715.5 61 | Nasturtium | 715.5 | 61 |  | 0.1083 |  |  | 0.975 |  |  |  | 25 | 0.1325 | 75 | 0.1578 | 670.6 |  | ASTM B 231 | 715.5 61 Nasturtium | Southwire
715.5 37 | Violet | 715.5 | 37 |  | 0.1391 |  |  | 0.974 |  |  |  | 25 | 0.1325 | 75 | 0.1578 | 671 |  | ASTM B 231 | 715.5 37 Violet | Southwire
750 61 | Cattail | 750 | 61 |  | 0.1109 |  |  | 0.998 |  |  |  | 25 | 0.1266 | 75 | 0.1508 | 703.2 |  | ASTM B 231 | 750 61 Cattail | Southwire
750 37 | Petunia | 750 | 37 |  | 0.1424 |  |  | 0.997 |  |  |  | 25 | 0.1266 | 75 | 0.1508 | 703.2 |  | ASTM B 231 | 750 37 Petunia | Southwire
795 37 | Arbutus | 795 | 37 |  | 0.1466 |  |  | 1.026 |  |  |  | 25 | 0.1197 | 75 | 0.1425 | 745.3 |  | ASTM B 231 | 795 37 Arbutus | Southwire
795 61 | Lilac | 795 | 61 |  | 0.1142 |  |  | 1.028 |  |  |  | 25 | 0.1197 | 75 | 0.1425 | 745.7 |  | ASTM B 231 | 795 61 Lilac | Southwire
874.5 37 | Anemone | 874.5 | 37 |  | 0.1538 |  |  | 1.077 |  |  |  | 25 | 0.1090 | 75 | 0.1298 | 820.3 |  | ASTM B 231 | 874.5 37 Anemone | Southwire
874.5 61 | Crocus | 874.5 | 61 |  | 0.1198 |  |  | 1.078 |  |  |  | 25 | 0.1090 | 75 | 0.1300 | 820.6 |  | ASTM B 231 | 874.5 61 Crocus | Southwire
900 37 | Cockscomb | 900 | 37 |  | 0.156 |  |  | 1.092 |  |  |  | 25 | 0.1064 | 75 | 0.1264 | 844 |  | ASTM B 231 | 900 37 Cockscomb | Southwire
900 61 | Snapdragon | 900 | 61 |  | 0.1215 |  |  | 1.094 |  |  |  | 25 | 0.1064 | 75 | 0.1264 | 844 |  | ASTM B 231 | 900 61 Snapdragon | Southwire
954 61 | Goldenrod | 954 | 61 |  | 0.1251 |  |  | 1.126 |  |  |  | 25 | 0.1007 | 75 | 0.1195 | 894.8 |  | ASTM B 231 | 954 61 Goldenrod | Southwire
954 37 | Magnolia | 954 | 37 |  | 0.1606 |  |  | 1.124 |  |  |  | 25 | 0.1007 | 75 | 0.1195 | 894.5 |  | ASTM B 231 | 954 37 Magnolia | Southwire
1000 61 | Cameilla | 1000 | 61 |  | 0.1280 |  |  | 1.152 |  |  |  | 25 | 0.0963 | 75 | 0.1142 | 936.8 |  | ASTM B 231 | 1000 61 Cameilla | Southwire
1000 37 | Hawkweed | 1000 | 37 |  | 0.1644 |  |  | 1.150 |  |  |  | 25 | 0.0963 | 75 | 0.1142 | 937.3 |  | ASTM B 231 | 1000 37 Hawkweed | Southwire
1033.5 37 | Bluebell | 1033.5 | 37 |  | 0.1671 |  |  | 1.170 |  |  |  | 25 | 0.0934 | 75 | 0.1107 | 968.3 |  | ASTM B 231 | 1033.5 37 Bluebell | Southwire
1033.5 61 | Larkspur | 1033.5 | 61 |  | 0.1302 |  |  | 1.172 |  |  |  | 25 | 0.0934 | 75 | 0.1107 | 969.2 |  | ASTM B 231 | 1033.5 61 Larkspur | Southwire
1113 61 | Marigold | 1113 | 61 |  | 0.1351 |  |  | 1.216 |  |  |  | 25 | 0.0872 | 75 | 0.1032 | 1044 |  | ASTM B 231 | 1113 61 Marigold | Southwire
1192.5 61 | Hawthorn | 1192.5 | 61 |  | 0.1398 |  |  | 1.258 |  |  |  | 25 | 0.0819 | 75 | 0.0967 | 1117 |  | ASTM B 231 | 1192.5 61 Hawthorn | Southwire
1272 61 | Narcissus | 1272 | 61 |  | 0.1444 |  |  | 1.300 |  |  |  | 25 | 0.0772 | 75 | 0.0912 | 1192 |  | ASTM B 231 | 1272 61 Narcissus | Southwire
1351.5 61 | Columbine | 1351.5 | 61 |  | 0.1488 |  |  | 1.340 |  |  |  | 25 | 0.0731 | 75 | 0.0861 | 1266 |  | ASTM B 231 | 1351.5 61 Columbine | Southwire
1431 61 | Carnation | 1431 | 61 |  | 0.1532 |  |  | 1.379 |  |  |  | 25 | 0.0695 | 75 | 0.0817 | 1342 |  | ASTM B 231 | 1431 61 Carnation | Southwire
1510.5 61 | Galdious | 1510.5 | 61 |  | 0.1574 |  |  | 1.417 |  |  |  | 25 | 0.0663 | 75 | 0.0778 | 1417 |  | ASTM B 231 | 1510.5 61 Galdious | Southwire
1590 61 | Coreopsis | 1590 | 61 |  | 0.1614 |  |  | 1.454 |  |  |  | 25 | 0.0634 | 75 | 0.0743 | 1489 |  | ASTM B 231 | 1590 61 Coreopsis | Ratekit
1750 61 | Jessamine | 1750 | 61 |  | 0.1694 |  |  | 1.525 |  |  |  | 25 | 0.0585 | 75 | 0.0683 | 1641 |  | ASTM B 231 | 1750 61 Jessamine | Southwire
2000 91 | Cowslip | 2000 | 91 |  | 0.1482 |  |  | 1.630 |  |  |  | 25 | 0.0525 | 75 | 0.0609 | 1873 |  | ASTM B 231 | 2000 91 Cowslip | Southwire
2500 91 | Lupine | 2500 | 91 |  | 0.1657 |  |  | 1.823 |  |  |  | 25 | 0.0446 | 75 | 0.0511 | 2365 |  | ASTM B 231 | 2500 91 Lupine | Southwire
3000 127 | Trilium | 3000 | 127 |  | 0.1537 |  |  | 1.996 |  |  |  | 25 | 0.0392 | 75 | 0.0445 | 2840 |  | ASTM B 231 | 3000 127 Trilium | Southwire
3500 127 | Bluebonnet | 3500 | 127 |  | 0.1660 |  |  | 2.158 |  |  |  | 25 | 0.0355 | 75 | 0.0399 | 3345 |  | ASTM B 231 | 3500 127 Bluebonnet | Southwire

## ACAR
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
ACAR
355 12/7 | 355 - 12/7 | 355 | 12 | 7 | 0.1367 | 0.1367 | 0.399 | 0.684 |  |  |  | 25 | 0.2776 | 75 | 0.3296 | 333 | 0.3296 | ASTM B 524 | 355 - 12/7 | Southwire
355 15/4 | 355 - 15/4 | 355 | 15 | 4 | 0.1367 | 0.1367 | 0.182 | 0.684 |  |  |  | 25 | 0.2714 | 75 | 0.3233 | 333.3 | 0.3233 | ASTM B 524 | 355 - 15/4 | Southwire
395.1 15/4 | 395.1 - 15/4 | 395.1 | 15 | 4 | 0.1442 | 0.1442 | 0.192 | 0.721 |  |  |  | 25 | 0.2441 | 75 | 0.2907 | 369.9 | 0.2907 | ASTM B 524 | 395.1 - 15/4 | Southwire
465.9 12/7 | 465.9 - 12/7 | 465.9 | 12 | 7 | 0.1566 | 0.1566 | 0.457 | 0.783 |  |  |  | 25 | 0.2121 | 75 | 0.2517 | 435.9 | 0.2517 | ASTM B 524 | 465.9 - 12/7 | Southwire
503.6 12/7 | 503.6 - 12/7 | 503.6 | 12 | 7 | 0.1628 | 0.1628 | 0.475 | 0.814 |  |  |  | 25 | 0.1965 | 75 | 0.2330 | 471.1 | 0.2330 | ASTM B 524 | 503.6 - 12/7 | Southwire
503.6 15/4 | 503.6 - 15/4 | 503.6 | 15 | 4 | 0.1628 | 0.1628 | 0.217 | 0.814 |  |  |  | 25 | 0.1921 | 75 | 0.2286 | 471.5 | 0.2286 | ASTM B 524 | 503.6 - 15/4 | Southwire
559.5 15/4 | 559.5 - 15/4 | 559.5 | 15 | 4 | 0.1716 | 0.1716 | 0.229 | 0.858 |  |  |  | 25 | 0.1732 | 75 | 0.2060 | 523.8 | 0.2060 | ASTM B 524 | 559.5 - 15/4 | Southwire
587.2 15/4 | 587.2 - 15/4 | 587.2 | 15 | 4 | 0.1758 | 0.1758 | 0.234 | 0.879 |  |  |  | 25 | 0.1652 | 75 | 0.1964 | 549.8 | 0.1964 | ASTM B 524 | 587.2 - 15/4 | Southwire
653.1 12/7 | 653.1 - 12/7 | 653.1 | 12 | 7 | 0.1854 | 0.1854 | 0.541 | 0.927 |  |  |  | 25 | 0.1523 | 75 | 0.1804 | 611 | 0.1804 | ASTM B 524 | 653.1 - 12/7 | Southwire
653.1 15/4 | 653.1 - 15/4 | 653.1 | 15 | 4 | 0.1854 | 0.1854 | 0.247 | 0.927 |  |  |  | 25 | 0.1490 | 75 | 0.1769 | 611.5 | 0.1769 | ASTM B 524 | 653.1 - 15/4 | Southwire
739.8 18/19 | 739.8 - 18/19 | 739.8 | 18 | 19 | 0.1414 | 0.1414 | 1.045 | 0.99 |  |  |  | 25 | 0.1378 | 75 | 0.1625 | 691.6 | 0.1625 | ASTM B 524 | 739.8 - 18/19 | Southwire
739.8 30/7 | 739.8 - 30/7 | 739.8 | 30 | 7 | 0.1414 | 0.1414 | 0.231 | 0.99 |  |  |  | 25 | 0.1316 | 75 | 0.1562 | 692.7 | 0.1562 | ASTM B 524 | 739.8 - 30/7 | Southwire
739.8 24/13 | 739.8 - 24/13 | 739.8 | 24 | 13 | 0.1414 | 0.1414 | 0.536 | 0.99 |  |  |  | 25 | 0.1346 | 75 | 0.1593 | 692.1 | 0.1593 | ASTM B 524 | 739.8 - 24/13 | Southwire
739.8 33/4 | 739.8 - 33/4 | 739.8 | 33 | 4 | 0.1414 | 0.1414 | 0.12 | 0.99 |  |  |  | 25 | 0.1302 | 75 | 0.1547 | 693 | 0.1547 | ASTM B 524 | 739.8 - 33/4 | Southwire
853.7 18/19 | 853.7 - 18/19 | 853.7 | 18 | 19 | 0.1519 | 0.1519 | 1.122 | 1.063 |  |  |  | 25 | 0.1201 | 75 | 0.1414 | 798.1 | 0.1414 | ASTM B 524 | 853.7 - 18/19 | Southwire
853.7 30/7 | 853.7 - 30/7 | 853.7 | 30 | 7 | 0.1519 | 0.1519 | 0.248 | 1.063 |  |  |  | 25 | 0.1147 | 75 | 0.1359 | 799.4 | 0.1359 | ASTM B 524 | 853.7 - 30/7 | Southwire
853.7 24/13 | 853.7 - 24/13 | 853.7 | 24 | 13 | 0.1519 | 0.1519 | 0.576 | 1.063 |  |  |  | 25 | 0.1173 | 75 | 0.1386 | 798.7 | 0.1386 | ASTM B 524 | 853.7 - 24/13 | Southwire
927.2 18/19 | 927.2 - 18/19 | 927.2 | 18 | 19 | 0.1583 | 0.1583 | 1.17 | 1.108 |  |  |  | 25 | 0.1110 | 75 | 0.1305 | 866.7 | 0.1305 | ASTM B 524 | 927.2 - 18/19 | Southwire
927.2 30/7 | 927.2 - 30/7 | 927.2 | 30 | 7 | 0.1583 | 0.1583 | 0.259 | 1.108 |  |  |  | 25 | 0.1061 | 75 | 0.1255 | 868.2 | 0.1255 | ASTM B 524 | 927.2 - 30/7 | Southwire
927.2 24/13 | 927.2 - 24/13 | 927.2 | 24 | 13 | 0.1583 | 0.1583 | 0.6 | 1.108 |  |  |  | 25 | 0.1084 | 75 | 0.1280 | 867.5 | 0.1280 | ASTM B 524 | 927.2 - 24/13 | Southwire
1024.5 18/19 | 1024.5 - 18/19 | 1024.5 | 18 | 19 | 0.1664 | 0.1664 | 1.23 | 1.165 |  |  |  | 25 | 0.1010 | 75 | 0.1187 | 957.7 | 0.1187 | ASTM B 524 | 1024.5 - 18/19 | Southwire
1024.5 30/7 | 1024.5 - 30/7 | 1024.5 | 30 | 7 | 0.1664 | 0.1664 | 0.272 | 1.165 |  |  |  | 25 | 0.0966 | 75 | 0.1142 | 959.3 | 0.1142 | ASTM B 524 | 1024.5 - 30/7 | Southwire
1024.5 24/13 | 1024.5 - 24/13 | 1024.5 | 24 | 13 | 0.1664 | 0.1664 | 0.631 | 1.165 |  |  |  | 25 | 0.0987 | 75 | 0.1164 | 958.5 | 0.1164 | ASTM B 524 | 1024.5 - 24/13 | Southwire
1081 18/19 | 1081 - 18/19 | 1081 | 18 | 19 | 0.1709 | 0.1709 | 1.262 | 1.196 |  |  |  | 25 | 0.0960 | 75 | 0.1127 | 1010.2 | 0.1127 | ASTM B 524 | 1081 - 18/19 | Southwire
1081 30/7 | 1081 - 30/7 | 1081 | 30 | 7 | 0.1709 | 0.1709 | 0.279 | 1.196 |  |  |  | 25 | 0.0918 | 75 | 0.1084 | 1011.9 | 0.1084 | ASTM B 524 | 1081 - 30/7 | Southwire
1081 24/13 | 1081 - 24/13 | 1081 | 24 | 13 | 0.1709 | 0.1709 | 0.648 | 1.196 |  |  |  | 25 | 0.0939 | 75 | 0.1105 | 1011.1 | 0.1105 | ASTM B 524 | 1081 - 24/13 | Southwire
1109 18/19 | 1109 - 18/19 | 1109 | 18 | 19 | 0.1731 | 0.1731 | 1.279 | 1.212 |  |  |  | 25 | 0.0937 | 75 | 0.1100 | 1036.4 | 0.1100 | ASTM B 524 | 1109 - 18/19 | Southwire
1109 30/7 | 1109 - 30/7 | 1109 | 30 | 7 | 0.1731 | 0.1731 | 0.283 | 1.212 |  |  |  | 25 | 0.0897 | 75 | 0.1058 | 1038.1 | 0.1058 | ASTM B 524 | 1109 - 30/7 | Southwire
1109 24/13 | 1109 - 24/13 | 1109 | 24 | 13 | 0.1731 | 0.1731 | 0.657 | 1.212 |  |  |  | 25 | 0.0917 | 75 | 0.1078 | 1037.2 | 0.1078 | ASTM B 524 | 1109 - 24/13 | Southwire
1172 18/19 | 1172 - 18/19 | 1172 | 18 | 19 | 0.178 | 0.178 | 1.315 | 1.246 |  |  |  | 25 | 0.0891 | 75 | 0.1044 | 1095.9 | 0.1044 | ASTM B 524 | 1172 - 18/19 | Southwire
1172 30/7 | 1172 - 30/7 | 1172 | 30 | 7 | 0.178 | 0.178 | 0.291 | 1.246 |  |  |  | 25 | 0.0852 | 75 | 0.1004 | 1097.7 | 0.1004 | ASTM B 524 | 1172 - 30/7 | Southwire
1172 24/13 | 1172 - 24/13 | 1172 | 24 | 13 | 0.178 | 0.178 | 0.675 | 1.246 |  |  |  | 25 | 0.0871 | 75 | 0.1024 | 1096.8 | 0.1024 | ASTM B 524 | 1172 - 24/13 | Southwire
1172 33/4 | 1172 - 33/4 | 1172 | 33 | 4 | 0.1780 | 0.1780 | 0.151 | 1.246 |  |  |  | 25 | 0.0843 | 75 | 0.0995 | 1098.2 | 0.0995 | ASTM B 524 | 1172 - 33/4 | Southwire
1197 18/19 | 1197 - 18/19 | 1197 | 18 | 19 | 0.1799 | 0.1799 | 1.329 | 1.259 |  |  |  | 25 | 0.0873 | 75 | 0.1023 | 1119.4 | 0.1023 | ASTM B 524 | 1197 - 18/19 | Southwire
1197 30/7 | 1197 - 30/7 | 1197 | 30 | 7 | 0.1799 | 0.1799 | 0.294 | 1.259 |  |  |  | 25 | 0.0836 | 75 | 0.0985 | 1121.3 | 0.0985 | ASTM B 524 | 1197 - 30/7 | Southwire
1197 24/13 | 1197 - 24/13 | 1197 | 24 | 13 | 0.1799 | 0.1799 | 0.682 | 1.259 |  |  |  | 25 | 0.0854 | 75 | 0.1003 | 1120.3 | 0.1003 | ASTM B 524 | 1197 - 24/13 | Southwire
1280 18/19 | 1280 - 18/19 | 1280 | 18 | 19 | 0.186 | 0.186 | 1.374 | 1.302 |  |  |  | 25 | 0.0821 | 75 | 0.0961 | 1196.6 | 0.0961 | ASTM B 524 | 1280 - 18/19 | Southwire
1280 30/7 | 1280 - 30/7 | 1280 | 30 | 7 | 0.186 | 0.186 | 0.304 | 1.302 |  |  |  | 25 | 0.0787 | 75 | 0.0925 | 1198.6 | 0.0925 | ASTM B 524 | 1280 - 30/7 | Southwire
1280 24/13 | 1280 - 24/13 | 1280 | 24 | 13 | 0.186 | 0.186 | 0.705 | 1.302 |  |  |  | 25 | 0.0803 | 75 | 0.0942 | 1197.6 | 0.0942 | ASTM B 524 | 1280 - 24/13 | Southwire
1362 42/19 | 1362 - 42/19 | 1362 | 42 | 19 | 0.1494 | 0.1494 | 0.608 | 1.345 |  |  |  | 25 | 0.0756 | 75 | 0.0886 | 1274.1 | 0.0886 | ASTM B 524 | 1362 - 42/19 | Southwire
1362 54/7 | 1362 - 54/7 | 1362 | 54 | 7 | 0.1494 | 0.1494 | 0.174 | 1.345 |  |  |  | 25 | 0.0737 | 75 | 0.0888 | 1275.4 | 0.0888 | ASTM B 524 | 1362 - 54/7 | Southwire
1703 42/19 | 1703 - 42/19 | 1703 | 42 | 19 | 0.1671 | 0.1671 | 0.68 | 1.504 |  |  |  | 25 | 0.0622 | 75 | 0.0723 | 1593.9 | 0.0723 | ASTM B 524 | 1703 - 42/19 | Southwire
1703 48/13 | 1703 - 48/13 | 1703 | 48 | 13 | 0.1671 | 0.1671 | 0.407 | 1.504 |  |  |  | 25 | 0.0614 | 75 | 0.0715 | 1594.7 | 0.0715 | ASTM B 524 | 1703 - 48/13 | Southwire
1703 54/7 | 1703 - 54/7 | 1703 | 54 | 7 | 0.1671 | 0.1671 | 0.195 | 1.504 |  |  |  | 25 | 0.0607 | 75 | 0.0725 | 1595.5 | 0.0725 | ASTM B 524 | 1703 - 54/7 | Southwire
1933 42/19 | 1933 - 42/19 | 1933 | 42 | 19 | 0.1780 | 0.1780 | 0.725 | 1.602 |  |  |  | 25 | 0.0559 | 75 | 0.0647 | 1808.6 | 0.0647 | ASTM B 524 | 1933 - 42/19 | Southwire
1933 48/13 | 1933 - 48/13 | 1933 | 48 | 13 | 0.178 | 0.178 | 0.434 | 1.602 |  |  |  | 25 | 0.0553 | 75 | 0.0641 | 1809.5 | 0.0641 | ASTM B 524 | 1933 - 48/13 | Southwire
1933 54/7 | 1933 - 54/7 | 1933 | 54 | 7 | 0.178 | 0.178 | 0.208 | 1.602 |  |  |  | 25 | 0.0546 | 75 | 0.0648 | 1810.4 | 0.0648 | ASTM B 524 | 1933 - 54/7 | Southwire
2267 42/19 | 2267 - 42/19 | 2267 | 42 | 19 | 0.1928 | 0.1928 | 0.785 | 1.735 |  |  |  | 25 | 0.0496 | 75 | 0.0571 | 2142.7 | 0.0571 | ASTM B 524 | 2267 - 42/19 | Southwire
2267 48/13 | 2267 - 48/13 | 2267 | 48 | 13 | 0.1928 | 0.1928 | 0.47 | 1.735 |  |  |  | 25 | 0.0491 | 75 | 0.0565 | 2143.8 | 0.0565 | ASTM B 524 | 2267 - 48/13 | Southwire
2267 54/7 | 2267 - 54/7 | 2267 | 54 | 7 | 0.1928 | 0.1928 | 0.225 | 1.735 |  |  |  | 25 | 0.0486 | 75 | 0.0571 | 2144.9 | 0.0571 | ASTM B 524 | 2267 - 54/7 | Southwire
2338 42/19 | 2338 - 42/19 | 2338 | 42 | 19 | 0.1958 | 0.1958 | 0.797 | 1.762 |  |  |  | 25 | 0.0484 | 75 | 0.0556 | 2209.9 | 0.0556 | ASTM B 524 | 2338 - 42/19 | Southwire
2338 48/13 | 2338 - 48/13 | 2338 | 48 | 13 | 0.1958 | 0.1958 | 0.477 | 1.762 |  |  |  | 25 | 0.0479 | 75 | 0.0551 | 2211 | 0.0551 | ASTM B 524 | 2338 - 48/13 | Southwire
2338 54/7 | 2338 - 54/7 | 2338 | 54 | 7 | 0.1958 | 0.1958 | 0.228 | 1.762 |  |  |  | 25 | 0.0474 | 75 | 0.0557 | 2212.1 | 0.0557 | ASTM B 524 | 2338 - 54/7 | Southwire
2493 54/37 | 2493 - 54/37 | 2493 | 54 | 37 | 0.19576 |  |  | 1.821 |  |  |  | 25 | 0.045936 | 75 | 0.0528 | 2363 |  | ASTM B 524 | 2493 - 54/37 | Alcan

## ACCC
*** Values on this sheet are in Imperial Units
| Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
ACCC
611 HAWK | 611 | [5 empty] | 0.858 |  |  |  | 25 | 0.14942 | 75 | 0.17952 | 624 |  | ACCC | 611.0 kcmil ACCC/TW (Hawk) | TransPower
713 DOVE | 713 | [5 empty] | 0.927 |  |  |  | 25 | 0.1283 | 75 | 0.15418 | 728 |  | ACCC | 713.0 kcmil ACCC/TW (Dove) | TransPower
816 GROSBEAK | 816 | [5 empty] | 0.99 |  |  |  | 25 | 0.11299 | 75 | 0.13517 | 832 |  | ACCC | 816.0 kcmil ACCC/TW (Grosbeak) | TransPower
1020 DRAKE | 1020 | [5 empty] | 1.108 |  |  |  | 25 | 0.090816 | 75 | 0.10877 | 1046 |  | ACCC | 1020 kcmil ACCC/TW (Drake) | TransPower
1222 CARDINAL | 1222 | [5 empty] | 1.196 |  |  |  | 25 | 0.077088 | 75 | 0.091872 | 1228 |  | ACCC | 1222 kcmil ACCC/TW (Cardinal) | TransPower
1572 BITTERN | 1572 | [5 empty] | 1.345 |  |  |  | 25 | 0.061248 | 75 | 0.072864 | 1554 |  | ACCC | 1572 kcmil ACCC/TW (Bittern) | TransPower
1966 LAPWING | 1966 | [5 empty] | 1.504 |  |  |  | 25 | 0.051005 | 75 | 0.059664 | 1960 |  | ACCC | 1966 kcmil ACCC/TW (Lapwing) | TransPower
2242 CHUKAR | 2242 | [5 empty] | 1.602 |  |  |  | 25 | 0.045883 | 75 | 0.053328 | 2225 |  | ACCC | 2242 kcmil ACCC/TW (Chukar) | TransPower

## ACCR
Updated as of August 2015 | *** Values on this sheet are in Imperial Units
| Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec
ACCR 373-T13 (Brant ACCR) | 373.2022 | 24 | 7 | 0.1247 | 0.0831 |  | 0.748 |  | 13 |  | 25 | 0.24273 | 240 | 0.44848 | 351.5149 | 56.4851 | ACCR
ACCR-TW_1033-T28 | 1033.35 | 24 | 37 | 0.2075 | 0.0889 |  | 1.222 |  | 28 |  | 25 | 0.082928 | 240 | 0.15215 | 973.3007 | 336.6993 | ACCR
ACCR_427-T13 | 427.0934 | 24 | 7 | 0.1334 | 0.0889 |  | 0.8 |  | 13 |  | 25 | 0.21228 | 240 | 0.39198 | 402.2745 | 64.7255 | ACCR
ACCR_558-T73 | 557.7622 | 56 | 37 | 0.0998 | 0.1046 |  | 1.132 |  | 73 |  | 25 | 0.13012 | 240 | 0.24049 | 666.2975 | 331.7025 | ACCR
ACCR_680-T19 | 679.6619 | 28 | 19 | 0.1558 | 0.0831 |  | 1.039 |  | 19 |  | 25 | 0.13065 | 240 | 0.24054 | 640.1659 | 154.8341 | ACCR
ACCR_788-T26 | 787.7635 | 32 | 19 | 0.1569 | 0.1046 |  | 1.151 |  | 26 |  | 25 | 0.10993 | 240 | 0.2022 | 741.9856 | 246.0144 | ACCR
ACCR 1272-T11 (Bittern ACCR) | 1237.9556 | 51 | 19 | 0.1558 | 0.0831 |  | 1.35 |  | 11 |  | 25 | 0.076361 | 240 | 0.13826 | 1171.7044 | 153.2956 | ACCR
ACCR_Condor_824-T13 | 824.0662 | 24 | 19 | 0.1853 | 0.0741 |  | 1.112 |  | 13 |  | 25 | 0.11123 | 240 | 0.20396 | 776.1786 | 121.8214 | ACCR
ACCR 1033-T13 (Curlew ACCR) | 1035.8415 | 54 | 19 | 0.1385 | 0.0831 |  | 1.247 |  | 13 |  | 25 | 0.089534 | 240 | 0.16329 | 980.4067 | 153.5933 | ACCR
ACCR 795-T16 (Drake ACCR) | 824.7099 | 26 | 19 | 0.1781 | 0.0831 |  | 1.128 |  | 16 |  | 25 | 0.10951 | 240 | 0.20095 | 776.7849 | 153.2151 | ACCR
ACCR 557-T23 (Eagle ACCR) | 575.4675 | 30 | 19 | 0.1385 | 0.0831 |  | 0.97 |  | 23 |  | 25 | 0.15174 | 240 | 0.27989 | 542.0264 | 154.9736 | ACCR
ACCR 636-T10 (Goldfinch ACCR) | 633.558 | 22 | 7 | 0.1697 | 0.0943 |  | 0.962 |  | 10 |  | 25 | 0.14559 | 240 | 0.26786 | 596.7411 | 73.2589 | ACCR
ACCR 636-T16 (Grosbeak ACCR) | 655.6534 | 26 | 19 | 0.1588 | 0.0741 |  | 1.006 |  | 16 |  | 25 | 0.13709 | 240 | 0.25238 | 617.5526 | 122.4474 | ACCR
ACCR 477-T16(Hawk ACCR) | 470.3465 | 26 | 7 | 0.1345 | 0.1046 |  | 0.852 |  | 16 |  | 25 | 0.19008 | 240 | 0.35088 | 443.0141 | 89.9859 | ACCR
ACCR 1590-T11 (Lapwing ACCR) | 1594.1702 | 51 | 19 | 0.1768 | 0.0943 |  | 1.532 |  | 11 |  | 25 | 0.060485 | 240 | 0.10803 | 1508.8556 | 197.1444 | ACCR
ACCR 397-T23 (Lark ACCR) | 400.2075 | 30 | 7 | 0.1155 | 0.1155 |  | 0.809 |  | 23 |  | 25 | 0.21714 | 240 | 0.40128 | 376.9509 | 110.0491 | ACCR
ACCR 336-T16 (Linnet ACCR) | 339.6767 | 26 | 7 | 0.1143 | 0.0889 |  | 0.724 |  | 16 |  | 25 | 0.26262 | 240 | 0.48547 | 319.9377 | 65.0623 | ACCR
ACCR 300-T16 (Ostrich ACCR) | 296.5622 | 26 | 7 | 0.1068 | 0.0831 |  | 0.677 |  | 16 |  | 25 | 0.30041 | 240 | 0.55551 | 279.3286 | 57.6714 | ACCR
ACCR 267-T16 (Partridge ACCR) | 257.4065 | 26 | 7 | 0.0995 | 0.0774 |  | 0.63 |  | 16 |  | 25 | 0.34614 | 240 | 0.64026 | 242.4483 | 49.5517 | ACCR
ACCR 795-T10 (Puffin ACCR) | 780.0516 | 22 | 7 | 0.1883 | 0.1046 |  | 1.067 |  | 10 |  | 25 | 0.11886 | 240 | 0.218 | 734.7218 | 90.2782 | ACCR
ACCR 715-T13 (Stilt ACCR) | 720.7894 | 24 | 7 | 0.1733 | 0.1155 |  | 1.04 |  | 13 |  | 25 | 0.12662 | 240 | 0.23269 | 678.9034 | 109.0966 | ACCR
ACCR-TW_1033-T23 | 1033.35 | 24 | 19 | 0.2075 | 0.1111 |  | 1.189 |  | 23 |  | 25 | 0.084958 | 240 | 0.15568 | 973.3007 | 269.6993 | ACCR
ACCR TW 1158-T13 (Hudson TW ACCR) | 1153.702 | 22 | 19 | 0.229 | 0.0889 |  | 1.201 |  | 13 |  | 25 | 0.077943 | 240 | 0.145 | 1086.6589 | 176.3411 | ACCR
ACCR TW 795-T13 (Condor TW ACCR) | 795.2072 | 20 | 19 | 0.1994 | 0.0741 |  | 0.992 |  | 13 |  | 25 | 0.11446 | 240 | 0.2102 | 748.9967 | 120.0033 | ACCR
ACCR TW 1033-T13 (Curlew TW ACCR) | 1033.3058 | 20 | 19 | 0.2273 | 0.0831 |  | 1.132 |  | 13 |  | 25 | 0.088935 | 240 | 0.16246 | 973.2591 | 149.7409 | ACCR
ACCR TW 1622-T13 (Pecos TW ACCR) | 1621.9753 | 38 | 19 | 0.2066 | 0.1046 |  | 1.411 |  | 13 |  | 25 | 0.05838 | 240 | 0.10482 | 1527.7203 | 246.2797 | ACCR
ACCR 557-T16 (Dove ACCR) | 573.3585 | 26 | 7 | 0.1485 | 0.1155 |  | 0.941 |  | 16 |  | 25 | 0.15621 | 240 | 0.28795 | 540.0399 | 109.9601 | ACCR
ACCR 267-T23 (Junco ACCR) | 266.7747 | 30 | 7 | 0.0943 | 0.0943 |  | 0.66 |  | 23 |  | 25 | 0.32528 | 240 | 0.60173 | 251.2721 | 73.7279 | ACCR
ACCR_131-T58 | 131.2939 | 12 | 7 | 0.1046 | 0.1046 |  | 0.523 |  | 58 |  | 25 | 0.57863 | 240 | 1.0712 | 123.6643 | 90.3357 | ACCR
ACCR_183-T114 | 182.8486 | 19 | 19 | 0.0981 | 0.1046 |  | 0.719 |  | 114 |  | 25 | 0.34828 | 240 | 0.64474 | 172.223 | 242.777 | ACCR
ACCR_270-T35 | 270.296 | 9 | 7 | 0.1733 | 0.1155 |  | 0.693 |  | 35 |  | 25 | 0.30659 | 240 | 0.56725 | 254.5888 | 109.4112 | ACCR
ACCR 397-T16 (Ibis ACCR) | 381.9254 | 26 | 7 | 0.1212 | 0.0943 |  | 0.768 |  | 16 |  | 25 | 0.23354 | 240 | 0.43154 | 359.7313 | 73.2687 | ACCR
ACCR TW 763-T17 (Wabash TW ACCR) | 762.8418 | 20 | 19 | 0.1953 | 0.0831 |  | 0.99 |  | 17 |  | 25 | 0.11701 | 240 | 0.21519 | 718.5121 | 151.4879 | ACCR
ACCR TW 477-T16 (Hawk TW ACCR) | 477.0691 | 18 | 7 | 0.1628 | 0.1046 |  | 0.789 |  | 16 |  | 25 | 0.18703 | 240 | 0.34522 | 449.346 | 88.654 | ACCR
ACCR TW 572-T13 (Mohawk TW ACCR) | 571.8962 | 20 | 7 | 0.1691 | 0.1046 |  | 0.845 |  | 13 |  | 25 | 0.15806 | 240 | 0.29131 | 538.6626 | 88.3374 | ACCR
ACCR TW 665-T16 (Oswego TW ACCR) | 664.6658 | 20 | 19 | 0.1823 | 0.0741 |  | 0.93 |  | 16 |  | 25 | 0.13486 | 240 | 0.2483 | 626.0412 | 120.9588 | ACCR
ACCR TW 958-T16 (Suwanee TW ACCR) | 958.081 | 24 | 19 | 0.1998 | 0.0889 |  | 1.099 |  | 16 |  | 25 | 0.094324 | 240 | 0.17279 | 902.4057 | 172.5943 | ACCR
ACCR TW 1335-T13 (Thames TW ACCR) | 1334.5129 | 38 | 19 | 0.1874 | 0.0943 |  | 1.275 |  | 13 |  | 25 | 0.070012 | 240 | 0.12689 | 1256.9627 | 201.0373 | ACCR
ACCR 1272-T9 (Diver ACCR) | 1321.0949 | 48 | 19 | 0.1659 | 0.0774 |  | 1.382 |  | 9 |  | 25 | 0.07234 | 240 | 0.1304 | 1244.3244 | 132.6756 | ACCR
ACCR 1351-T13 (Martin ACCR) | 1334.4394 | 54 | 19 | 0.1572 | 0.0943 |  | 1.415 |  | 13 |  | 25 | 0.070479 | 240 | 0.12733 | 1263.0246 | 196.9754 | ACCR
ACCR 477-T13 (Flicker ACCR) | 480.534 | 24 | 7 | 0.1415 | 0.0943 |  | 0.849 |  | 13 |  | 25 | 0.18885 | 240 | 0.34847 | 452.6096 | 73.3904 | ACCR
ACCR_1851-T13 | 1852.1482 | 54 | 19 | 0.1852 | 0.1111 |  | 1.667 |  | 13 |  | 25 | 0.052327 | 240 | 0.092607 | 1753.0274 | 271.9726 | ACCR
ACCR_1742-T9 | 1741.932 | 48 | 19 | 0.1905 | 0.0889 |  | 1.588 |  | 9 |  | 25 | 0.056298 | 240 | 0.099668 | 1640.7061 | 175.2939 | ACCR
ACCR_1962-T11 | 1961.2157 | 51 | 19 | 0.1961 | 0.1046 |  | 1.7 |  | 11 |  | 25 | 0.050368 | 240 | 0.088492 | 1847.247 | 251.753 | ACCR
ACCR_195-T20 | 194.5222 | 7 | 7 | 0.1667 | 0.0741 |  | 0.556 |  | 20 |  | 25 | 0.45128 | 240 | 0.83508 | 183.2183 | 45.7817 | ACCR
ACCR_236-T16 | 236.1343 | 26 | 7 | 0.0953 | 0.0741 |  | 0.603 |  | 16 |  | 25 | 0.37758 | 240 | 0.69852 | 222.4123 | 45.5877 | ACCR
ACCR_207-T23 | 207.1683 | 30 | 7 | 0.0831 | 0.0831 |  | 0.582 |  | 23 |  | 25 | 0.41868 | 240 | 0.77476 | 195.1295 | 57.8705 | ACCR
Specific heat of the core: W-Sec/lb-C 391

## ACSSTW
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
ACSSTW
336.4 18/7 Type 16 | Linnet | 336.4 | 18 | 7 |  | 0.0884 | 0.2652 | 0.659 |  | 16 | 2 | 25 | 0.2647 | 75 | 0.3181 | 315.9 | 145.5 | ASTM B 857 | 336.4 18/7 Type 16 Linnet | Southwire
336.4 16/7 Type 23 | Oriole | 336.4 | 16 | 7 |  | 0.1059 | 0.3177 | 0.693 |  | 23 | 2 | 25 | 0.2622 | 75 | 0.3151 | 316.1 | 208.7 | ASTM B 857 | 336.4 16/7 Type 23 Oriole | Southwire
477 18/7 Type 13 | Flicker | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.1877 | 75 | 0.2255 | 447.8 | 164.4 | ASTM B 857 | 477 18/7 Type 13 Flicker | Southwire
477 18/7 Type 16 | Hawk | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.18691 | 75 | 0.22493 | 448.1 | 206.3 | ASTM B 857 | 477 18/7 Type 16 Hawk | Alcan
477 16/7 Type 23 | Hen | 477 | 16 | 7 |  | 0.1261 | 0.3783 | 0.825 |  | 23 | 2 | 25 | 0.1852 | 75 | 0.2225 | 448.3 | 296 | ASTM B 857 | 477 16/7 Type 23 Hen | Southwire
556.5 18/7 Type 13 | Parakeet | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1612 | 75 | 0.1935 | 522.4 | 191.7 | ASTM B 857 | 556.5 18/7 Type 13 Parakeet | Southwire
556.5 20/7 Type 16 | Dove | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.15998 | 75 | 0.19219 | 522.9 | 241 | ASTM B 857 | 556.5 20/7 Type 16 Dove | Alcan
565.3 20/7 Type 16 | Calumet | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1581 | 75 | 0.1898 | 531.2 | 244.4 | ASTM B 857 | 565.3 20/7 Type 16 Calumet | Southwire
571.7 18/7 Type 13 | Mohawk | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.1570 | 75 | 0.1884 | 536.6 | 197.4 | ASTM B 857 | 571.7 18/7 Type 13 Mohawk | Southwire
636 18/7 Type 13 | Rook | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.890 |  | 13 | 2 | 25 | 0.1413 | 75 | 0.1696 | 597.0 | 219.1 | ASTM B 857 | 636 18/7 Type 13 Rook | Southwire
636 20/7 Type 16 | Grosbeak | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.14045 | 75 | 0.16843 | 597.6 | 275.1 | ASTM B 857 | 636 20/7 Type 16 Grosbeak | Alcan
636 18/7 Type 23 | Scoter | 636 | 18 | 7 |  | 0.1456 | 0.4368 | 0.953 |  | 23 | 2 | 25 | 0.1393 | 75 | 0.1672 | 597.6 | 394.6 | ASTM B 857 | 636 18/7 Type 23 Scoter | Southwire
664.8 20/7 Type 16 | Oswego | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1347 | 75 | 0.1617 | 624.6 | 288 | ASTM B 857 | 664.8 20/7 Type 16 Oswego | Southwire
666.6 20/7 Type 13 | Mystic | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1349 | 75 | 0.1619 | 625.7 | 229.7 | ASTM B 857 | 666.6 20/7 Type 13 Mystic | Southwire
762.8 20/7 Type 16 | Wabash | 762.8 | 20 | 7 |  | 0.1331 | 0.3993 | 0.99 |  | 16 | 2 | 25 | 0.1177 | 75 | 0.1411 | 716.7 | 330 | ASTM B 857 | 762.8 20/7 Type 16 Wabash | Southwire
768.2 20/7 Type 13 | Maumee | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1174 | 75 | 0.1407 | 721.1 | 265.7 | ASTM B 857 | 768.2 20/7 Type 13 Maumee | Southwire
795 17/7 Type 7 | Tern | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.960 |  | 7 | 2 | 25 | 0.1147 | 75 | 0.1373 | 745.2 | 146.1 | ASTM B 857 | 795 17/7 Type 7 Tern | Southwire
795 18/7 Type 10 | Puffin | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.980 |  | 10 | 2 | 25 | 0.1139 | 75 | 0.1365 | 745.9 | 228.4 | ASTM B 857 | 795 18/7 Type 10 Puffin | Southwire
795 20/7 Type 13 | Condor | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1136 | 75 | 0.1361 | 746.3 | 273.9 | ASTM B 857 | 795 20/7 Type 13 Condor | Southwire
795 20/7 Type 16 | Drake | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.010 |  | 16 | 2 | 25 | 0.11246 | 75 | 0.13464 | 747.0 | 344.2 | ASTM B 857 | 795 20/7 Type 16 Drake | Alcan
900 20/7 Type 13 | Canary | 900 | 20 | 7 |  | 0.1291 | 0.3873 | 1.055 |  | 13 | 3 | 25 | 0.1007 | 75 | 0.1205 | 844.9 | 310.2 | ASTM B 857 | 900 20/7 Type 13 Canary | Southwire
946.7 35/7 Type 10 | Fraser | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0969 | 75 | 0.1190 | 892.6 | 248 | ASTM B 857 | 946.7 35/7 Type 10 Fraser | Southwire
954 30/7 Type 5 | Phoenix | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.0970 | 75 | 0.1190 | 897.7 | 130.4 | ASTM B 857 | 954 30/7 Type 5 Phoenix | Southwire
954 32/7 Type 7 | Rail | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0967 | 75 | 0.1187 | 898.6 | 175 | ASTM B 857 | 954 32/7 Type 7 Rail | Southwire
954 20/7 Type 13 | Cardinal | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.09451 | 75 | 0.11299 | 895.5 | 328.7 | ASTM B 857 | 954 20/7 Type 13 Cardinal | Alcan
957.2 32/7 Type 7 | Kettle | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.060 |  | 7 | 3 | 25 | 0.0964 | 75 | 0.1183 | 901.6 | 176.2 | ASTM B 857 | 957.2 32/7 Type 7 Kettle | Southwire
959.6 22/7 Type 16 | Suwannee | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0941 | 75 | 0.1127 | 901.6 | 415 | ASTM B 857 | 959.6 22/7 Type 16 Suwannee | Southwire
966.2 21/7 Type 13 | Columbia | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.0940 | 75 | 0.1124 | 906.9 | 333.2 | ASTM B 857 | 966.2 21/7 Type 13 Columbia | Southwire
1033.5 30/7 Type 5 | Snowbird | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0899 | 75 | 0.1101 | 972.5 | 141.2 | ASTM B 857 | 1033.5 30/7 Type 5 Snowbird | Southwire
1033.5 32/7 Type 7 | Ortolan | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.0896 | 75 | 0.1098 | 972.5 | 189.8 | ASTM B 857 | 1033.5 32/7 Type 7 Ortolan | Southwire
1033.5 20/7 Type 13 | Curlew | 1033.5 | 20 | 7 |  | 0.1383 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.08818 | 75 | 0.10507 | 970.1 | 356.0 | ASTM B 857 | 1033.5 20/7 Type 13 Curlew | Alcan
1113 30/7 Type 5 | Avocet | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0838 | 75 | 0.0938 | 1047 | 152.1 | ASTM B 857 | 1113 30/7 Type 5 Avocet | Southwire
1113 33/7 Type 7 | Bluejay | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0835 | 75 | 0.0935 | 1048 | 204.8 | ASTM B 857 | 1113 33/7 Type 7 Bluejay | Southwire
1113 38/19 Type 13 | Finch | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0826 | 75 | 0.1012 | 1051 | 376.1 | ASTM B 857 | 1113 38/19 Type 13 Finch | Southwire
1158 33/7 Type 7 | Genesee | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0805 | 75 | 0.0983 | 1091 | 216 | ASTM B 857 | 1158 33/7 Type 7 Genesee | Southwire
1158.4 25/7 Type 13 | Hudson | 1158.4 | 25 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.0790 | 75 | 0.0943 | 1087 | 400 | ASTM B 857 | 1158.4 25/7 Type 13 Hudson | Southwire
1168.1 30/7 Type 5 | Cheyenne | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0801 | 75 | 0.0979 | 1099 | 159.6 | ASTM B 857 | 1168.1 30/7 Type 5 Cheyenne | Southwire
1192.5 30/7 Type 5 | Oxbird | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0786 | 75 | 0.0960 | 1122 | 163 | ASTM B 857 | 1192.5 30/7 Type 5 Oxbird | Southwire
1192.5 33/7 Type 7 | Bunting | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0783 | 75 | 0.0956 | 1123 | 219.1 | ASTM B 857 | 1192.5 33/7 Type 7 Bunting | Southwire
1192.5 38/19 Type 13 | Grackle | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0773 | 75 | 0.0947 | 1126 | 403 | ASTM B 857 | 1192.5 38/19 Type 13 Grackle | Southwire
1233.6 38/19 Type 13 | Yukon | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.07498 | 75 | 0.0887 | 1166.5 | 419.5 | ASTM B 857 | 1233.6 38/19 Type 13 Yukon | Alcan
1257.1 35/7 Type 7 | Nelson | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0745 | 75 | 0.0909 | 1184 | 231.3 | ASTM B 857 | 1257.1 35/7 Type 7 Nelson | Southwire
1272 30/7 Type 5 | Catawba | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0741 | 75 | 0.0902 | 1197 | 174 | ASTM B 857 | 1272 30/7 Type 5 Catawba | Southwire
1272 30/7 Type 5 | Scissortail | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0741 | 75 | 0.0902 | 1198 | 174 | ASTM B 857 | 1272 30/7 Type 5 Scissortail | Southwire
1272 35/7 Type 7 | Bittern | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0737 | 75 | 0.0899 | 1198 | 233.9 | ASTM B 857 | 1272 35/7 Type 7 Bittern | Southwire
1272 39/19 Type 13 | Pheasant | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.07286 | 75 | 0.08659 | 1201 | 430 | ASTM B 857 | 1272 39/19 Type 13 Pheasant | Alcan
1334.6 39/19 Type 13 | Thames | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.0696 | 75 | 0.0849 | 1260 | 451.4 | ASTM B 857 | 1334.6 39/19 Type 13 Thames | Southwire
1351.5 35/7 Type 7 | Dipper | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0697 | 75 | 0.0849 | 1273 | 248.3 | ASTM B 857 | 1351.5 35/7 Type 7 Dipper | Southwire
1351.5 39/19 Type 13 | Martin | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.300 |  | 13 | 3 | 25 | 0.0688 | 75 | 0.0839 | 1276 | 456 | ASTM B 857 | 1351.5 39/19 Type 13 Martin | Southwire
1359.7 36/7 Type 7 | Mackenzie | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0694 | 75 | 0.0844 | 1281 | 250 | ASTM B 857 | 1359.7 36/7 Type 7 Mackenzie | Southwire
1372.5 30/7 Type 5 | Truckee | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0691 | 75 | 0.0840 | 1292 | 187.6 | ASTM B 857 | 1372.5 30/7 Type 5 Truckee | Southwire
1431 36/7 Type 7 | Bobolink | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0662 | 75 | 0.0804 | 1347 | 263.1 | ASTM B 857 | 1431 36/7 Type 7 Bobolink | Southwire
1431 39/19 Type 13 | Plover | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0652 | 75 | 0.0795 | 1351 | 483 | ASTM B 857 | 1431 39/19 Type 13 Plover | Southwire
1433.6 39/19 Type 13 | Merrimack | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.340 |  | 13 | 3 | 25 | 0.0651 | 75 | 0.0793 | 1354 | 484.2 | ASTM B 857 | 1433.6 39/19 Type 13 Merrimack | Southwire
1455.3 36/7 Type 7 | MiramichiACSS | 1455.3 | 36 | 7 |  | 0.120 | 0.360 | 1.302 |  | 7 | 3 | 25 | 0.0652 | 75 | 0.0792 | 1371 | 268 | ASTM B 857 | 1455.3 36/7 Type 7 MiramichiACSS | Southwire
1467.8 33/7 Type 5 | St. Croix | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.0650 | 75 | 0.0789 | 1381 | 202 | ASTM B 857 | 1467.8 33/7 Type 5 St. Croix | Southwire
1533.3 39/19 Type 13 | Rio Grande | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0612 | 75 | 0.0744 | 1448 | 519 | ASTM B 857 | 1533.3 39/19 Type 13 Rio Grande | Southwire
1557.4 36/7 Type 7 | Potomac | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0613 | 75 | 0.0743 | 1467 | 287 | ASTM B 857 | 1557.4 36/7 Type 7 Potomac | Southwire
1569 33/7 Type 5 | Platte | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0613 | 75 | 0.0742 | 1476 | 215 | ASTM B 857 | 1569 33/7 Type 5 Platte | Southwire
1590 36/7 Type 7 | Lapwing | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.05966 | 75 | 0.07022 | 1498 | 292 | ASTM B 857 | 1590 36/7 Type 7 Lapwing | Alcan
1590 42/19 Type 13 | Falcon | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.05914 | 75 | 0.07022 | 1501 | 537 | ASTM B 857 | 1590 42/19 Type 13 Falcon | Alcan
1622 39/19 Type 13 | Pecos | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.058 | 75 | 0.0688 | 1532 | 574 | ASTM B 857 | 1622 39/19 Type 13 Pecos | Southwire
1657.4 36/7 Type 7 | Schuylkill | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0581 | 75 | 0.0702 | 1561 | 305 | ASTM B 857 | 1657.4 36/7 Type 7 Schuylkill | Southwire
1730.6 39/19 Type 13 | James | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.470 |  | 13 | 3 | 25 | 0.0549 | 75 | 0.0664 | 1634 | 585 | ASTM B 857 | 1730.6 39/19 Type 13 James | Southwire
1758.6 37/7 Type 7 | Pee Dee | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0551 | 75 | 0.0665 | 1656 | 324 | ASTM B 857 | 1758.6 37/7 Type 7 Pee Dee | Southwire
1780 37/19 Type 8 | Chukar | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.05438 | 75 | 0.05396 | 1675 | 386.7 | ASTM B 857 | 1780 37/19 Type 8 Chukar | Alcan
1926.9 42/19 Type 13 | Cumberland | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.05016 | 75 | 0.05861 | 1819 | 649.8 | ASTM B 857 | 1926.9 42/19 Type 13 Cumberland | Alcan
1949.6 42/7 Type 7 | Athabaska | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.05069 | 75 | 0.05914 | 1836 | 361 | ASTM B 857 | 1949.6 42/7 Type 7 Athabaska | Alcan
2153.8 64/19 Type 8 | Powder | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0464 | 75 | 0.0543 | 2043 | 467.5 | ASTM B 857 | 2153.8 64/19 Type 8 Powder | Southwire
2156 64/19 Type 8 | Bluebird | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0464 | 75 | 0.0543 | 2045 | 467.5 | ASTM B 857 | 2156 64/19 Type 8 Bluebird | Southwire
2627.3 64/19 Type 8 | Santee | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0396 | 75 | 0.0459 | 2492 | 571 | ASTM B 857 | 2627.3 64/19 Type 8 Santee | Southwire

## ACSR
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
ACSR
6 6/1 | Turkey | 6 | 6 | 1 | 0.0661 | 0.0661 | 0.0661 | 0.198 | 2.66 |  |  | 25 | 3.454 | 75 | 4.320 | 24.5 | 11.6 | ASTM B 232 | 6 6/1 Turkey | Southwire
4 6/1 | Swan | 4 | 6 | 1 | 0.0834 | 0.0834 | 0.0834 | 0.25 | 3.35 |  |  | 25 | 2.172 | 75 | 2.765 | 38.9 | 18.4 | ASTM B 232 | 4 6/1 Swan | Southwire
4 7/1 | Swanate | 4 | 7 | 1 | 0.0772 | 0.1029 | 0.1029 | 0.257 | 3.45 |  |  | 25 | 2.147 | 75 | 2.779 | 38.9 | 28 | ASTM B 232 | 4 7/1 Swanate | Southwire
2 6/1 | Sparrow | 2 | 6 | 1 | 0.1052 | 0.1052 | 0.1052 | 0.316 | 4.23 |  |  | 25 | 1.366 | 75 | 1.778 | 61.9 | 29.3 | ASTM B 232 | 2 6/1 Sparrow | Southwire
2 7/1 | Sparate | 2 | 7 | 1 | 0.0974 | 0.1299 | 0.1299 | 0.325 | 4.35 |  |  | 25 | 1.351 | 75 | 1.787 | 61.9 | 44.7 | ASTM B 232 | 2 7/1 Sparate | Southwire
1 6/1 | Robin | 1 | 6 | 1 | 0.1181 | 0.1182 | 0.1182 | 0.355 | 4.75 |  |  | 25 | 1.083 | 75 | 1.427 | 78.1 | 37 | ASTM B 232 | 1 6/1 Robin | Southwire
1/0 6/1 | Raven | 1/0 | 6 | 1 | 0.1327 | 0.1327 | 0.1327 | 0.398 | 5.33 |  |  | 25 | 0.859 | 75 | 1.145 | 98.5 | 46.6 | ASTM B 232 | 1/0 6/1 Raven | Southwire
2/0 6/1 | Quail | 2/0 | 6 | 1 | 0.1489 | 0.1489 | 0.1489 | 0.447 | 5.99 |  |  | 25 | 0.681 | 75 | 0.924 | 124.1 | 58.7 | ASTM B 232 | 2/0 6/1 Quail | Southwire
3/0 6/1 | Pigeon | 3/0 | 6 | 1 | 0.1672 | 0.1672 | 0.1672 | 0.502 | 6.72 |  |  | 25 | 0.541 | 75 | 0.746 | 156.4 | 74 | ASTM B 232 | 3/0 6/1 Pigeon | Southwire
4/0 6/1 | Penguin | 4/0 | 6 | 1 | 0.1878 | 0.1878 | 0.1878 | 0.563 | 7.55 |  |  | 25 | 0.434 | 75 | 0.611 | 197.4 | 93.4 | ASTM B 232 | 4/0 6/1 Penguin | Ratekit
80 8/1 | Grouse | 80 | 8 | 1 | 0.100 | 0.167 | 0.167 | 0.367 | 4.77 |  |  | 25 | 1.112 | 75 | 1.525 | 75 | 73.9 | ASTM B 232 | 80 8/1 Grouse | Southwire
101.8 12/7 | Petrel | 101.8 | 12 | 7 | 0.0921 | 0.0921 | 0.2763 | 0.461 | 5.76 |  |  | 25 | 0.853 | 75 | 1.321 | 95.9 | 157.9 | ASTM B 232 | 101.8 12/7 Petrel | Southwire
110.8 12/7 | Minorca | 110.8 | 12 | 7 | 0.0961 | 0.0961 | 0.2883 | 0.481 | 6.01 |  |  | 25 | 0.783 | 75 | 1.233 | 104.4 | 171.9 | ASTM B 232 | 110.8 12/7 Minorca | Southwire
134.6 12/7 | Leghorn | 134.6 | 12 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.53 | 6.62 |  |  | 25 | 0.645 | 75 | 1.053 | 126.8 | 208.7 | ASTM B 232 | 134.6 12/7 Leghorn | Southwire
159 12/7 | Guinea | 159 | 12 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.576 | 7.19 |  |  | 25 | 0.491 | 75 | 0.921 | 149.7 | 246.6 | ASTM B 232 | 159 12/7 Guinea | Southwire
211.3 12/7 | Cochin | 211.3 | 12 | 7 | 0.1327 | 0.1327 | 0.3981 | 0.664 | 8.29 |  |  | 25 | 0.411 | 75 | 0.732 | 199 | 327.8 | ASTM B 232 | 211.3 12/7 Cochin | Southwire
266.8 18/1 | Waxwing | 266.8 | 18 | 1 | 0.1217 | 0.1217 | 0.1217 | 0.609 |  |  |  | 25 | 0.3471 | 75 | 0.4155 | 249.9 | 39.2 | ASTM B 232 | 266.8 18/1 Waxwing | Southwire
266.8 26/7 | Partridge | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3437 | 75 | 0.4113 | 251.3 | 115.6 | ASTM B 232 | 266.8 26/7 Partridge | Southwire
266.8 30/7 | Junco | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.3413 | 75 | 0.4083 | 251.9 | 165.5 | ASTM B 232 | 266.8 30/7 Junco | Southwire
300.0 26/7 | Ostrich | 300.0 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.3058 | 75 | 0.3659 | 282.5 | 129.7 | ASTM B 232 | 300.0 26/7 Ostrich | Southwire
336.4 18/1 | Merlin | 336.4 | 18 | 1 | 0.1367 | 0.1367 | 0.1367 | 0.684 |  |  |  | 25 | 0.2756 | 75 | 0.3298 | 315.3 | 49.5 | ASTM B 232 | 336.4 18/1 Merlin | Southwire
336.4 24/7 | Widgeon | 336.4 | 24 | 7 | 0.1184 | 0.0789 | 0.2367 | 0.7103 |  |  |  | 25 | 0.2740 | 75 | 0.3279 | 316.9 | 115.9 | ASTM B 232 | 336.4 24/7 Widgeon | Southwire
336.4 26/7 | Linnet | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.273 | 75 | 0.327 | 316.6 | 145.4 | ASTM B 232 | 336.4 26/7 Linnet | Ratekit
336.4 30/7 | Oriole | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2708 | 75 | 0.3240 | 317.7 | 208.7 | ASTM B 232 | 336.4 30/7 Oriole | Southwire
397.5 18/1 | Chickadee | 397.5 | 18 | 1 | 0.1486 | 0.1486 | 0.1486 | 0.743 |  |  |  | 25 | 0.2336 | 75 | 0.2794 | 372.5 | 58.5 | ASTM B 232 | 397.5 18/1 Chickadee | Southwire
397.5 24/7 | Brant | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2321 | 75 | 0.2777 | 374.4 | 137 | ASTM B 232 | 397.5 24/7 Brant | Southwire
397.5 26/7 | Ibis | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2311 | 75 | 0.2764 | 374.1 | 171.9 | ASTM B 232 | 397.5 26/7 Ibis | Southwire
397.5 30/7 | Lark | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2294 | 75 | 0.2743 | 375.3 | 246.5 | ASTM B 232 | 397.5 30/7 Lark | Southwire
477.0 18/1 | Pelican | 477.0 | 18 | 1 | 0.1628 | 0.1628 | 0.1628 | 0.814 |  |  |  | 25 | 0.1950 | 75 | 0.2331 | 447.1 | 70.2 | ASTM B 232 | 477.0 18/1 Pelican | Southwire
477.0 24/7 | Flicker | 477.0 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1937 | 75 | 0.2316 | 449.4 | 164.5 | ASTM B 232 | 477.0 24/7 Flicker | Southwire
477.0 26/7 | Hawk | 477.0 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1928 | 75 | 0.2305 | 449 | 206.4 | ASTM B 232 | 477.0 26/7 Hawk | Southwire
477.0 30/7 | Hen | 477.0 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.191 | 75 | 0.229 | 450.4 | 296 | ASTM B 232 | 477.0 30/7 Hen | Ratekit
556.5 18/1 | Osprey | 556.5 | 18 | 1 | 0.1758 | 0.1758 | 0.1758 | 0.879 |  |  |  | 25 | 0.1676 | 75 | 0.2002 | 521.4 | 81.8 | ASTM B 232 | 556.5 18/1 Osprey | Southwire
556.5 24/7 | Parakeet | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.166 | 75 | 0.199 | 524.3 | 191.8 | ASTM B 232 | 556.5 24/7 Parakeet | Ratekit
556.5 26/7 | Dove | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1655 | 75 | 0.1978 | 524.2 | 241 | ASTM B 232 | 556.5 26/7 Dove | Southwire
556.5 30/7 | Eagle | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1642 | 75 | 0.1963 | 525.4 | 345.2 | ASTM B 232 | 556.5 30/7 Eagle | Southwire
605.0 24/7 | Peacock | 605.0 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1532 | 75 | 0.1830 | 570.1 | 208.7 | ASTM B 232 | 605.0 24/7 Peacock | Southwire
605.0 26/7 | Squab | 605.0 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1524 | 75 | 0.1821 | 569.5 | 261.8 | ASTM B 232 | 605.0 26/7 Squab | Southwire
605.0 30/19 | Teal | 605.0 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1513 | 75 | 0.1808 | 571.2 | 367.4 | ASTM B 232 | 605.0 30/19 Teal | Southwire
605.0 30/7 | Wood Duck | 605.0 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1512 | 75 | 0.1806 | 571.2 | 375.3 | ASTM B 232 | 605.0 30/7 Wood Duck | Southwire
605.0 54/7 | Duck | 605.0 | 54 | 7 | 0.1058 | 0.1058 | 0.3174 | 0.952 |  |  |  | 25 | 0.1533 | 75 | 0.1880 | 569.3 | 208.3 | ASTM B 232 | 605.0 54/7 Duck | Southwire
636.0 18/1 | Kingbird | 636.0 | 18 | 1 | 0.188 | 0.188 | 0.188 | 0.94 |  |  |  | 25 | 0.1470 | 75 | 0.1755 | 596.3 | 93.6 | ASTM B 232 | 636.0 18/1 Kingbird | Southwire
636.0 24/7 | Rook | 636.0 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1458 | 75 | 0.1742 | 599.1 | 219.1 | ASTM B 232 | 636.0 24/7 Rook | Southwire
636.0 26/7 | Grosbeak | 636.0 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1451 | 75 | 0.1733 | 599 | 275.2 | ASTM B 232 | 636.0 26/7 Grosbeak | Southwire
636.0 30/7 | Scoter | 636.0 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1439 | 75 | 0.1719 | 600.5 | 394.6 | ASTM B 232 | 636.0 30/7 Scoter | Southwire
636.0 30/19 | Egret | 636.0 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1440 | 75 | 0.1720 | 600.5 | 386.7 | ASTM B 232 | 636.0 30/19 Egret | Southwire
636.0 36/1 | Swift | 636.0 | 36 | 1 | 0.1329 | 0.1329 | 0.1329 | 0.93 |  |  |  | 25 | 0.1477 | 75 | 0.1763 | 596 | 46.8 | ASTM B 232 | 636.0 36/1 Swift | Southwire
636.0 54/7 | Goose | 636.0 | 54 | 7 | 0.1085 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1459 | 75 | 0.1789 | 598.8 | 219.1 | ASTM B 232 | 636.0 54/7 Goose | Southwire
666.6 24/7 | Flamingo | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1 |  |  |  | 25 | 0.1393 | 75 | 0.1663 | 628.2 | 229.7 | ASTM B 232 | 666.6 24/7 Flamingo | Southwire
666.6 26/7 | Gannet | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1385 | 75 | 0.1654 | 627.7 | 288.5 | ASTM B 232 | 666.6 26/7 Gannet | Southwire
666.6 54/7 | Gull | 666.6 | 54 | 7 | 0.1111 | 0.1111 | 0.3333 | 0.9999 |  |  |  | 25 | 0.1394 | 75 | 0.1708 | 627.8 | 229.7 | ASTM B 232 | 666.6 54/7 Gull | Southwire
715.5 24/7 | Stilt | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1299 | 75 | 0.1551 | 674.2 | 246.6 | ASTM B 232 | 715.5 24/7 Stilt | Southwire
715.5 26/7 | Starling | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1292 | 75 | 0.1543 | 674 | 309.7 | ASTM B 232 | 715.5 26/7 Starling | Southwire
715.5 30/19 | Redwing | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1282 | 75 | 0.1531 | 675.3 | 434 | ASTM B 232 | 715.5 30/19 Redwing | Southwire
715.5 54/7 | Crow | 715.5 | 54 | 7 | 0.1151 | 0.1151 | 0.345 | 1.04 |  |  |  | 25 | 0.1299 | 75 | 0.1592 | 673.8 | 246.5 | ASTM B 232 | 715.5 54/7 Crow | Southwire
795.0 20/7 | Turbit | 795.0 | 20 | 7 | 0.1994 | 0.0886 | 0.2658 | 1.0634 |  |  |  | 25 | 0.1185 | 75 | 0.1412 | 749 | 146.1 | ASTM B 232 | 795.0 20/7 Turbit | Southwire
795.0 22/7 | Puffin | 795.0 | 22 | 7 | 0.1901 | 0.1056 | 0.3168 | 1.0772 |  |  |  | 25 | 0.1179 | 75 | 0.1405 | 748.8 | 207.6 | ASTM B 232 | 795.0 22/7 Puffin | Southwire
795.0 24/7 | Cuckoo | 795.0 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1172 | 75 | 0.1398 | 748.8 | 273.9 | ASTM B 232 | 795.0 24/7 Cuckoo | Southwire
795.0 26/7 | Drake | 795.0 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.117 | 75 | 0.139 | 749.1 | 344.3 | ASTM B 232 | 795.0 26/7 Drake | Ratekit
795.0 30/7 | Skimmer | 795.0 | 30 | 7 | 0.1628 | 0.1628 | 0.4884 | 1.14 |  |  |  | 25 | 0.1155 | 75 | 0.1379 | 750.7 | 493.3 | ASTM B 232 | 795.0 30/7 Skimmer | Southwire
795.0 30/19 | Mallard | 795.0 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.116 | 75 | 0.138 | 750.7 | 483.2 | ASTM B 232 | 795.0 30/19 Mallard | Ratekit
795.0 36/1 | Coot | 795.0 | 36 | 1 | 0.1486 | 0.1486 | 0.1486 | 1.04 |  |  |  | 25 | 0.1190 | 75 | 0.1417 | 745.1 | 58.5 | ASTM B 232 | 795.0 36/1 Coot | Southwire
795.0 45/7 | Tern | 795.0 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1185 | 75 | 0.1421 | 748.6 | 146.1 | ASTM B 232 | 795.0 45/7 Tern | Southwire
795.0 54/7 | Condor | 795.0 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.117 | 75 | 0.14 | 748.4 | 273.9 | ASTM B 232 | 795.0 54/7 Condor | Ratekit
900.0 45/7 | Ruddy | 900.0 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1051 | 75 | 0.1259 | 847.4 | 165.5 | ASTM B 232 | 900.0 45/7 Ruddy | Southwire
900.0 54/7 | Canary | 900.0 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1039 | 75 | 0.1269 | 847.7 | 310.2 | ASTM B 232 | 900.0 54/7 Canary | Southwire
954.0 20/7 | Corncrake | 954.0 | 20 | 7 | 0.2184 | 0.0971 | 0.291 | 1.165 |  |  |  | 25 | 0.0994 | 75 | 0.1183 | 898.5 | 175.5 | ASTM B 232 | 954.0 20/7 Corncrake | Southwire
954.0 24/7 | Redbird | 954.0 | 24 | 7 | 0.1994 | 0.1329 | 0.399 | 1.196 |  |  |  | 25 | 0.0982 | 75 | 0.1170 | 898.8 | 328.7 | ASTM B 232 | 954.0 24/7 Redbird | Southwire
954.0 30/7 | Merganser | 954.0 | 30 | 7 | 0.1783 | 0.1783 | 0.5349 | 1.2481 |  |  |  | 25 | 0.0967 | 75 | 0.1152 | 900.5 | 591.7 | ASTM B 232 | 954.0 30/7 Merganser | Southwire
954.0 45/7 | Rail | 954.0 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0994 | 75 | 0.1189 | 898.5 | 175.5 | ASTM B 232 | 954.0 45/7 Rail | Southwire
954.0 54/7 | Cardinal | 954.0 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0982 | 75 | 0.1199 | 898.3 | 328.7 | ASTM B 232 | 954.0 54/7 Cardinal | Southwire
1033.5 42/7 | Snowbird | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0925 | 75 | 0.1105 | 973.9 | 141.5 | ASTM B 232 | 1033.5 42/7 Snowbird | Southwire
1033.5 45/7 | Ortolan | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0922 | 75 | 0.11 | 972.8 | 189.9 | ASTM B 232 | 1033.5 45/7 Ortolan | Ratekit
1033.5 54/7 | Curlew | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.091 | 75 | 0.108 | 972.8 | 356 | ASTM B 232 | 1033.5 54/7 Curlew | Ratekit
1113.0 45/7 | Bluejay | 1113.0 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0859 | 75 | 0.102 | 1048.7 | 204.8 | ASTM B 232 | 1113.0 45/7 Bluejay | Ratekit
1113.0 54/19 | Finch | 1113.0 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0851 | 75 | 0.101 | 1053.9 | 376.1 | ASTM B 232 | 1113.0 54/19 Finch | Ratekit
1192.5 45/7 | Bunting | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0805 | 75 | 0.0959 | 1123.4 | 219.1 | ASTM B 232 | 1192.5 45/7 Bunting | Southwire
1192.5 54/19 | Grackle | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.0798 | 75 | 0.0970 | 1128.6 | 402.8 | ASTM B 232 | 1192.5 54/19 Grackle | Southwire
1272.0 45/7 | Bittern | 1272.0 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0759 | 75 | 0.0898 | 1197.7 | 233.9 | ASTM B 232 | 1272.0 45/7 Bittern | Ratekit
1272.0 54/19 | Pheasant | 1272.0 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0751 | 75 | 0.089 | 1204.3 | 429.4 | ASTM B 232 | 1272.0 54/19 Pheasant | Ratekit
1351.5 45/7 | Dipper | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0718 | 75 | 0.0852 | 1272.9 | 248.3 | ASTM B 232 | 1351.5 45/7 Dipper | Southwire
1351.5 54/19 | Martin | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0710 | 75 | 0.0860 | 1279.1 | 455.9 | ASTM B 232 | 1351.5 54/19 Martin | Southwire
1431.0 45/7 | Bobolink | 1431.0 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0681 | 75 | 0.0808 | 1347.5 | 263.1 | ASTM B 232 | 1431.0 45/7 Bobolink | Southwire
1431.0 54/19 | Plover | 1431.0 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0673 | 75 | 0.0814 | 1354.6 | 483.2 | ASTM B 232 | 1431.0 54/19 Plover | Southwire
1510.5 45/7 | Nuthatch | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0649 | 75 | 0.0768 | 1422.5 | 277.5 | ASTM B 232 | 1510.5 45/7 Nuthatch | Southwire
1510.5 54/19 | Parrot | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0641 | 75 | 0.0774 | 1428.8 | 509.2 | ASTM B 232 | 1510.5 54/19 Parrot | Southwire
1590.0 45/7 | Lapwing | 1590.0 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.062 | 75 | 0.0729 | 1498.1 | 292.2 | ASTM B 232 | 1590.0 45/7 Lapwing | Ratekit
1590.0 54/19 | Falcon | 1590.0 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.0611 | 75 | 0.0721 | 1505 | 537 | ASTM B 232 | 1590.0 54/19 Falcon | Ratekit
1780.0 84/19 | Chukar | 1780.0 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0561 | 75 | 0.0658 | 1685.4 | 386.7 | ASTM B 232 | 1780.0 84/19 Chukar | Ratekit
2156.0 84/19 | Bluebird | 2156.0 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0477 | 75 | 0.0555 | 2040.4 | 467.5 | ASTM B 232 | 2156.0 84/19 Bluebird | Ratekit
2167.0 72/7 | Kiwi | 2167.0 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0484 | 75 | 0.0562 | 2051.4 | 249.2 | ASTM B 232 | 2167.0 72/7 Kiwi | Ratekit
2312.0 76/19 | Thrasher | 2312.0 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0454 | 75 | 0.0528 | 2187.9 | 335.4 | ASTM B 232 | 2312.0 76/19 Thrasher | Ratekit
2515.0 76/19 | Joree | 2515.0 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0428 | 75 | 0.0493 | 2380.1 | 364.9 | ASTM B 232 | 2515.0 76/19 Joree | Southwire

## AACSR
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
AACSR
266.8 26/7 | 266.8 - 26/7 | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3980 | 75 | 0.4656 | 250 | 115.6 |  | 266.8 26/7 | Southwire
266.8 30/7 | 266.8 - 30/7 | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.3946 | 75 | 0.4616 | 250.6 | 165.5 |  | 266.8 30/7 | Southwire
300.0 26/7 | 300.0 - 26/7 | 300.0 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.3540 | 75 | 0.4142 | 281 | 129.8 |  | 300.0 26/7 | Southwire
336.4 26/7 | 336.4 - 26/7 | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.3158 | 75 | 0.3694 | 315 | 145.4 |  | 336.4 26/7 | Southwire
336.4 30/7 | 336.4 - 30/7 | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.3131 | 75 | 0.3663 | 316 | 208.7 |  | 336.4 30/7 | Southwire
397.5 26/7 | 397.5 - 26/7 | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2675 | 75 | 0.3128 | 372.2 | 171.9 |  | 397.5 26/7 | Southwire
397.5 30/7 | 397.5 - 30/7 | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2651 | 75 | 0.3101 | 373.3 | 246.5 |  | 397.5 30/7 | Southwire
477.0 26/7 | 477.0 - 26/7 | 477.0 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.2231 | 75 | 0.2608 | 446.7 | 206.4 |  | 477.0 26/7 | Southwire
477.0 30/7 | 477.0 - 30/7 | 477.0 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.2211 | 75 | 0.2586 | 448.1 | 295.9 |  | 477.0 30/7 | Southwire
556.5 26/7 | 556.5 - 26/7 | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1915 | 75 | 0.2238 | 521.5 | 241 |  | 556.5 26/7 | Southwire
556.5 30/7 | 556.5 - 30/7 | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1897 | 75 | 0.2218 | 522.8 | 345.2 |  | 556.5 30/7 | Southwire
605.0 26/7 | 605.0 - 26/7 | 605.0 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1763 | 75 | 0.2060 | 566.6 | 261.8 |  | 605.0 26/7 | Southwire
605.0 30/19 | 605.0 - 30/19 | 605.0 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1748 | 75 | 0.2043 | 568.2 | 367.4 |  | 605.0 30/19 | Southwire
605.0 30/7 | 605.0 - 30/7 | 605.0 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1746 | 75 | 0.2041 | 568.2 | 375.3 |  | 605.0 30/7 | Southwire
636.0 26/7 | 636.0 - 26/7 | 636.0 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1678 | 75 | 0.1960 | 596 | 275.2 |  | 636.0 26/7 | Southwire
636.0 30/19 | 636.0 - 30/19 | 636.0 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1663 | 75 | 0.1944 | 597.4 | 386.6 |  | 636.0 30/19 | Southwire
636.0 30/7 | 636.0 - 30/7 | 636.0 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1662 | 75 | 0.1942 | 597.4 | 394.5 |  | 636.0 30/7 | Southwire
666.6 26/7 | 666.6 - 26/7 | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1601 | 75 | 0.1871 | 624.5 | 288.5 |  | 666.6 26/7 | Southwire
715.5 26/7 | 715.5 - 26/7 | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1493 | 75 | 0.1744 | 670.6 | 309.7 |  | 715.5 26/7 | Southwire
715.5 30/19 | 715.5 - 30/19 | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1481 | 75 | 0.1730 | 671.8 | 434 |  | 715.5 30/19 | Southwire
795.0 45/7 | 795.0 - 26/7 | 795.0 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1346 | 75 | 0.1572 | 745.3 | 344.2 |  | 795.0 45/7 | Southwire
795.0 54/7 | 795.0 - 30/19 | 795.0 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1334 | 75 | 0.1558 | 746.9 | 483.1 |  | 795.0 54/7 | Southwire
795.0 26/7 | 795.0 - 45/7 | 795.0 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1670 | 75 | 0.1609 | 744.8 | 146.1 |  | 795.0 26/7 | Southwire
795.0 30/19 | 795.0 - 54/7 | 795.0 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1354 | 75 | 0.1625 | 744.5 | 273.8 |  | 795.0 30/19 | Southwire
795.0 30/7 | 795.0 - 30/7 | 795.0 | 30 | 7 | 0.1628 | 0.1628 | 0.4884 | 1.14 |  |  |  | 25 | 0.1333 | 75 | 0.1557 | 746.9 | 493.2 |  | 795.0 30/7 | Southwire
900.0 45/7 | 900.0 - 45/7 | 900.0 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1214 | 75 | 0.1424 | 843.1 | 165.5 |  | 900.0 45/7 | Southwire
900.0 54/7 | 900.0 - 54/7 | 900.0 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1200 | 75 | 0.1437 | 843.4 | 310.2 |  | 900.0 54/7 | Southwire
954.0 45/7 | 954.0 - 45/7 | 954.0 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.1148 | 75 | 0.1345 | 893.9 | 175.5 |  | 954.0 45/7 | Southwire
954.0 54/7 | 954.0 - 54/7 | 954.0 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.1133 | 75 | 0.1357 | 893.7 | 328.7 |  | 954.0 54/7 | Southwire
954.0 30/19 | 954.0 - 30/19 | 954.0 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.1116 | 75 | 0.1302 | 895.9 | 579.5 |  | 954.0 30/19 | Southwire
1033.5 45/7 | 1033.5 - 45/7 | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.1062 | 75 | 0.1244 | 967.8 | 189.8 |  | 1033.5 45/7 | Southwire
1033.5 54/7 | 1033.5 - 54/7 | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.246 |  |  |  | 25 | 0.1049 | 75 | 0.1254 | 967.8 | 356 |  | 1033.5 54/7 | Southwire
1113.0 45/7 | 1113.0 - 45/7 | 1113.0 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0990 | 75 | 0.1158 | 1043.4 | 204.8 |  | 1113.0 45/7 | Southwire
1113.0 54/19 | 1113.0 - 54/19 | 1113.0 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0981 | 75 | 0.1172 | 1048.5 | 376.1 |  | 1113.0 54/19 | Southwire
1192.5 45/7 | 1192.5 - 45/7 | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0927 | 75 | 0.1083 | 1117.6 | 219.1 |  | 1192.5 45/7 | Southwire
1192.5 54/19 | 1192.5 - 54/19 | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.0918 | 75 | 0.1096 | 1122.8 | 402.7 |  | 1192.5 54/19 | Southwire
1272.0 45/7 | 1272.0 - 45/7 | 1272.0 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0872 | 75 | 0.1018 | 1191.6 | 233.9 |  | 1272.0 45/7 | Southwire
1272.0 54/19 | 1272.0 - 54/19 | 1272.0 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0864 | 75 | 0.1029 | 1198.1 | 429.3 |  | 1272.0 54/19 | Southwire
1351.5 45/7 | 1351.5 - 45/7 | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0824 | 75 | 0.0961 | 1266.4 | 248.3 |  | 1351.5 45/7 | Southwire
1351.5 54/19 | 1351.5 - 54/19 | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0815 | 75 | 0.0970 | 1272.6 | 455.8 |  | 1351.5 54/19 | Southwire
1431.0 45/7 | 1431.0 - 45/7 | 1431.0 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0781 | 75 | 0.0910 | 1340.5 | 263.1 |  | 1431.0 45/7 | Southwire
1431.0 54/19 | 1431.0 - 54/19 | 1431.0 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0772 | 75 | 0.0918 | 1347.7 | 483.1 |  | 1431.0 54/19 | Southwire
1510.5 45/7 | 1510.5 - 45/7 | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0743 | 75 | 0.0864 | 1415.2 | 277.4 |  | 1510.5 45/7 | Southwire
1510.5 54/19 | 1510.5 - 54/19 | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0734 | 75 | 0.0872 | 1421.5 | 509.2 |  | 1510.5 54/19 | Southwire
1590.0 45/7 | 1590.0 - 45/7 | 1590.0 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0709 | 75 | 0.0824 | 1490.4 | 292.2 |  | 1590.0 45/7 | Southwire
1590.0 54/19 | 1590.0 - 54/19 | 1590.0 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.0700 | 75 | 0.0830 | 1497.3 | 537 |  | 1590.0 54/19 | Southwire
1780.0 84/19 | 1780.0 - 84/19 | 1780.0 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0640 | 75 | 0.0739 | 1676.8 | 386.6 |  | 1780.0 84/19 | Southwire
2034.5 72/7 | 2034.5 - 72/7 | 2034.5 | 72 | 7 | 0.1681 | 0.1122 | 0.3366 | 1.681 |  |  |  | 25 | 0.0577 | 75 | 0.0663 | 1915.8 | 234.3 |  | 2034.5 72/7 | Southwire
2057.0 76/19 | 2057.0 - 76/19 | 2057.0 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.7 |  |  |  | 25 | 0.0569 | 75 | 0.0653 | 1936.5 | 298.5 |  | 2057.0 76/19 | Southwire
2156.0 84/19 | 2156.0 - 84/19 | 2156.0 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0541 | 75 | 0.0621 | 2029.9 | 467.4 |  | 2156.0 84/19 | Southwire
2167.0 72/7 | 2167.0 - 72/7 | 2167.0 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0547 | 75 | 0.0627 | 2040.8 | 249.1 |  | 2167.0 72/7 | Southwire
2312.0 76/19 | 2312.0 - 76/19 | 2312.0 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0516 | 75 | 0.0589 | 2176.6 | 335.4 |  | 2312.0 76/19 | Southwire
2515.0 76/19 | 2515.0 - 76/19 | 2515.0 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0481 | 75 | 0.0548 | 2367.9 | 364.8 |  | 2515.0 76/19 | Southwire

## AACTW
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
AACTW
322.5 - 17 | Logan | 322.5 | 17 |  |  |  |  | 0.6 |  |  | 2 | 25 | 0.2898 | 75 | 0.3468 | 302.3 |  |  | 322.5 - 17 Logan | Southwire
336.4 - 17 | Tulip | 336.4 | 17 |  |  |  |  | 0.612 |  |  | 2 | 25 | 0.2779 | 75 | 0.3325 | 315.3 |  |  | 336.4 - 17 Tulip | Southwire
397.5 - 17 | Canna | 397.5 | 17 |  |  |  |  | 0.661 |  |  | 2 | 25 | 0.2355 | 75 | 0.2817 | 372.6 |  |  | 397.5 - 17 Canna | Southwire
449.4 - 17 | Wheeler | 449.4 | 17 |  |  |  |  | 0.7 |  |  | 2 | 25 | 0.2087 | 75 | 0.2494 | 421.2 |  |  | 449.4 - 17 Wheeler | Southwire
477 - 17 | Cosmos | 477 | 17 |  |  |  |  | 0.72 |  |  | 2 | 25 | 0.1968 | 75 | 0.2352 | 447.1 |  |  | 477 - 17 Cosmos | Southwire
500 - 17 | Zinnia | 500 | 17 |  |  |  |  | 0.736 |  |  | 2 | 25 | 0.1879 | 75 | 0.2245 | 468.7 |  |  | 500 - 17 Zinnia | Southwire
556.5 - 17 | Mistletoe | 556.5 | 17 |  |  |  |  | 0.775 |  |  | 2 | 25 | 0.1691 | 75 | 0.2020 | 521.3 |  |  | 556.5 - 17 Mistletoe | Southwire
595.8 - 17 | Robson | 595.8 | 17 |  |  |  |  | 0.8 |  |  | 2 | 25 | 0.1582 | 75 | 0.1888 | 558.4 |  |  | 595.8 - 17 Robson | Southwire
600 - 17 | Meadowsweet | 600 | 17 |  |  |  |  | 0.803 |  |  | 2 | 25 | 0.1571 | 75 | 0.1875 | 562.4 |  |  | 600 - 17 Meadowsweet | Southwire
636 - 17 | Orchid | 636 | 17 |  |  |  |  | 0.825 |  |  | 2 | 25 | 0.1485 | 75 | 0.1771 | 596.1 |  |  | 636 - 17 Orchid | Southwire
700 - 17 | Verbena | 700 | 17 |  |  |  |  | 0.864 |  |  | 2 | 25 | 0.1353 | 75 | 0.1613 | 656.1 |  |  | 700 - 17 Verbena | Southwire
750 - 17 | Nasturtium | 750 | 17 |  |  |  |  | 0.893 |  |  | 2 | 25 | 0.1266 | 75 | 0.1508 | 702.1 |  |  | 750 - 17 Nasturtium | Southwire
761.5 - 17 | McKinley | 761.5 | 17 |  |  |  |  | 0.9 |  |  | 2 | 25 | 0.1247 | 75 | 0.1486 | 713.7 |  |  | 761.5 - 17 McKinley | Southwire
795 - 17 | Arbutus | 795 | 17 |  |  |  |  | 0.919 |  |  | 2 | 25 | 0.1197 | 75 | 0.1425 | 745.1 |  |  | 795 - 17 Arbutus | Southwire
900 - 17 | Cockscomb | 900 | 17 |  |  |  |  | 0.99 |  |  | 3 | 25 | 0.1064 | 75 | 0.1264 | 843.6 |  |  | 900 - 17 Cockscomb | Southwire
918.8 - 31 | Rainier | 918.8 | 31 |  |  |  |  | 1.000 |  |  | 3 | 25 | 0.1043 | 75 | 0.1239 | 861.2 |  |  | 918.8 - 31 Rainier | Southwire
954 - 31 | Magnolia | 954 | 31 |  |  |  |  | 1.018 |  |  | 3 | 25 | 0.1007 | 75 | 0.1195 | 894.2 |  |  | 954 - 31 Magnolia | Southwire
1000 - 31 | Hawkweed | 1000 | 31 |  |  |  |  | 1.041 |  |  | 3 | 25 | 0.0963 | 75 | 0.1142 | 937.3 |  |  | 1000 - 31 Hawkweed | Southwire
1033.5 - 31 | Bluebell | 1033.5 | 31 |  |  |  |  | 1.057 |  |  | 3 | 25 | 0.0934 | 75 | 0.1107 | 968.7 |  |  | 1033.5 - 31 Bluebell | Southwire
1113 - 31 | Marigold | 1113 | 31 |  |  |  |  | 1.095 |  |  | 3 | 25 | 0.0872 | 75 | 0.1032 | 1043.2 |  |  | 1113 - 31 Marigold | Southwire
1123.1 - 31 | Helens | 1123.1 | 31 |  |  |  |  | 1.1 |  |  | 3 | 25 | 0.0865 | 75 | 0.1023 | 1052.7 |  |  | 1123.1 - 31 Helens | Southwire
1192.5 - 31 | Hawthorn | 1192.5 | 31 |  |  |  |  | 1.132 |  |  | 3 | 25 | 0.0819 | 75 | 0.0967 | 1117.7 |  |  | 1192.5 - 31 Hawthorn | Southwire
1272 - 31 | Narcissus | 1272 | 31 |  |  |  |  | 1.168 |  |  | 3 | 25 | 0.0772 | 75 | 0.0911 | 1192.2 |  |  | 1272 - 31 Narcissus | Southwire
1346.8 - 31 | Baker | 1346.8 | 31 |  |  |  |  | 1.2 |  |  | 3 | 25 | 0.0734 | 75 | 0.0864 | 1262.3 |  |  | 1346.8 - 31 Baker | Southwire
1351.5 - 31 | Columbine | 1351.5 | 31 |  |  |  |  | 1.202 |  |  | 3 | 25 | 0.0731 | 75 | 0.0861 | 1266.3 |  |  | 1351.5 - 31 Columbine | Southwire
1431 - 31 | Carnation | 1431 | 31 |  |  |  |  | 1.236 |  |  | 3 | 25 | 0.0695 | 75 | 0.0817 | 1341.3 |  |  | 1431 - 31 Carnation | Southwire
1583.2 - 34 | Hood | 1583.2 | 34 |  |  |  |  | 1.3 |  |  | 3 | 25 | 0.0637 | 75 | 0.0746 | 1483.9 |  |  | 1583.2 - 34 Hood | Southwire
1590 - 49 | Coreopsis | 1590 | 49 |  |  |  |  | 1.315 |  |  | 4 | 25 | 0.0635 | 75 | 0.0743 | 1490.3 |  |  | 1590 - 49 Coreopsis | Southwire
1750 - 49 | Jessamine | 1750 | 49 |  |  |  |  | 1.377 |  |  | 4 | 25 | 0.0585 | 75 | 0.0683 | 1640.3 |  |  | 1750 - 49 Jessamine | Southwire
1812.7 - 49 | Whitney | 1812.7 | 49 |  |  |  |  | 1.4 |  |  | 4 | 25 | 0.0568 | 75 | 0.0662 | 1699.0 |  |  | 1812.7 - 49 Whitney | Southwire
2000 - 49 | Cowslip | 2000 | 49 |  |  |  |  | 1.468 |  |  | 4 | 25 | 0.0525 | 75 | 0.0609 | 1893.0 |  |  | 2000 - 49 Cowslip | Southwire
2093.6 - 49 | Powell | 2093.6 | 49 |  |  |  |  | 1.5 |  |  | 4 | 25 | 0.0510 | 75 | 0.0591 | 1981.6 |  |  | 2093.6 - 49 Powell | Southwire
2388.1 - 52 | Jefferson | 2388.1 | 52 |  |  |  |  | 1.6 |  |  | 4 | 25 | 0.0461 | 75 | 0.0530 | 2260.3 |  |  | 2388.1 - 52 Jefferson | Southwire
2500 - 71 | Lupine | 2500 | 71 |  |  |  |  | 1.648 |  |  | 5 | 25 | 0.0446 | 75 | 0.0511 | 2366.2 |  |  | 2500 - 71 Lupine | Southwire
3000 - 71 | Trillium | 3000 | 71 |  |  |  |  | 1.799 |  |  | 5 | 25 | 0.0392 | 75 | 0.0445 | 2839.5 |  |  | 3000 - 71 Trillium | Southwire

## ACSS
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
ACSS
266.8 30/7 | Junco | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.660 |  |  |  | 25 | 0.3320 | 75 | 0.3991 | 251.3 | 165.5 | ASTM B 856 | 266.8 30/7 Junco | Southwire
266.8 26/7 | Partridge | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3343 | 75 | 0.4019 | 251.3 | 115.6 | ASTM B 856 | 266.8 26/7 Partridge | Southwire
300 26/7 | Ostrich | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.680 |  |  |  | 25 | 0.2974 | 75 | 0.3575 | 282.5 | 129.8 | ASTM B 856 | 300 26/7 Ostrich | Southwire
336.4 26/7 | Linnet | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.720 |  |  |  | 25 | 0.2654 | 75 | 0.3190 | 316.6 | 145.5 | ASTM B 856 | 336.4 26/7 Linnet | Southwire
336.4 30/7 | Oriole | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2635 | 75 | 0.3167 | 317.7 | 208.7 | ASTM B 856 | 336.4 30/7 Oriole | Southwire
336.4 22/7 | WoodCock | 336.4 | 22 | 7 | 0.1237 | 0.0687 | 0.2061 | 0.701 |  |  |  | 25 | 0.2677 | 75 | 0.3218 | 317.1 | 87.8 | ASTM B 856 | 336.4 22/7 WoodCock | Southwire
397.5 24/7 | Brant | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2258 | 75 | 0.2714 | 374.4 | 137 | ASTM B 856 | 397.5 24/7 Brant | Southwire
397.5 26/7 | Ibis | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2248 | 75 | 0.2701 | 374.1 | 171.9 | ASTM B 856 | 397.5 26/7 Ibis | Southwire
397.5 30/7 | Lark | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2232 | 75 | 0.2681 | 375.3 | 246.6 | ASTM B 856 | 397.5 30/7 Lark | Southwire
397.5 20/7 | Ptarmigan | 397.5 | 20 | 7 | 0.141 | 0.0627 | 0.1881 | 0.752 |  |  |  | 25 | 0.2277 | 75 | 0.2737 | 374.5 | 73.2 | ASTM B 856 | 397.5 20/7 Ptarmigan | Southwire
477 24/7 | Flicker | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1885 | 75 | 0.2264 | 449.4 | 164.5 | ASTM B 856 | 477 24/7 Flicker | Southwire
477 26/7 | Hawk | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1876 | 75 | 0.2253 | 449 | 206.4 | ASTM B 856 | 477 26/7 Hawk | Southwire
477 30/7 | Hen | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1862 | 75 | 0.2236 | 450.4 | 296 | ASTM B 856 | 477 30/7 Hen | Southwire
477 20/7 | Tailorbird | 477 | 20 | 7 | 0.1544 | 0.0686 | 0.2058 | 0.824 |  |  |  | 25 | 0.1901 | 75 | 0.2284 | 449.1 | 87.6 | ASTM B 856 | 477 20/7 Tailorbird | Southwire
556.5 26/7 | Dove | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1610 | 75 | 0.1933 | 524.2 | 241 | ASTM B 856 | 556.5 26/7 Dove | Southwire
556.5 24/7 | Parakeet | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1618 | 75 | 0.1943 | 524.3 | 191.8 | ASTM B 856 | 556.5 24/7 Parakeet | Southwire
556.5 22/7 | Sapsucker | 556.5 | 22 | 7 | 0.159 | 0.0883 | 0.2649 | 0.901 |  |  |  | 25 | 0.1626 | 75 | 0.1952 | 523.9 | 145.1 | ASTM B 856 | 556.5 22/7 Sapsucker | Southwire
605 24/7 | Peacock | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1490 | 75 | 0.1789 | 570 | 208.7 | ASTM B 856 | 605 24/7 Peacock | Southwire
605 26/7 | Squab | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1483 | 75 | 0.1780 | 569.5 | 261.8 | ASTM B 856 | 605 26/7 Squab | Southwire
605 30/19 | Teal | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1472 | 75 | 0.1767 | 571.2 | 367.5 | ASTM B 856 | 605 30/19 Teal | Southwire
605 30/7 | Wood Duck | 605 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1471 | 75 | 0.1766 | 571.2 | 375.3 | ASTM B 856 | 605 30/7 Wood Duck | Southwire
636 30/19 | Egret | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1402 | 75 | 0.1682 | 600.5 | 386.7 | ASTM B 856 | 636 30/19 Egret | Southwire
636 22/7 | Goldfinch | 636 | 22 | 7 | 0.170 | 0.0944 | 0.2832 | 0.963 |  |  |  | 25 | 0.1426 | 75 | 0.1711 | 598.9 | 165.9 | ASTM B 856 | 636 22/7 Goldfinch | Southwire
636 26/7 | Grosbeak | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.991 |  |  |  | 25 | 0.1412 | 75 | 0.1694 | 599 | 275.2 | ASTM B 856 | 636 26/7 Grosbeak | Southwire
636 24/7 | Rook | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1419 | 75 | 0.1702 | 599.1 | 219.1 | ASTM B 856 | 636 24/7 Rook | Southwire
636 30/7 | Scoter | 636 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1401 | 75 | 0.1681 | 600.5 | 394.6 | ASTM B 856 | 636 30/7 Scoter | Southwire
666.6 24/7 | Flamingo | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1.000 |  |  |  | 25 | 0.1355 | 75 | 0.1625 | 628.2 | 229.7 | ASTM B 856 | 666.6 24/7 Flamingo | Southwire
666.6 26/7 | Gannet | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1348 | 75 | 0.1617 | 627.7 | 288.5 | ASTM B 856 | 666.6 26/7 Gannet | Southwire
715.5 30/19 | Redwing | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1248 | 75 | 0.1497 | 675.3 | 434.1 | ASTM B 856 | 715.5 30/19 Redwing | Southwire
715.5 26/7 | Starling | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1258 | 75 | 0.1508 | 674 | 309.7 | ASTM B 856 | 715.5 26/7 Starling | Southwire
715.5 24/7 | Stilt | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1264 | 75 | 0.1516 | 674.2 | 246.6 | ASTM B 856 | 715.5 24/7 Stilt | Southwire
795 54/7 | Condor | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1141 | 75 | 0.1406 | 748.4 | 273.9 | ASTM B 856 | 795 54/7 Condor | Southwire
795 24/7 | Cuckoo | 795 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1141 | 75 | 0.1367 | 748.8 | 273.9 | ASTM B 856 | 795 24/7 Cuckoo | Southwire
795 26/7 | Drake | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1135 | 75 | 0.1359 | 749.1 | 344.3 | ASTM B 856 | 795 26/7 Drake | Southwire
795 42/7 | Macaw | 795 | 42 | 7 | 0.1376 | 0.0764 | 0.2292 | 1.055 |  |  |  | 25 | 0.1157 | 75 | 0.1385 | 749 | 108.6 | ASTM B 856 | 795 42/7 Macaw | Southwire
795 30/19 | Mallard | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.140 |  |  |  | 25 | 0.1125 | 75 | 0.1349 | 750.7 | 483.2 | ASTM B 856 | 795 30/19 Mallard | Southwire
795 22/7 | Puffin | 795 | 22 | 7 | 0.1901 | 0.1056 | 0.3168 | 1.077 |  |  |  | 25 | 0.1147 | 75 | 0.1374 | 748.8 | 207.6 | ASTM B 856 | 795 22/7 Puffin | Southwire
795 45/7 | Tern | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1153 | 75 | 0.1390 | 748.6 | 146.1 | ASTM B 856 | 795 45/7 Tern | Southwire
900 54/7 | Canary | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1012 | 75 | 0.1245 | 847.7 | 310.2 | ASTM B 856 | 900 54/7 Canary | Southwire
900 45/7 | Ruddy | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1023 | 75 | 0.1232 | 847.4 | 165.5 | ASTM B 856 | 900 45/7 Ruddy | Southwire
954 30/19 | Canvasback | 954 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.0942 | 75 | 0.1128 | 900.5 | 579.6 | ASTM B 856 | 954 30/19 Canvasback | Southwire
954 54/7 | Cardinal | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0956 | 75 | 0.1176 | 898.3 | 328.7 | ASTM B 856 | 954 54/7 Cardinal | Southwire
954 20/7 | Corncrake | 954 | 20 | 7 | 0.2184 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0968 | 75 | 0.1156 | 898.5 | 175.5 | ASTM B 856 | 954 20/7 Corncrake | Southwire
954 45/7 | Rail | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0968 | 75 | 0.1164 | 898.5 | 175.5 | ASTM B 856 | 954 45/7 Rail | Southwire
954 24/7 | Redbird | 954 | 24 | 7 | 0.1994 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0956 | 75 | 0.1144 | 898.8 | 328.7 | ASTM B 856 | 954 24/7 Redbird | Southwire
954 48/7 | Towhee | 954 | 48 | 7 | 0.141 | 0.1097 | 0.3291 | 1.175 |  |  |  | 25 | 0.0964 | 75 | 0.1152 | 898.8 | 224 | ASTM B 856 | 954 48/7 Towhee | Southwire
1033.5 54/7 | Curlew | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0886 | 75 | 0.1087 | 972.8 | 356 | ASTM B 856 | 1033.5 54/7 Curlew | Southwire
1033.5 45/7 | Ortolan | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0897 | 75 | 0.1077 | 972.8 | 189.9 | ASTM B 856 | 1033.5 45/7 Ortolan | Southwire
1033.5 42/7 | Snowbird | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0901 | 75 | 0.1074 | 973.9 | 141.5 | ASTM B 856 | 1033.5 42/7 Snowbird | Southwire
1113 45/7 | Bluejay | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.258 |  |  |  | 25 | 0.0837 | 75 | 0.1003 | 1048.7 | 204.8 | ASTM B 856 | 1113 45/7 Bluejay | Southwire
1113 54/19 | Finch | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.292 |  |  |  | 25 | 0.0830 | 75 | 0.1017 | 1053.9 | 376.1 | ASTM B 856 | 1113 54/19 Finch | Southwire
1192.5 45/7 | Bunting | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0785 | 75 | 0.0939 | 1123.4 | 219.1 | ASTM B 856 | 1192.5 45/7 Bunting | Southwire
1192.5 54/19 | Grackle | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.337 |  |  |  | 25 | 0.0777 | 75 | 0.0951 | 1128.6 | 402.8 | ASTM B 856 | 1192.5 54/19 Grackle | Southwire
1272 45/7 | Bittern | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0739 | 75 | 0.0884 | 1197.7 | 233.9 | ASTM B 856 | 1272 45/7 Bittern | Southwire
1272 54/19 | Pheasant | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.381 |  |  |  | 25 | 0.0732 | 75 | 0.0894 | 1204.3 | 429.4 | ASTM B 856 | 1272 54/19 Pheasant | Southwire
1351.5 45/7 | Dipper | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0699 | 75 | 0.0835 | 1272.9 | 248.3 | ASTM B 856 | 1351.5 45/7 Dipper | Southwire
1351.5 54/19 | Martin | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0692 | 75 | 0.0844 | 1279.1 | 455.9 | ASTM B 856 | 1351.5 54/19 Martin | Southwire
1431 45/7 | Bobolink | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0664 | 75 | 0.0791 | 1347.5 | 263.1 | ASTM B 856 | 1431 45/7 Bobolink | Southwire
1431 54/19 | Plover | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0656 | 75 | 0.0799 | 1354.6 | 483.2 | ASTM B 856 | 1431 54/19 Plover | Southwire
1510.5 45/7 | Nuthatch | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0633 | 75 | 0.0752 | 1422.5 | 277.5 | ASTM B 856 | 1510.5 45/7 Nuthatch | Southwire
1510.5 54/19 | Parrot | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0624 | 75 | 0.0759 | 1428.8 | 509.2 | ASTM B 856 | 1510.5 54/19 Parrot | Southwire
1590 54/19 | Falcon | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.544 |  |  |  | 25 | 0.0596 | 75 | 0.0724 | 1505 | 537 | ASTM B 856 | 1590 54/19 Falcon | Southwire
1590 45/7 | Lapwing | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0605 | 75 | 0.0718 | 1498.1 | 292.2 | ASTM B 856 | 1590 45/7 Lapwing | Southwire
1590 42/7 | Ratite | 1590 | 42 | 7 | 0.1946 | 0.1081 | 0.3243 | 1.492 |  |  |  | 25 | 0.0608 | 75 | 0.0718 | 1498.1 | 217.5 | ASTM B 856 | 1590 42/7 Ratite | Southwire
1780 84/19 | Chukar | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.601 |  |  |  | 25 | 0.0547 | 75 | 0.0645 | 1685.4 | 386.7 | ASTM B 856 | 1780 84/19 Chukar | Southwire
2034.5 72/7 | Mockingbird | 2034.5 | 72 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.681 |  |  |  | 25 | 0.0498 | 75 | 0.0581 | 1925.7 | 233.9 | ASTM B 856 | 2034.5 72/7 Mockingbird | Southwire
2057 76/19 | Roadrunner | 2057 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.700 |  |  |  | 25 | 0.0490 | 75 | 0.0573 | 1946.5 | 298.6 | ASTM B 856 | 2057 76/19 Roadrunner | Southwire
2156 84/19 | Bluebird | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0466 | 75 | 0.0544 | 2040.4 | 467.5 | ASTM B 856 | 2156 84/19 Bluebird | Southwire
2167 72/7 | Kiwi | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0473 | 75 | 0.0551 | 2051.4 | 249.2 | ASTM B 856 | 2167 72/7 Kiwi | Southwire
2312 76/19 | Thrasher | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0447 | 75 | 0.0519 | 2187.9 | 335.4 | ASTM B 856 | 2312 76/19 Thrasher | Southwire
2515 76/19 | Joree | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.880 |  |  |  | 25 | 0.0419 | 75 | 0.0484 | 2380.1 | 364.9 | ASTM B 856 | 2515 76/19 Joree | Southwire

## ACSRTW
*** Values on this sheet are in Imperial Units
|  | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp ˚C | Low Resistance Ω/mile | Hi Temp ˚C | Hi Resistance Ω/mile | Al Weight | St Weight | Spec |  | Values from
ACSRTW
336.4 14/1 Type 6 | Merlin | 336.4 | 14 | 1 |  | 0.1367 | 0.1367 | 0.63 |  | 6 | 2 | 25 | 0.2756 | 75 | 0.3298 | 315.5 | 49.5 |  | 336.4 14/1 Type 6 Merlin | Southwire
405.1 14/1 Type 6 | Monongahela | 405.1 | 14 | 1 |  | 0.152 | 0.152 | 0.68 |  | 6 | 2 | 25 | 0.2291 | 75 | 0.2740 | 379.8 | 61.2 |  | 405.1 14/1 Type 6 Monongahela | Southwire
477 18/7 Type 13 | Flicker | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.1930 | 75 | 0.2307 | 448.4 | 164.4 |  | 477 18/7 Type 13 Flicker | Southwire
477 18/7 Type 16 | Hawk | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.1923 | 75 | 0.2298 | 448.7 | 206.3 |  | 477 18/7 Type 16 Hawk | Southwire
556.5 20/7 Type 16 | Dove | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.1650 | 75 | 0.1972 | 523.5 | 241 |  | 556.5 20/7 Type 16 Dove | Southwire
556.5 18/7 Type 13 | Parakeet | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1657 | 75 | 0.1980 | 523.2 | 191.7 |  | 556.5 18/7 Type 13 Parakeet | Southwire
565.3 20/7 Type 16 | Calumet | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1625 | 75 | 0.1941 | 531 | 244.8 |  | 565.3 20/7 Type 16 Calumet | Southwire
571.7 18/7 Type 13 | Mohawk | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.1613 | 75 | 0.1928 | 537.3 | 197.4 |  | 571.7 18/7 Type 13 Mohawk | Southwire
636 20/7 Type 16 | Grosbeak | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.1446 | 75 | 0.1727 | 598.4 | 275.1 |  | 636 20/7 Type 16 Grosbeak | Southwire
636 18/7 Type 13 | Rook | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.89 |  | 13 | 2 | 25 | 0.1452 | 75 | 0.1735 | 597.9 | 219.1 |  | 636 18/7 Type 13 Rook | Southwire
636 27/1 Type 3 | Swift | 636 | 27 | 1 |  | 0.1329 | 0.1329 | 0.85 |  | 3 | 3 | 25 | 0.1482 | 75 | 0.1816 | 599.2 | 46.8 |  | 636 27/1 Type 3 Swift | Southwire
664.8 20/7 Type 16 | Oswego | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1385 | 75 | 0.1653 | 625.4 | 288 |  | 664.8 20/7 Type 16 Oswego | Southwire
666.6 20/7 Type 13 | Mystic | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1387 | 75 | 0.1656 | 626.6 | 229.7 |  | 666.6 20/7 Type 13 Mystic | Southwire
762.8 20/7 Type 16 | Wabash | 762.8 | 20 | 7 |  | 0.1331 | 0.3343 | 0.99 |  | 16 | 2 | 25 | 0.1212 | 75 | 0.1446 | 717 | 330 |  | 762.8 20/7 Type 16 Wabash | Southwire
768.2 20/7 Type 13 | Maumee | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1207 | 75 | 0.1439 | 722.1 | 265.7 |  | 768.2 20/7 Type 13 Maumee | Southwire
768.9 27/1 Type 3 | Nechako | 768.9 | 27 | 1 |  | 0.152 | 0.152 | 0.93 |  | 3 | 3 | 25 | 0.1232 | 75 | 0.1506 | 720.7 | 61.2 |  | 768.9 27/1 Type 3 Nechako | Southwire
795 20/7 Type 13 | Condor | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1167 | 75 | 0.1392 | 747.2 | 273.8 |  | 795 20/7 Type 13 Condor | Southwire
795 20/7 Type 16 | Drake | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.01 |  | 16 | 2 | 25 | 0.1161 | 75 | 0.1386 | 747.8 | 344.2 |  | 795 20/7 Type 16 Drake | Southwire
795 18/7 Type 10 | Puffin | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.98 |  | 10 | 2 | 25 | 0.1171 | 75 | 0.1396 | 746.9 | 228.4 |  | 795 18/7 Type 10 Puffin | Southwire
795 17/7 Type 7 | Tern | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.96 |  | 7 | 2 | 25 | 0.1178 | 75 | 0.1405 | 745.9 | 146.1 |  | 795 17/7 Type 7 Tern | Southwire
946.7 35/7 Type 10 | Fraser | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0995 | 75 | 0.1214 | 894 | 248 |  | 946.7 35/7 Type 10 Fraser | Southwire
954 20/7 Type 13 | Cardinal | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.0977 | 75 | 0.1164 | 897.3 | 328.7 |  | 954 20/7 Type 13 Cardinal | Southwire
954 30/7 Type 5 | Phoenix | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.0996 | 75 | 0.1213 | 901.6 | 130.4 |  | 954 30/7 Type 5 Phoenix | Southwire
954 32/7 Type 7 | Rail | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0993 | 75 | 0.1210 | 900 | 175 |  | 954 32/7 Type 7 Rail | Southwire
957.2 32/7 Type 7 | Kettle | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.06 |  | 7 | 3 | 25 | 0.0990 | 75 | 0.1206 | 902.8 | 176.2 |  | 957.2 32/7 Type 7 Kettle | Southwire
959.6 22/7 Type 16 | Suwannee | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0967 | 75 | 0.1152 | 903 | 415 |  | 959.6 22/7 Type 16 Suwannee | Southwire
966.2 21/7 Type 13 | Columbia | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.0966 | 75 | 0.1150 | 908 | 333 |  | 966.2 21/7 Type 13 Columbia | Southwire
1033.5 21/7 Type 13 | Curlew | 1033.5 | 21 | 7 |  | 0.1363 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.0905 | 75 | 0.1077 | 971.1 | 355.9 |  | 1033.5 21/7 Type 13 Curlew | Southwire
1033.5 32/7 Type 7 | Ortolan | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.0920 | 75 | 0.1120 | 975.2 | 189.8 |  | 1033.5 32/7 Type 7 Ortolan | Southwire
1033.5 30/7 Type 5 | Snowbird | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0923 | 75 | 0.1123 | 973.8 | 141.2 |  | 1033.5 30/7 Type 5 Snowbird | Southwire
1113 30/7 Type 5 | Avocet | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0861 | 75 | 0.1045 | 1048.9 | 152.1 |  | 1113 30/7 Type 5 Avocet | Southwire
1113 33/7 Type 7 | Bluejay | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0858 | 75 | 0.1042 | 1052.2 | 204.8 |  | 1113 33/7 Type 7 Bluejay | Southwire
1113 38/19 Type 13 | Finch | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0848 | 75 | 0.1032 | 1052.6 | 376.4 |  | 1113 38/19 Type 13 Finch | Southwire
1158 33/7 Type 7 | Genesee | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0826 | 75 | 0.1003 | 1092 | 216 |  | 1158 33/7 Type 7 Genesee | Southwire
1158.4 26/7 Type 13 | Hudson | 1158.4 | 26 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.0811 | 75 | 0.0964 | 1089 | 400 |  | 1158.4 26/7 Type 13 Hudson | Southwire
1168.1 30/7 Type 5 | Cheyenne | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0823 | 75 | 0.0998 | 1100.4 | 159.6 |  | 1168.1 30/7 Type 5 Cheyenne | Southwire
1192.5 33/7 Type 7 | Bunting | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0804 | 75 | 0.0975 | 1124 | 219 |  | 1192.5 33/7 Type 7 Bunting | Southwire
1192.5 38/19 Type 13 | Grackle | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0794 | 75 | 0.0965 | 1127 | 403 |  | 1192.5 38/19 Type 13 Grackle | Southwire
1192.5 30/7 Type 5 | Oxbird | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0807 | 75 | 0.0978 | 1123 | 163 |  | 1192.5 30/7 Type 5 Oxbird | Southwire
1233.6 38/19 Type 13 | Yukon | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.0769 | 75 | 0.0934 | 1166.5 | 419.5 |  | 1233.6 38/19 Type 13 Yukon | Southwire
1257.1 35/7 Type 7 | Nelson | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0765 | 75 | 0.0927 | 1185.7 | 231.3 |  | 1257.1 35/7 Type 7 Nelson | Southwire
1272 35/7 Type 7 | Bittern | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0757 | 75 | 0.0917 | 1199 | 234 |  | 1272 35/7 Type 7 Bittern | Southwire
1272 30/7 Type 5 | Catawba | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0760 | 75 | 0.0920 | 1198 | 174 |  | 1272 30/7 Type 5 Catawba | Southwire
1272 39/19 Type 13 | Pheasant | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.0747 | 75 | 0.0907 | 1202 | 430 |  | 1272 39/19 Type 13 Pheasant | Southwire
1272 30/7 Type 5 | Scissortail | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0760 | 75 | 0.0920 | 1198 | 174 |  | 1272 30/7 Type 5 Scissortail | Southwire
1334.6 39/19 Type 13 | Thames | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.0714 | 75 | 0.0866 | 1261.6 | 451.4 |  | 1334.6 39/19 Type 13 Thames | Southwire
1351.5 35/7 Type 7 | Dipper | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0716 | 75 | 0.0865 | 1274 | 248 |  | 1351.5 35/7 Type 7 Dipper | Southwire
1351.5 39/19 Type 13 | Martin | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.3 |  | 13 | 3 | 25 | 0.0706 | 75 | 0.0856 | 1278 | 456 |  | 1351.5 39/19 Type 13 Martin | Southwire
1359.7 36/7 Type 7 | Mackenzie | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0712 | 75 | 0.0860 | 1280 | 250 |  | 1359.7 36/7 Type 7 Mackenzie | Southwire
1372.5 30/7 Type 5 | Truckee | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0709 | 75 | 0.0856 | 1293.4 | 187.6 |  | 1372.5 30/7 Type 5 Truckee | Southwire
1431 36/7 Type 7 | Bobolink | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0679 | 75 | 0.0820 | 1350 | 263 |  | 1431 36/7 Type 7 Bobolink | Southwire
1431 39/19 Type 13 | Plover | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0669 | 75 | 0.0810 | 1353 | 483 |  | 1431 39/19 Type 13 Plover | Southwire
1433.6 39/19 Type 13 | Merrimack | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.34 |  | 13 | 3 | 25 | 0.0668 | 75 | 0.0809 | 1356 | 434 |  | 1433.6 39/19 Type 13 Merrimack | Southwire
1455.3 36/7 Type 7 | Miramichi | 1455.3 | 36 | 7 |  | 0.12 | 0.36 | 1.302 |  | 7 | 3 | 25 | 0.0669 | 75 | 0.0807 | 1372 | 268 |  | 1455.3 36/7 Type 7 Miramichi | Southwire
1467.8 33/7 Type 5 | St. Croix | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.0667 | 75 | 0.0804 | 1383 | 202 |  | 1467.8 33/7 Type 5 St. Croix | Southwire
1533.3 39/19 Type 13 | Rio Grande | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0628 | 75 | 0.0758 | 1449 | 519 |  | 1533.3 39/19 Type 13 Rio Grande | Southwire
1557.4 36/7 Type 7 | Potomac | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0629 | 75 | 0.0757 | 1468 | 287 |  | 1557.4 36/7 Type 7 Potomac | Southwire
1569 33/7 Type 5 | Platte | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0629 | 75 | 0.0756 | 1478 | 215 |  | 1569 33/7 Type 5 Platte | Southwire
1590 42/19 Type 13 | Falcon | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.0607 | 75 | 0.0733 | 1503 | 537 |  | 1590 42/19 Type 13 Falcon | Southwire
1590 36/7 Type 7 | Lapwing | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.0618 | 75 | 0.0743 | 1499 | 292 |  | 1590 36/7 Type 7 Lapwing | Southwire
1622 39/19 Type 13 | Pecos | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.0595 | 75 | 0.0718 | 1533 | 574 |  | 1622 39/19 Type 13 Pecos | Southwire
1657.4 36/7 Type 7 | Schuylkill | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0595 | 75 | 0.0715 | 1563 | 305 |  | 1657.4 36/7 Type 7 Schuylkill | Southwire
1730.6 39/19 Type 13 | James | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.47 |  | 13 | 3 | 25 | 0.0562 | 75 | 0.0677 | 1636 | 585 |  | 1730.6 39/19 Type 13 James | Southwire
1758.6 37/7 Type 7 | Pee Dee | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0565 | 75 | 0.0677 | 1658 | 324 |  | 1758.6 37/7 Type 7 Pee Dee | Southwire
1780 37/19 Type 8 | Chukar | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.0555 | 75 | 0.0666 | 1676 | 387 |  | 1780 37/19 Type 8 Chukar | Southwire
1926.9 42/19 Type 13 | Cumberland | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.0511 | 75 | 0.0613 | 1821 | 650 |  | 1926.9 42/19 Type 13 Cumberland | Southwire
1949.6 42/7 Type 7 | Athabaska | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.0517 | 75 | 0.0607 | 1838 | 361 |  | 1949.6 42/7 Type 7 Athabaska | Southwire
2153.8 64/19 Type 8 | Powder | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0475 | 75 | 0.0554 | 2030 | 468 |  | 2153.8 64/19 Type 8 Powder | Southwire
2156 64/19 Type 8 | Bluebird | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0475 | 75 | 0.0554 | 2047 | 468 |  | 2156 64/19 Type 8 Bluebird | Southwire
2627.3 64/19 Type 8 | Santee | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0405 | 75 | 0.0468 | 2477 | 571 |  | 2627.3 64/19 Type 8 Santee | Southwire

## qc (hidden)
Convected Heat Loss (qc), Watts Per Foot of Conductor
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 1.069 | 1.0331 | 0.99666 | 0.95961 | 0.922 | 0.88381 | 0.84504 | 0.80571 | 0.7658 | 0.72532 | 0.68427 | 0.64264
Emergency | 2.533 | 110 | 1.069 | 1.0331 | 0.99666 | 0.95961 | 0.922 | 0.88381 | 0.84504 | 0.80571 | 0.7658 | 0.72532 | 0.68427 | 0.64264
Normal | 0 | 120 | 1.17 | 1.1341 | 1.0976 | 1.0606 | 1.0229 | 0.98475 | 0.94599 | 0.90665 | 0.86674 | 0.82625 | 0.7852 | 0.74357
Emergency | 2.533 | 120 | 1.17 | 1.1341 | 1.0976 | 1.0606 | 1.0229 | 0.98475 | 0.94599 | 0.90665 | 0.86674 | 0.82625 | 0.7852 | 0.74357
Normal | 0 | 130 | 1.2732 | 1.2373 | 1.2009 | 1.1638 | 1.1262 | 1.088 | 1.0492 | 1.0099 | 0.96995 | 0.92946 | 0.8884 | 0.84677
Emergency | 2.533 | 130 | 1.2732 | 1.2373 | 1.2009 | 1.1638 | 1.1262 | 1.088 | 1.0492 | 1.0099 | 0.96995 | 0.92946 | 0.8884 | 0.84677
Normal | 0 | 140 | 1.3788 | 1.3428 | 1.3064 | 1.2693 | 1.2317 | 1.1935 | 1.1547 | 1.1154 | 1.0754 | 1.0349 | 0.99388 | 0.95225
Emergency | 2.533 | 140 | 1.3788 | 1.3428 | 1.3064 | 1.2693 | 1.2317 | 1.1935 | 1.1547 | 1.1154 | 1.0754 | 1.0349 | 0.99388 | 0.95225
Normal | 0 | 150 | 1.4866 | 1.4506 | 1.4141 | 1.3771 | 1.3395 | 1.3012 | 1.2625 | 1.2231 | 1.1832 | 1.1427 | 1.1016 | 1.06
Emergency | 2.533 | 150 | 1.4866 | 1.4506 | 1.4141 | 1.3771 | 1.3395 | 1.3012 | 1.2625 | 1.2231 | 1.1832 | 1.1427 | 1.1016 | 1.06
Normal | 0 | 160 | 1.5966 | 1.5607 | 1.5242 | 1.4871 | 1.4495 | 1.4113 | 1.3725 | 1.3332 | 1.2932 | 1.2527 | 1.2117 | 1.17
Emergency | 2.533 | 160 | 1.5966 | 1.5607 | 1.5242 | 1.4871 | 1.4495 | 1.4113 | 1.3725 | 1.3332 | 1.2932 | 1.2527 | 1.2117 | 1.17
Normal | 0 | 170 | 1.709 | 1.673 | 1.6365 | 1.5995 | 1.5618 | 1.5236 | 1.4848 | 1.4455 | 1.4055 | 1.365 | 1.3239 | 1.2823
Emergency | 2.533 | 170 | 1.709 | 1.673 | 1.6365 | 1.5995 | 1.5618 | 1.5236 | 1.4848 | 1.4455 | 1.4055 | 1.365 | 1.3239 | 1.2823

## qc0 (hidden)
Natural Convected Heat Loss (qc), Watts Per Foot of Conductor
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## qc1 (hidden)
Low Wind Convected Heat Loss (qc), Watts Per Foot of Conductor
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 1.069 | 1.0331 | 0.99666 | 0.95961 | 0.922 | 0.88381 | 0.84504 | 0.80571 | 0.7658 | 0.72532 | 0.68427 | 0.64264
Emergency | 2.533 | 110 | 1.069 | 1.0331 | 0.99666 | 0.95961 | 0.922 | 0.88381 | 0.84504 | 0.80571 | 0.7658 | 0.72532 | 0.68427 | 0.64264
Normal | 0 | 120 | 1.17 | 1.1341 | 1.0976 | 1.0606 | 1.0229 | 0.98475 | 0.94599 | 0.90665 | 0.86674 | 0.82625 | 0.7852 | 0.74357
Emergency | 2.533 | 120 | 1.17 | 1.1341 | 1.0976 | 1.0606 | 1.0229 | 0.98475 | 0.94599 | 0.90665 | 0.86674 | 0.82625 | 0.7852 | 0.74357
Normal | 0 | 130 | 1.2732 | 1.2373 | 1.2009 | 1.1638 | 1.1262 | 1.088 | 1.0492 | 1.0099 | 0.96995 | 0.92946 | 0.8884 | 0.84677
Emergency | 2.533 | 130 | 1.2732 | 1.2373 | 1.2009 | 1.1638 | 1.1262 | 1.088 | 1.0492 | 1.0099 | 0.96995 | 0.92946 | 0.8884 | 0.84677
Normal | 0 | 140 | 1.3788 | 1.3428 | 1.3064 | 1.2693 | 1.2317 | 1.1935 | 1.1547 | 1.1154 | 1.0754 | 1.0349 | 0.99388 | 0.95225
Emergency | 2.533 | 140 | 1.3788 | 1.3428 | 1.3064 | 1.2693 | 1.2317 | 1.1935 | 1.1547 | 1.1154 | 1.0754 | 1.0349 | 0.99388 | 0.95225
Normal | 0 | 150 | 1.4866 | 1.4506 | 1.4141 | 1.3771 | 1.3395 | 1.3012 | 1.2625 | 1.2231 | 1.1832 | 1.1427 | 1.1016 | 1.06
Emergency | 2.533 | 150 | 1.4866 | 1.4506 | 1.4141 | 1.3771 | 1.3395 | 1.3012 | 1.2625 | 1.2231 | 1.1832 | 1.1427 | 1.1016 | 1.06
Normal | 0 | 160 | 1.5966 | 1.5607 | 1.5242 | 1.4871 | 1.4495 | 1.4113 | 1.3725 | 1.3332 | 1.2932 | 1.2527 | 1.2117 | 1.17
Emergency | 2.533 | 160 | 1.5966 | 1.5607 | 1.5242 | 1.4871 | 1.4495 | 1.4113 | 1.3725 | 1.3332 | 1.2932 | 1.2527 | 1.2117 | 1.17
Normal | 0 | 170 | 1.709 | 1.673 | 1.6365 | 1.5995 | 1.5618 | 1.5236 | 1.4848 | 1.4455 | 1.4055 | 1.365 | 1.3239 | 1.2823
Emergency | 2.533 | 170 | 1.709 | 1.673 | 1.6365 | 1.5995 | 1.5618 | 1.5236 | 1.4848 | 1.4455 | 1.4055 | 1.365 | 1.3239 | 1.2823

## qc2 (hidden)
High Wind Convected Heat Loss (qc), Watts Per Foot of Conductor
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## qr (hidden)
Radiated Heat Loss (qr), Watts Per Foot of Conductor
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## qs (hidden)
Solar Heat Gain (qs), Watts Per Foot of Conductor
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Normal | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency | 2.533 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## uf (hidden)
Absolute Viscosity of Air (mf), (lb/ft*h)
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 0.047038 | 0.047314 | 0.04759 | 0.047864 | 0.048138 | 0.04841 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024
Emergency | 2.533 | 110 | 0.047038 | 0.047314 | 0.04759 | 0.047864 | 0.048138 | 0.04841 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024
Normal | 0 | 120 | 0.04759 | 0.047864 | 0.048138 | 0.04841 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554
Emergency | 2.533 | 120 | 0.04759 | 0.047864 | 0.048138 | 0.04841 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554
Normal | 0 | 130 | 0.048138 | 0.04841 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081
Emergency | 2.533 | 130 | 0.048138 | 0.04841 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081
Normal | 0 | 140 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603
Emergency | 2.533 | 140 | 0.048682 | 0.048952 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603
Normal | 0 | 150 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603 | 0.051863 | 0.052122
Emergency | 2.533 | 150 | 0.049222 | 0.04949 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603 | 0.051863 | 0.052122
Normal | 0 | 160 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603 | 0.051863 | 0.052122 | 0.05238 | 0.052637
Emergency | 2.533 | 160 | 0.049758 | 0.050024 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603 | 0.051863 | 0.052122 | 0.05238 | 0.052637
Normal | 0 | 170 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603 | 0.051863 | 0.052122 | 0.05238 | 0.052637 | 0.052894 | 0.053149
Emergency | 2.533 | 170 | 0.05029 | 0.050554 | 0.050818 | 0.051081 | 0.051342 | 0.051603 | 0.051863 | 0.052122 | 0.05238 | 0.052637 | 0.052894 | 0.053149

## pf (hidden)
Air Density (rf), (lb/ft3)
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 0.068223 | 0.067694 | 0.067174 | 0.066661 | 0.066156 | 0.065658 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824
Emergency | 2.533 | 110 | 0.068223 | 0.067694 | 0.067174 | 0.066661 | 0.066156 | 0.065658 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824
Normal | 0 | 120 | 0.067174 | 0.066661 | 0.066156 | 0.065658 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933
Emergency | 2.533 | 120 | 0.067174 | 0.066661 | 0.066156 | 0.065658 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933
Normal | 0 | 130 | 0.066156 | 0.065658 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067
Emergency | 2.533 | 130 | 0.066156 | 0.065658 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067
Normal | 0 | 140 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224
Emergency | 2.533 | 140 | 0.065168 | 0.064686 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224
Normal | 0 | 150 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224 | 0.059812 | 0.059405
Emergency | 2.533 | 150 | 0.06421 | 0.063741 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224 | 0.059812 | 0.059405
Normal | 0 | 160 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224 | 0.059812 | 0.059405 | 0.059003 | 0.058607
Emergency | 2.533 | 160 | 0.063279 | 0.062824 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224 | 0.059812 | 0.059405 | 0.059003 | 0.058607
Normal | 0 | 170 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224 | 0.059812 | 0.059405 | 0.059003 | 0.058607 | 0.058217 | 0.057831
Emergency | 2.533 | 170 | 0.062375 | 0.061933 | 0.061497 | 0.061067 | 0.060642 | 0.060224 | 0.059812 | 0.059405 | 0.059003 | 0.058607 | 0.058217 | 0.057831

## kf (hidden)
Thermal Conductivity of Air (kf) at Temperature , Tfilm W/ft (degrees C)
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | 0.0084675 | 0.0085241 | 0.0085808 | 0.0086374 | 0.008694 | 0.0087506 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897
Emergency | 2.533 | 110 | 0.0084675 | 0.0085241 | 0.0085808 | 0.0086374 | 0.008694 | 0.0087506 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897
Normal | 0 | 120 | 0.0085808 | 0.0086374 | 0.008694 | 0.0087506 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026
Emergency | 2.533 | 120 | 0.0085808 | 0.0086374 | 0.008694 | 0.0087506 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026
Normal | 0 | 130 | 0.008694 | 0.0087506 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154
Emergency | 2.533 | 130 | 0.008694 | 0.0087506 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154
Normal | 0 | 140 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282
Emergency | 2.533 | 140 | 0.0088071 | 0.0088637 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282
Normal | 0 | 150 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282 | 0.0094846 | 0.0095409
Emergency | 2.533 | 150 | 0.0089202 | 0.0089767 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282 | 0.0094846 | 0.0095409
Normal | 0 | 160 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282 | 0.0094846 | 0.0095409 | 0.0095973 | 0.0096536
Emergency | 2.533 | 160 | 0.0090332 | 0.0090897 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282 | 0.0094846 | 0.0095409 | 0.0095973 | 0.0096536
Normal | 0 | 170 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282 | 0.0094846 | 0.0095409 | 0.0095973 | 0.0096536 | 0.0097099 | 0.0097661
Emergency | 2.533 | 170 | 0.0091462 | 0.0092026 | 0.009259 | 0.0093154 | 0.0093718 | 0.0094282 | 0.0094846 | 0.0095409 | 0.0095973 | 0.0096536 | 0.0097099 | 0.0097661

## Resistance (hidden)
Conductor Electrical Resistance (R), (Ohms/ft.)
|  | Line Designation or Project Name: | Line 1234 | [7 empty] | Date Prepared: | 2026-07-30 06:24
|  | Line Description: | Substation A to Substation B | [7 empty] | Prepared by: | Mark Shuck
Conductor Size and Type:
Ambient Air Temperature (˚C)
Rating Condition | Wind Speed | Cond. Oper. Temp. | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| (ft./sec.) | (˚C)
Normal | 0 | 110 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency | 2.533 | 110 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal | 0 | 120 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency | 2.533 | 120 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal | 0 | 130 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency | 2.533 | 130 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal | 0 | 140 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency | 2.533 | 140 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal | 0 | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency | 2.533 | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal | 0 | 160 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency | 2.533 | 160 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Normal | 0 | 170 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Emergency | 2.533 | 170 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!